## Source of Data
GXP | Equipment Type | Device | Source 1 | Source 2 | Source 3 | Source 4
ALL | Air Break Switch | - | GEMA | AEL Drawings
ALL | Bus Coupler | - | GEMA | AEL Drawings | AEL Protection Database | Substation Photos
ALL | Cable | - | GEMA | AEL Drawings | General Cables Specifications | TIM Scada alarms report Rev 5
ALL | Circuit Breaker | - | GEMA | AEL Drawings | AEL Protection Database | Substation Photos
ALL | Fuse | - | GEMA
ALL | Link | - | GEMA
ALL | OH Line | - | GEMA | AEL Drawings | AEL OH Amp Calc.
ALL | Recloser | - | GEMA | AEL Protection Database
ALL | Regulator | - | GEMA | Equipment Name plate-GEMA | Equipment Name plate-Site Photos
ALL | RMU Switch | - | GEMA
ALL | Secionaliser | - | GEMA | AEL Protection Database | Equipment protection setting files
ALL | Switch | - | GEMA
ALL | Switchboard | - | GEMA | Tech 1
ALL | Transformer | - | GEMA | AEL Transformers Database
ABY | Circuit Breaker | Relay SEL 351S |  | TP Branch Report ABY.FDR.2722
ABY | Circuit Breaker | Relay SEL 351S |  | TP Branch Report ABY.FDR.2732
ABY | Circuit Breaker | Relay SEL 351S |  | TP Branch Report ABY.FDR.2742
ABY | Circuit Breaker | - |  | TP Branch Report ABY.TF.T2
BPD | Current Transformer | Other Equipment |  | TP Branch Report BDT.BPD.2
BPD | Disconnector | Disconnector |  | TP Branch Report BPD.DS.446
BPD | Disconnector | Disconnector |  | TP Branch Report BPD.DS.486
STU | Cable | - |  | TP Branch Report STU.TF.T5
STU | Cable | - |  | TP Branch Report STU.TF.T6
TIM | Cable | - |  | TP Branch Report TIM.FDR.2682
TIM | Cable | - |  | TP Branch Report TIM.TF.T3
TIM | Cable | - |  | TP Branch Report TIM.TF.T6
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2662
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2672
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2692
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2702
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2712
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2732
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2742
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2762
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2772
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2812
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2822
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2832
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2852
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2862
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2912
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2922
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2942
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2952
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2972
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2982
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.2992
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.3002
TIM | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TIM.FDR.3012
TIM | Transformer | LV Winding |  | TP Branch Report TIM.TF.T4
TKA | Cable | - |  | TP Branch Report TKA.TF.T1
TKA | OH Line | - |  | TP Branch Report ABY.TKA.1
TKA | Transformer | Tap Changer |  | TP Branch Report TKA.TF.T6
TMK | Bus | - |  | TP Branch Report TMK.TF.T2
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1192
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1202
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1212
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1222
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1262
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1272
TMK | Circuit Breaker | Relay SR760 |  | TP Branch Report TMK.FDR.1282
TMK | Circuit Breaker | Relay SEL 351S |  | TP Branch Report TMK.FDR.1292
TMK | OH Line | - |  | TP Branch Report TIM.TMK.1
TMK | OH Line | - |  | TP Branch Report TIM.TMK.2
TMK | Transformer | TapChanger |  | TP Branch Report TMK.TF.T1
TWZ | Circuit Breaker | - |  | TP Branch Report TWZ.FDR.6312
TWZ | Transformer | Transformer |  | TP Branch Report TWZ.TF.T18

## Summary
Stations | Limit 1 | 0 | 0 | 0 | 0 | Limit 2 | 0 | 0 | 0 | 0
| Start point | End Point | Description | Voltage | Rating | Start point | End Point | Description | Voltage | Rating
ABY Region
ABY_GXP | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB2712-Other Equipment | 11 | 11.4315 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 11 | 23.8157
ABY | F268 | C251 | OH Line-120 mm² Cu | 11 | 6.9161 | CB2722 | F268 | Cable-3-1c 400 mm² Al XLPE | 11 | 8.4356
CB2732_Raincliff | CB2732 | F234 SW.ST | Circuit Breaker-ABY-CB2732-Protection | 11 | 4.2868 | CB2732 | F234 SW.ST | OH Line-19/14 Cu | 11 | 4.6033
CB2742_Cave | CB2742 | Pole 53272 | Circuit Breaker-ABY-CB2742-Protection | 11 | 4.2868 | CB2742 | Pole 53272 | OH Line-DOG | 11 | 4.8938
CB2722_Fairlie | CB2722 | F388 | Circuit Breaker-ABY-CB2722-Protection | 11 | 8.5737 | F388 | OPU T-off | OH Line-PETREL | 33 | 9.879
FLE | OPU T-off | F377 | Circuit Breaker-FLE-F377-Protection | 11.1001 | 5.3833 | OPU T-off | F377 | Circuit Breaker-FLE-F323-Protection | 33 | 5.7158
F374_Cricklewood | F377 | Pole 11915 | OH Line-MINK | 11.1001 | 3.6265 | F377 | Pole 11915 | Circuit Breaker-FLE-F374-Protection | 11.1001 | 3.6914
F380_Fairlie Rural | F380 | Pole 15164 | Circuit Breaker-FLE-F380-Protection | 11.1001 | 3.6914 | F380 | Pole 15164 | OH Line-70 mm² Cu | 11.1001 | 4.7488
F383_Fairlie Township | F383 | Pole 15305 | Cable-1-3c 95 mm² AL PILC | 11.1001 | 3.2831 | F383 | Pole 15305 | Circuit Breaker-FLE-F383-Protection | 11.1001 | 3.6914
OPU | OPU T-off | F328 | Recloser -OPU-F400-Protection | 33 | 8.5737 | OPU T-off | F328 | OH Line-70 mm² Cu | 33 | 14.1179
| 7 | 8 | 9 | 10 | 11 | 7 | 8 | 9 | 10 | 11
BPD Region
BPD_GXP | 110 kV Bus | DS486 | Circuit Breaker-BPD-T2-CB482-Protection | 110 | 27.8167 | 110 kV Bus | 11 kV Bus | Current Transformer-BPD-T2-CB482-Other Equipment | 110 | 34.2946
BPD | 110 kV Bus | 11 kV Bus | Cable-6 1c 400mm2 Al XLPE | 11.22 | 17.4902 | 110 kV Bus | 11 kV Bus | Circuit Breaker-BPD-T2-CB36-Protection | 11.22 | 21.377
CB11_Waihao Downs | W614 LK | W624 RMU | Cable - 3c 95mm2 Al XLPE CWS HDPE | 11.22 | 4.6582 | JAGUAR OH Line | Cable 95 mm2 | Link - W614 | 11.22 | 5.8301
CB12_Ikawai | BPD12 CB | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22 | 6.5909 | W451 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22 | 7.5194
CB13_Waikakahi | BPD13 CB | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22 | 6.5909 | W452 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22 | 7.5194
CB1_Waihuna | W636 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22 | 7.5194 | Cable Joint | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22 | 7.6371
CB2_Tawai | W453 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22 | 7.5194 | Cable Joint | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22 | 7.6371
CB522_CNR | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CB3602_CNR | DS3604 | CB3602 | Circuit Breaker-BPD-T1-CB3602-Protection | 33 | 28.1216 | 33 kV Terminal | 3604 ABS | Air Break Switch-3604 ABS | 33 | 45.7261
CNR | CNR642 | 11 kV Bus | Circuit Breaker-CNR-CB35-Protection | 11 | 21.034 | CNR642 | 11 kV Bus | Cable-2x3x1c 630mm2 Al XLPE HDPE | 11 | 21.6361
CB8_Drier 2 | Joint | Y815 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11 | 7.2192 | 11 kV Bus | CNR-CB8 | Circuit Breaker-CNR-CB8-Protection | 11 | 7.6591
CB9_WetProcess | Joint | Y900 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11 | 7.5199 | 11 kV Bus | CNR-CB9 | Circuit Breaker-CNR-CB9-Protection | 11 | 7.6591
CB11_Boiler/Chiller 1 | Joint | Y1100 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11 | 7.2192 | 11 kV Bus | CNR-CB11 | Circuit Breaker-CNR-CB11-Protection | 11 | 7.6591
CB12_Office | Joint | Y1200 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11 | 7.5199 | 11 kV Bus | CNR-CB12 | Circuit Breaker-CNR-CB12-Protection | 11 | 7.6591
STU Region
STU_GXP | 110 kV Bus | 11 kV Bus | Transformer-T5-Tap Changer | 11.198 | 11.6373 | 110 kV Bus | 11 kV Bus | Cable-STU-CBL-2812-Cable | 11.198 | 12.8398
CB1_Otaio | STU-1 | Pole 31678 | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454 | 11 kV Bus | STU-1 | Circuit Breaker-STU-CB1-Protection | 11.198 | 6.9824
CB2_Glenavy | 11 kV Bus | STU-2 | Circuit Breaker-STU-CB2-Protection | 11.198 | 5.8187 | STU-2 | W405 ABS | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454
CB3_Waimate | 11 kV Bus | STD-3 | Circuit Breaker-STU-CB3-Protection | 11.198 | 5.8187 | STU-3 | W400 ABS | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454
CB7_Waihaorunga | STU-7 | W406 | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454 | 11 kV Bus | STD-7 | Circuit Breaker-STU-CB7-Protection | 11.198 | 6.9824
CB8_Mt Studholme | W200 ABS | A1103 TX | OH Line-70mm² Cu | 11.198 | 4.7907 | STU-8 | Pole 31677 | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454
CB9_Morven | 11 kV Bus | STD-9 | Circuit Breaker-STU-CB9-Protection | 11.198 | 5.8187 | STU-9 | Pole 31989 | Cable-3c-300mm² AL XLPE HDPE | 11.198 | 6.8454
TKA Region
TKA_GXP | CB32 | DS1046 | Circuit Breaker-TKA-CB1042-Protection | 33 | 10.4599 | CB32 | DS1046 | Circuit Breaker-TKA-CB32-Protection | 11 | 12.0031
TEK | M11 T-off | 11 kV Bus | Circuit Breaker-TEK-M202-Protection | 11 | 7.621 | M11 T-off | 11 kV Bus | OH Line-IODINE | 11 | 7.7901
M200_Haldon_Lilybank | 11 kV Bus | M194 | Cable-1-3c 150 mm² Al PILC | 11 | 3.5556 | M194 | Pole 14140 | OH Line-MINK | 11 | 3.5938
M201_Simons | M175 | Pole 25260 | OH Line-HERRING | 11 | 1.4044 | 11 kV Bus | M175 | Cable-1-3c 150 mm² Al PILC | 11 | 3.5556
M204_Lakeside_Drive | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | 0
M205_Godley | M186 | M296 | OH Line-HERRING | 11 | 1.4044 | 11 kV Bus | M184 | Circuit Breaker-TEK-M205-Protection | 11 | 1.9053
M206_Tekapo Township | 11 kV Bus | M180 | Cable-1-3c 150 mm² Al PILC | 11 | 3.5556 | M180 | Pole 14122 | OH Line-MINK | 11 | 3.5938
HLB | Pole 14150 | TX E117 | Recloser-M82-Protection | 11 | 1.1432 | M193 | Pole 14149 | OH Line-HERRING | 11 | 1.4044
M32_Lilybank | M32 | TX E58 | OH Line-HERRING | 22 | 2.8087 | Pole 51596 | M32 | OH Line-MINK | 22 | 7.1876
M33_Haldon | M33 | Pole 24654 | OH Line-HERRING | 22 | 2.8087 | Pole 51596 | M33 | OH Line-MINK | 22 | 7.1876
OMR | M175 | Pole 25260 | OH Line-HERRING | 11 | 1.4044 | M329 | M339 | Recloser-M331-Protection | 11 | 2.2863
M338_Old Man Range | M335 | Pole 51625 | Recloser-OMR-M338-Protection | 22 | 2.2863 | M335 | Pole 51625 | OH Line-HERRING | 22 | 2.8087
TKA_M11 | M11 T-off | Pole 18992 | Recloser - TKA_M11-M346 - Protection | 33 | 8.5737 | M11 T-off | Pole 18992 | OH Line - 3-70mm2 Cu | 33 | 14.1179
SBT_33kV | CB1042 | DS1046 | Circuit Breaker-TKA-CB1042-Protection | 33 | 10.4599 | M55 | Pole 24021 | OH Line-19/14 Cu | 33 | 13.8322
UHT | M303 | M301 | Circuit Breaker-UHT-M302-Protection | 33 | 2.8579 | M271 | M54 | Secionaliser-M272-Protection | 33 | 4.5726
M158_Village | M158 | M148 | Circuit Breaker-UHT-M158-Protection | 11 | 1.9053 | M158 | M148 | Cable-1-3c 150 mm² Al PILC | 11 | 4.9479
M159_Village | M159 | M160 | Circuit Breaker-UHT-M159-Protection | 11 | 1.9053 | M159 | M160 | Cable-1-3c 150 mm² Al PILC | 11 | 4.9479
TMK Region
TMK_GXP | DS134 | 33 kV Bus | Circuit Breaker-TMK-CB1252-Protection | 33.594 | 28.8605 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-TapChanger | 110 | 57.1577
CB1292_Geraldine | 33 kV Bus | G217 | OH Line-DOG | 33.594 | 14.9457 | 33 kV Bus | G217 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 20.3209
CB1282_Clandeboye No.4 | 33 kV Bus | CBT663 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 23.6932 | REC T663 | 11 kV Bus | Recloser-T663-Protection | 33.594 | 31.4207
CB1272_Clandeboye No.2 | Pole 02049 | Pole 02052 | OH Line-WOLF | 33.594 | 28.864 | 33 kV Bus | CD1-D1246-T2 | Circuit Breaker-TMK-CB1272-Protection | 33.594 | 29.6751
CB1262_Temuka No.2 | 33 kV Bus | TMK-D816-T2 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 24.8067 | 33 kV Bus | TMK-D816-T2 | Circuit Breaker-TMK-CB1262-Protection | 33.594 | 33.8646
CB1222_Clandeboye No.3 | Pole 02081 | CBT662 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 23.6932 | Pole 02049 | Pole 02053 | OH Line-WOLF | 33.594 | 28.864
CB1212_Temuka No.1 | 33 kV Bus | TMK-D816-T1 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 24.8067 | 33 kV Bus | TMK-D816-T1 | Circuit Breaker-TMK-CB1212-Protection | 33.594 | 33.8646
CB1202_Rangitata | T557 | G127 | Cable-1-3c 95 mm² Al XLPE | 33.594 | 12.058 | T557 | G127 | OH Line-DOG | 33.594 | 14.9457
CB1192_Clandeboye No.1 | 33 kV Bus | Pole 02081 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 23.6932 | 33 kV Bus | CD1-D1246-T1 | Circuit Breaker-TMK-CB1192-Protection | 33.594 | 29.6751
TMK | TMK-D816-T1 | 11 kV Bus | Cable-6-1c 500 mm² Cu XLPE | 11 | 19.8525 | TMK-D816-T1 | 11 kV Bus | Circuit Breaker-TMK-CB4-Protection | 11 | 20.5768
CB1_Temuka West | 11 kV Bus | T200 | Cable-1-3c 300 mm² Al XLPE HD | 11 | 4.9407 | T200 | T201 | OH Line-CHAFER | 11 | 7.3944
CB2_Milford | 11 kV Bus | T500 | Cable-1-3c 150 mm² Al PILC | 11 | 3.0371 | T500 | T120 | OH Line-DOG | 11 | 4.8938
CB3_Winchester | Pole 47049 | T548 | Link-T546 | 11 | 5.7158 | Pole 47049 | T548 | OH Line-JAGUAR | 11 | 7.372
CB7_Rangitata | Pole 47048 | T549 | Link-T547 | 11 | 5.7158 | Pole 47048 | T549 | OH Line-JAGUAR | 11 | 7.372
CB8_Temuka East | T102 | Pole 36752 | OH Line-7/0.136 Cu | 11 | 4.5917 | 11 kV Bus | T101 | Cable-1-3c 300 mm² Al PILC | 11 | 6.1372
CB9_Waitohi | T300 | Pole 36779 | OH Line-19/16 Cu | 11 | 3.3533 | 11 kV Bus | T300 | Cable-1-3c 240 mm² Al PILC | 11 | 5.6816
GLD | G217 | G222 | Circuit Breaker-GLD-G260-Protection | 11.055 | 12.0631 | 33 kV Bus | G217 | OH Line-DOG | 33.594 | 14.9457
G194_Speechly | G222 | Pole 03224 | OH Line-MINK | 11.055 | 3.6118 | G195 | G318 | OH Line - 70mm2 - | 11.055 | 4.7295
G191_Geraldine Township | G192 | G320 | OH Line-7/0.136 Cu | 11.055 | 4.6146 | G320 | G278 | OH Line - 70mm2 | 11.055 | 4.7295
G156_Woodbury | G222 | G277 | OH Line-7/0.136 Cu | 11.055 | 4.6146 | G222 | G277 | Link-G277 | 11.055 | 5.7443
RGA_T1 | Pole 02052 | CB1416 | AEL-Fonterra Contractual-10 MW Limit | 33.594 | 10 | ABS1524 | CB35 | Cable-3-1c 630 mm² Cu XLPE | 11.22 | 15.4264
CB2_Arundel | T595 | Pole 05969 | OH Line-DOG | 11.22 | 4.9917 | CB2 | T595 | Cable-1-3c 185 mm² XLPE | 11.22 | 5.2589
CB3_Mahan Road | CB3 | TX43 | Cable-1-3c 95 mm² XLPE | 11.22 | 4.0457 | TX43 | Pole 48705 | OH Line-DOG | 11.22 | 4.9917
CB4_Main South Road | CB4 | T703 | OH Line-DOG | 11.22 | 4.9917 | CB4 | T703 | Cable-1-3c 185 mm² XLPE | 11.22 | 5.2589
RGA_T2 | T557 | G127 | Cable-1-3c 95 mm² Al XLPE | 33.594 | 12.058 | T557 | G127 | OH Line-DOG | 33.594 | 14.9457
CB11_Belfield | T587 | Pole 808827 | OH Line-IODINE | 11.22 | 5.3518 | CB11 | T587 | Circuit Breaker-RGA_T2-CB11-Protection | 11.22 | 5.8301
CB12_Orton | T590 | Pole 46673 | OH Line-IODINE | 11.22 | 5.3518 | CB12 | T590 | Circuit Breaker-RGA_T2-CB12-Protection | 11.22 | 5.8301
CB13_Rangitata Island | T435 | T596 | OH Line-DOG | 11.22 | 4.9917 | CB13 | T435 | Cable-1-3c 185 mm² XLPE | 11.22 | 5.2589
CD_1 | Recloser T615 | 11 kV Bus | Cable-3-1c 300 mm² Al XLPE | 33.594 | 20.2319 | Recloser T615 | 11 kV Bus | Circuit Breaker-CD1-T606-Protection | 11 | 22.8631
T600_Tie to Milk Powder 2 | 11 kV Bus | T465 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.7761 | 11 kV Bus | T465 | Circuit Breaker-CD1-T600-Protection | 11 | 7.621
T601_Fire Services | 11 kV Bus | T256 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.7761 | 11 kV Bus | T256 | Circuit Breaker-CD1-T601 | 11 | 7.621
T602_Whey Processing | 11 kV Bus | T172 | Cable-1-3c 185 mm² Al PILC | 11 | 4.5641 | 11 kV Bus | T172 | Circuit Breaker-CD1-T602 | 11 | 7.621
T603_Lactose Plant | 11 kV Bus | T569 | Cable-3-1c 400 mm² Al XLPE | 11 | 6.5163 | 11 kV Bus | T569 | Circuit Breaker-CD1-T603 | 11 | 7.621
T605_Tie to Milford | 11 kV Bus | T166 | Cable-1-3c 95 mm² Al PILC | 11 | 2.3391 | 11 kV Bus | T166 | Circuit Breaker-CD1-T605 | 11 | 4.8012
T609_Milk Reception | 11 kV Bus | T153 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.7761 | 11 kV Bus | T153 | Circuit Breaker-CD1-T609 | 11 | 7.621
T610_Chilled Water 1 | 11 kV Bus | T249 | Cable-1-3c 185 mm² Al PILC | 11 | 3.423 | 11 kV Bus | T249 | Circuit Breaker-CD1-T610 | 11 | 7.621
T611_Effluent Plant | 11 kV Bus | T246 | Cable-1-3c 185 mm² Al PILC | 11 | 3.423 | 11 kV Bus | T246 | Circuit Breaker-CD1-T611 | 11 | 7.621
T612_Milk Treatment | 11 kV Bus | T139 | Cable-1-3c 95 mm² Al PILC | 11 | 2.3391 | 11 kV Bus | T139 | Circuit Breaker-CD1-T612 | 11 | 7.621
T613_Rolleston Rd | 11 kV Bus | T131 | Cable-1-3c 185 mm² Al PILC | 11 | 3.423 | T131 | Pole 51393 | OH Line-MINK | 11 | 3.5938
T614_Tie to Powder Handling | 11 kV Bus | T580 | Cable-1-3c 300 mm² Al XLPE | 11 | 6.1209 | 11 kV Bus | T580 | Circuit Breaker-CD1-T614 | 11 | 7.621
CD_2 | Pole 02081 | CBT662 | Cable-3-1c 400 mm² Al XLPE | 33.594 | 23.6932 | REC T662 | 11 kV Bus | Circuit Breaker-CD2-T657-Protection | 11 | 26.6736
T650_Tie to Milk Powder 1 | 11 kV Bus | T278 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.4312 | #N/A | #N/A | #N/A | #N/A | 9.1452
T651_Milk Powder 3 | 11 kV Bus | T364 | Cable-1-3c 300 mm² Al XLPE | 11 | 6.2933 | 11 kV Bus | T364 | Circuit Breaker-CD2-T651-Protection | 11 | 9.1452
T652_Tie to WPC | 11 kV Bus | T379 | Cable-1-3c 185 mm² XLPE | 11 | 4.1875 | 11 kV Bus | T379 | Cable-1-3c 185 mm² Al PILC | 11 | 4.6184
T653_Chilled Water 3 | 11 kV Bus | T373 | Cable-1-3c 300 mm² Al XLPE | 11 | 6.0347 | 11 kV Bus | T373 | Circuit Breaker-CD2-T653-Protection | 11 | 9.1452
T654_Tie to Boiler House | 11 kV Bus | T670 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.8909 | 11 kV Bus | T670 | Cable-3-1c 400 mm² Al XLPE | 11 | 7.7975
T658_Milk Powder 2 | 11 kV Bus | T482 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.4312 | 11 kV Bus | T482 | Circuit Breaker-CD2-T658-Protection | 11 | 9.1452
T659_Tie to Energy Centre 1 | 11 kV Bus | T383 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.8308 | 11 kV Bus | T383 | Circuit Breaker-CD2-T659-Protection | 11 | 9.1452
T660_Refrigeration | 11 kV Bus | T338 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.4312 | 11 kV Bus | T338 | Circuit Breaker-CD2-T660-Protection | 11 | 9.1452
T661_Laboratory | 11 kV Bus | T182 | Cable-1-3c 300 mm² Al XLPE | 11 | 5.4312 | 11 kV Bus | T182 | Circuit Breaker-CD2-T661-Protection | 11 | 9.1452
CB2_Mozz3_1 | 11 kV Bus | T708 | Circuit Breaker-CD2-CB2-Protection | 11 | 11.4315 | 11 kV Bus | T708 | RMU Switch-T708 | 11 | 12.0031
CB15_Mozz3_2 | 11 kV Bus | T737 | Circuit Breaker-CD2-CB15-Protection | 11 | 11.4315 | 11 kV Bus | T737 | RMU Switch-T737 | 11 | 12.0031
TIM Region
TIM_GXP | 110 kV Bus | 11 kV Bus | Circuit Breaker-TIM-CB2752-Protection | 11 | 29.4172 | 110 kV Bus | 11 kV Bus | Tap Changer-TIM.TF.T3-Tap Changer | 110 | 47.6314
TIM_NST_SUBTRANS | CB2692 | NST35 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11 | 15.3614 | 11 kV Bus | CB2692 | Circuit Breaker-TIM-CB2692-Protection | 11 | 22.5582
TIM_GRM_SUBTRANS | Joint | TEGRASMERE19 | Cable-3c 400mm² Cu PILC SWA | 11 | 7.8604 | 11 kV Bus | CB2812 | Circuit Breaker-TIM-CB2812-Protection | 11 | 10.4789
TIM_WSS_SUBTRANS | 11 kV Bus | CB2662 | Circuit Breaker-TIM-CB2662-Protection | 11 | 7.621 | #N/A | #N/A | #N/A | #N/A | 0
CB2682_Showgrounds Hill | CB2682 | L1080 | Cable-3x 1c 400mm2 Al XLPE HDPE | 11 | 6.5731 | 11 kV Bus | CB2682 | Circuit Breaker-TIM-CB2682-Protection | 11 | 7.621
CB2692_North ST.1 | CB2692 | NST35 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11 | 15.3614 | 11 kV Bus | CB2692 | Circuit Breaker-TIM-CB2692-Protection | 11 | 22.5582
CB2702_Morgans Rd | Pole 35233 | Joint | Cable-3c 150mm² Al PILC STA | 11 | 3.5825 | Pole 35185 | Pole 35229 | Cable-3c 185mm² Al XLPE HDPE | 11 | 4.9614
CB2712_Mountain View Rd | Joint | ABS L978 | Cable-3c 300mm² Al XLPE MDPE | 11 | 7.02 | 11 kV Bus | CB2712 | Circuit Breaker-TIM-CB2712-Protection | 11 | 7.621
CB2732_ATM_T1 | 11 kV Bus | CB2732 | Circuit Breaker-TIM-CB2732-Protection | 11 | 20.3481 | CB2732 | B774/T1 | Cable-2 x 3/1c 630mm² Cu | 11 | 21.3492
CB2742_Levels Plain | Joint | ABS L767 | Cable-3c 300mm² Al XLPE MDPE | 11 | 7.5161 | 11 kV Bus | CB2742 | Circuit Breaker-TIM-CB2742-Protection | 11 | 7.621
CB2762_AEL Yard | Joint | ABS L516 | Cable-3c 240mm² AL PILC STA | 11 | 5.3353 | CB2762 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11 | 7.558
CB2832_Grants Rd | Joint | L773 | Cable-3c 240mm² AL PILC STA | 11 | 5.3353 | 11 kV Bus | CB2832 | Circuit Breaker-TIM-CB2832-Protection | 11 | 7.621
CB2852_Hadlow | Pole 25185 | Pole 35228 | Cable-3c 185mm² Al XLPE HDPE | 11 | 4.9614 | CB2852 | L800 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11 | 7.3388
CB2862_Meadows Rd | Joint | RMU L420 | Cable-3c 300mm² Al XLPE HDPE | 11 | 7.5161 | 11 kV Bus | CB2862 | Circuit Breaker-TIM-CB2862-Protection | 11 | 7.621
CB2922_ATM_T2 | 11 kV Bus | CB2922 | Circuit Breaker-TIM-CB2922-Protection | 11 | 20.3481 | CB2922 | B774/T2 | Cable-2 x 3/1c 630mm² Cu | 11 | 21.3492
CB2942_Old North Rd | Joint | L462 | Cable-3c 0.4in² Al PILC SWA | 11 | 5.3501 | 11 kV Bus | CB2942 | Circuit Breaker-TIM-CB2942-Protection | 11 | 7.621
CB2952_Highfield | Joint | RMU L549 | Cable-3c 240mm² Al PILC STA | 11 | 5.3353 | 11 kV Bus | CB2952 | Circuit Breaker-TIM-CB2952-Protection | 11 | 7.621
CB2972_Smithfield | Joint | L461 | Cable-3c 0.4in² Al PILC SWA | 11 | 5.3501 | 11 kV Bus | CB2972 | Circuit Breaker-TIM-CB-2972-Relay SEL 351S | 11 | 6.9732
CB2982_North ST.2 | CB2982 | NST36 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11 | 15.3614 | 11 kV Bus | CB2982 | Circuit Breaker-TIM-CB2982-Protection | 11 | 22.5582
CB2992_Goulds Road | CB2992 | L1075 | Cable-TIM-CB2992 | 11 | 6.5731 | 11 kV Bus | CB2992 | Circuit Breaker-TIM-CB2992-Protection | 11 | 7.621
GRM | 11 kV Bus | 11 kV Bus | Switchboard - 11 kV Switchboard | 11 | 57.1577 | #N/A | #N/A | #N/A | #N/A | 0
GRM_HNT_SUBTRANS | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11 | 5.6675 | 11 kV Bus | TEGRASMERE4 | Circuit Breaker-GRM-CB4-Protection | 11 | 7.621
GRM_NST_SUBTRANS | Joint | Joint | Cable-3c 0.3in² Cu PILC STAS | 11 | 5.6675 | Grasmere | NST6 | Circuit Breaker-NST-CB6-Protection | 11 | 7.621
CB2_White St | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11 | 3.0598 | Joint | TE64 | Cable-3c 185mm² Al PILC HDPE | 11 | 3.6634
CB4_GRM-HNT A | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11 | 5.6675 | 11 kV Bus | TEGRASMERE4 | Circuit Breaker-GRM-CB4-Protection | 11 | 7.621
CB5_Nile St | TEGRASMERE5 | TEE1 RMU | Cable-3c 300mm² Al PILC SWAS | 11 | 4.4472 | 11 kV Bus | TEGRASMERE5 | Circuit Breaker-GRM-CB5-Protection | 11 | 5.792
CB6_Parkview Terrace | TEGRASMERE6 | TER1RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 4.344 | 11 kV Bus | TEGRASMERE6 | Circuit Breaker-GRM-CB6-Protection | 11 | 5.792
CB7_Douglas St | Joint | TEF13 RMU | Cable-3c 185mm² Al XLPE HDPE | 11 | 4.4946 | Joint | Joint | Cable-3c 300mm² Al PILC SWAS | 11 | 5.3648
CB9_GRM-NST A | Joint | Joint | Cable-3c 0.3in² Cu PILC STAS | 11 | 5.6675 | 11 kV Bus | TEGRASMERE9 | Circuit Breaker-GRM-CB9-Protection | 11 | 7.621
CB10_Ashbury Park | Joint | Joint | Cable-3c 0.25in² Al PILC STAS | 11 | 3.8372 | Joint | TEM1 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 4.344
CB12_Selwyn St | Joint | TEL6 RMU | Cable-3c 300mm² Al PILC | 11 | 3.3553 | TEGRASMERE12 | Joint | Cable-3c 300mm² Al XLPE PVC | 11 | 4.2736
CB13_GRM-HNT B | Joint | TEHUNT12 | Cable-3c 0.3in² Cu PILC STAS | 11 | 5.6675 | 11 kV Bus | TEGRASMERE13 | Circuit Breaker-GRM-CB13-Protection | 11 | 7.621
CB15_Park Lane | TEGRASMERE15 | TEE28 RMU | Cable-3c 300mm² Al PILC SWA | 11 | 3.2888 | 11 kV Bus | TEGRASMERE15 | Circuit Breaker-GRM-CB15-Protection | 11 | 5.792
CB16_Evans St | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11 | 3.2001 | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11 | 3.8372
CB17_June St | Joint | TEF10 RMU | Cable-3c 0.4in² Al PILC SWA | 11 | 4.4309 | 11 kV Bus | TEGRASMERE17 | Circuit Breaker-GRM-CB17-Protection | 11 | 5.792
CB18_GRM-NST B | Joint | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11 | 5.6675 | 11 kV Bus | TEGRASMERE18 | Circuit Breaker-GRM-CB18-Protection | 11 | 7.621
CB20_Hobbs St | TEGRASMERE20 | TEM7 RMU | Cable-3c 0.4in² Al PILC DSTA | 11 | 3.8635 | 11 kV Bus | TEGRASMERE20 | Circuit Breaker-GRM-CB20-Protection | 11 | 5.792
NST | CB2692 | NST35 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11 | 15.3614 | 11 kV Bus | CB2692 | Circuit Breaker-TIM-CB2692-Protection | 11 | 22.5582
CB3_Redruth 1 | Joint | L748 RMU | Cable-3/1c 300mm² Al CWS | 11 | 5.2076 | 11 kV Bus | NST03 | Circuit Breaker-NST-CB3-Protection | 11 | 5.792
CB4_Rose St | Joint | TEQ21 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 4.3531 | 11 kV Bus | NST04 | Circuit Breaker-NST-CB4-Protection | 11 | 5.792
CB5_Craigie Ave | Joint | TEQ25 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 3.8471 | 11 kV Bus | NST05 | Circuit Breaker-NST-CB5-Protection | 11 | 5.792
CB8_Barnard St | Joint | TEW1 | Cable-3c 0.15in² Cu PILC STA | 11 | 3.287 | 11 kV Bus | NST08 | Circuit Breaker-NST-CB8-Protection | 11 | 3.8105
CB9_Port 1 | Joint | TEX47 RMU | Cable-3c 300mm² Al XLPE MDPE | 11 | 5.2076 | 11 kV Bus | NST09 | Circuit Breaker-NST-CB9-Protection | 11 | 5.792
CB10_Fraser St | Joint | TEW33 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 3.806 | 11 kV Bus | NST10 | Circuit Breaker-NST-CB10-Protection | 11 | 5.792
CB11_Hayes St | Joint | TEW7 RMU | Cable-3c 0.25in² Al PILC STAS | 11 | 3.9414 | 11 kV Bus | NST11 | Circuit Breaker-NST-CB11-Protection | 11 | 5.792
CB12_High St | Joint | Joint | Cable-3c 0.25in² Al PILC SWA | 11 | 3.9414 | Joint | Joint | Cable-3c 185mm² Al PILC SWA | 11 | 4.6851
CB13_Port 2 | Joint | TEX50 RMU | Cable-3c 300mm² Al XLPE MDPE | 11 | 5.2076 | 11 kV Bus | NST13 | Circuit Breaker-NST-CB13-Protection | 11 | 5.792
CB16_Victoria St | Joint | TEP12 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 3.9994 | 11 kV Bus | NST16 | Circuit Breaker-NST-CB16-Protection | 11 | 5.792
CB17_Stafford St | Joint | Joint | Cable-3c 0.075in² Cu PILC STAS | 11 | 2.5879 | Joint | Joint | Cable-3c 0.15in² Cu PILC SWA | 11 | 3.287
CB18_Redruth 2 | Joint | L783 RMU | Cable-3c 300mm² Al XLPE CWS MDPE | 11 | 5.2076 | 11 kV Bus | NST18 | Circuit Breaker-NST-CB18-Protection | 11 | 5.792
HNT | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11 | 5.6675 | 11 kV Bus | TEGRASMERE4 | Circuit Breaker-GRM-CB4-Protection | 11 | 7.621
CB1_Harper St | 11 kV Bus | TEHUNT1 | Circuit Breaker-HNT-CB1-Protection | 11 | 3.8105 | TEHUNT1 | TEJ17 | Cable-3c 185mm² Al PILC SWAS | 11 | 4.2761
CB2_Wilson St | TED18 | POLE 45041 | OH Line-GOPHER | 11 | 2.1035 | 11 kV Bus | TEHUNT2 | Circuit Breaker-HNT-CB2-Protection | 11 | 3.8105
CB3_HNT-GRM A | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11 | 5.6675 | 11 kV Bus | TEGRASMERE 4 | Circuit Breaker-HNT-CB3-Protection | 11 | 7.621
CB4_Baker St | 11 kV Bus | TEHUNT4 | Circuit Breaker-HNT-CB4-Protection | 11 | 3.8105 | Joint | TED5 | Cable-3c 0.25in² Al PILC DSTA | 11 | 3.9878
CB5_Le Cren St | Joint | TEK9 RMU | Cable-3c 0.25in² Al PILC SWA | 11 | 3.4583 | 11 kV Bus | TEHUNT5 | Circuit Breaker-HNT-CB5-Protection | 11 | 3.8105
CB6_HNT-NST A | TEHUNT6 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11 | 5.5589 | Joint | NST07 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11 | 7.5813
HNT_NST_SUBTRANS | TEHUNT6 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11 | 5.5589 | Joint | NST07 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11 | 7.5813
CB7_Church St SS | Joint | TEJ4 | Cable-3c 0.15in² Al PILC STAS | 11 | 3.0574 | 11 kV Bus | TEHUNT7 | Circuit Breaker-HNT-CB7-Protection | 11 | 3.8105
CB10_Gibson St | 11 kV Bus | TEHUNT10 | Circuit Breaker-HNT-CB10-Protection | 11 | 3.8105 | TEHUNT10 | TEJ8 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 3.991
CB11_Rhodes St | Joint | TEJ7 Link | Cable-3c 185mm² Al PILC SWAS | 11 | 3.155 | 11 kV Bus | TEHUNT11 | Circuit Breaker-HNT-CB11-Protection | 11 | 3.8105
CB12_HNT-GRM B | Joint | TEHUNT12 | Cable-3c 0.3in² Cu PILC STAS | 11 | 5.6675 | TEGRASMERE13 | TEHUNT12 | Circuit Breaker-HNT-CB12-Protection | 11 | 7.621
CB13_Clifton Terrace | 11 kV Bus | TEHUNT13 | Circuit Breaker-HNT-CB13-Protection | 11 | 3.8105 | TEHUNT13 | TE62 | Cable-3c 185mm² Al PILC SWAS | 11 | 3.877
CB14_Church St NS | Joint | TER8 RMU | Cable-3c 95mm² AL PILC SWAS | 11 | 2.9991 | 11 kV Bus | TEHUNT14 | Circuit Breaker-HNT-CB14-Protection | 11 | 3.8105
CB15_HNT-NST B | TEHUNT15 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11 | 5.5589 | 11 kV Bus | TEHUNT15 | Circuit Breaker-HNT-CB15-Protection | 11 | 7.621
HNT_NST_SUBTRANS | TEHUNT6 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11 | 5.5589 | Joint | NST07 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11 | 7.5813
CB16_Arthur St | 11 kV Bus | TEHUNT16 | Circuit Breaker-HNT-CB16-Protection | 11 | 3.8105 | TEHUNT16 | TEJ16 RMU | Cable-3c 185mm² Al PILC SWAS | 11 | 4.2761
ATM | 33 kV Bus | CB L413 | Circuit Breaker-ATM-L413-Protection | 33 | 13.7178 | 11 kV Bus | CB2732 | Circuit Breaker-TIM-CB2732-Protection | 11 | 20.3481
L413_L418_Pareora | Pole 03576 | Pole 51637 | OH Line-MINK | 33 | 10.7815 | Pole 01408 | Pole 01401 | OH Line-QUAIL | 33 | 11.2147
WSS | 11 kV Bus | CB2662 | Circuit Breaker-TIM-CB2662-Protection | 11 | 7.621 | #N/A | #N/A | #N/A | #N/A | 0
CB2662_Waipopo | Joint | Joint | Cable - 3c 240mm² AL PILC | 11 | 5.264 | L905 | Joint | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11 | 7.1971
CB2672_Washdyke | L912 | LX25 | Cable - 3c 240mm² AL PILC | 11 | 5.264 | LX25 | B1110 | OH Line - Weke | 11 | 5.2776
CB3002_Elginshire | Joint | B1541 | Cable - 3c 240mm² AL PILC | 11 | 4.4965 | Joint | L868 | Cable - 3c 300mm² AL XLPE HDPE Screened | 11 | 7.2628
CB3012_Arowhenua | Joint | L357 | Cable - 3c 150mm² Al PILC STA | 11 | 3.7612 | Joint | L873 | Cable - 3c 300mm² AL XLPE HDPE Screened | 11 | 6.7561
PAR | 33 kV Bus | 11 kV Bus | Cable-2 x 3/1c 400mm² AL XLPE HDPE Screened | 11.22 | 16.4991 | 33 kV Bus | 11 kV Bus | Cable-2 x 3/1c 400mm² AL XLPE HDPE Screened | 11.22 | 16.8038
CB3_Works No. 1 | 11 kV Bus | PAR3 | Circuit Breaker-PAR-CB3-Protection | 11.22 | 5.8301 | PAR3 | No.1 RMU | Cable-3c 240mm² AL PILC DSTA | 11.22 | 5.8598
CB4_St Andrews | 11 kV Bus | PAR4 | Circuit Breaker-PAR-CB4-Protection | 11.22 | 4.8973 | L572 Link | L570 ABS | OH Line-DOG | 11.22 | 4.9917
CB5_Works No. 2 | 11 kV Bus | PAR5 | Circuit Breaker-PAR-CB5-Protection | 11.22 | 5.8301 | PAR5 | No.2 RMU | Cable-3c 240mm² AL PILC DSTA | 11.22 | 5.8598
CB6_Normanby | Link L179 | Pole 36354 | OH Line-RANGO | 11.22 | 3.9652 | 11 kV Bus | PAR6 | Circuit Breaker-PAR-CB6-Protection | 11.22 | 4.8973
CB7_Holmestation | L571 | Pole 43326 | OH Line-MINK | 11.22 | 3.6657 | 11 kV Bus | PAR7 | Circuit Breaker-PAR-CB7-Protection | 11.22 | 4.8973
ATM_2 | 33 kV Bus | CB L418 | Circuit Breaker-ATM-L418-Protection | 33 | 13.7178 | 11 kV Bus | CB2922 | Circuit Breaker-TIM-CB2922-Protection | 11 | 20.3481
L269_PleasantPoint | L247 ABS | L994 ABS | Cable-3/1c 95mm² AL XLPE PVC screened | 33 | 9.7996 | CB L269 | Pole 872745 | OH Line-QUAIL | 33 | 11.2147
PLP | 33 kV Bus | 11 kV Bus | Circuit Breaker-PLP-CB3-Protection | 11.22 | 6.7629 | 33 kV Bus | 11 kV Bus | OH Line-70mm² Cu | 11.22 | 7.035
CB1_Waitawa | 0 | Fuse L260 | OH Line-Ferret | 11.22 | 2.8762 | PLPTCB 1 | Joint | Cable-3c 150mm² Al PILC STA | 11.22 | 3.8869
CB2_Sutherlands | PLPTCB 2 | Link L254 | Cable-3c 150mm² Al PILC STA | 11.22 | 3.8869 | Link L254 | 0 | OH Line-7/10 Cu | 11.22 | 4.1782
CB4_Totara Valley | Link L262 | B1088 | OH Line-Mink | 11.22 | 3.673 | PLPTCB 4 | Link L262 | Cable-3c 150mm² Al PILC STA | 11.22 | 3.8869
CB5_Pleasant Point Township | Link L263 | 0 | OH line-7/14 Cu | 11.22 | 2.5458 | Joint | Link L263 | Cable-3 x 1c 185mm² Al XLPE | 11.22 | 3.5935
TWZ Region
TWZ_GXP | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Other Equipment | 33 | 6.8589 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Protection | 33 | 14.4037
TVS | Z69 | 11 kV Bus | Cable-3-1c 400 mm² AL XLPE | 11 | 6.2523 | Z69 | 11 kV Bus | Circuit Breaker-TVS-Z68-Protection | 33 | 8.5737
Z1_Urban No. 1 | 11 kV Bus | Z110 | Circuit Breaker-TVS-Z1-Protection | 11 | 2.896 | 11 kV Bus | Z110 | OH Line - MINK | 11 | 3.6009
Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | Circuit Breaker-TVS-Z2-Protection | 11 | 2.896 | 11 kV Bus | Pole 12571 | OH Line-MINK | 11 | 3.6009
Z3_Industrial | 11 kV Bus | E48 | Cable-1-3c 35 mm² AL PILC | 11 | 1.6269 | 11 kV Bus | E48 | Cable-1-3c 0.0225 in² Cu PILC | 11 | 1.8862
Z4_Twizel Rural | 11 kV Bus | Z401 | Circuit Breaker-TVS-Z4-Protection | 11 | 2.896 | 11 kV Bus | Pole 18576 | OH line - MINK | 11 | 3.6009

## Security of Supply Summary
Supply Level | Region | ID | Security of supply (as set by Transpower) |  | Desired security classification (by AEL) | 2021 Performance |  |  | RCP3 (proposed) |  | Year | 2021
|  |  | Classification | 2021 MVA |  | Capacity at required security classification | MVA in excess of security classification | Security classification at load MVA
Column9 | Column10 | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8
GXP | ABY | ABY | N | 20 | N | 4.58 |  | N | N Sec. Low Ec, Cons.
GXP | BPD | BPD | N | 54 | N-1 | 13.7 |  | N | N Sec. Low Ec, Cons.
GXP | STU | STU | N-1 | 10 | N-1 | 16.4 |  | N | N-1 Sec. Low Ec, Cons
GXP | TKA | TKA | N | 10 | N-1 | 6 |  | N | N Sec. Low Ec, Cons
GXP | TMK | TMK | N-1 | 54 | N-1 | 62 |  | N | N-1 Sec. High Ec, Cons
GXP | TIM | TIM | N-1 | 48 | N-1 | 66.4 |  | N | N-1 Sec. High Ec, Cons
GXP | TWZ | TWZ | N | 207 | N-1 | 3.5 |  | N | N Sec. High Ec, Cons
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Supply Levels Calasifications |  | 3: Existing Security of supply; 7: Forecasted Breach year
Supply Level | Region | ID | Desired security classification | MD | Classification | Capacity | Surplus capacity | FY | Status | Reference
|  |  |  | (MVA) |  | (MVA) | [Capacity – MD]
(MVA)
Column9 | Column10 | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Ref
SubTransmission | ABY | ABY-FLE1 | ST6 (N) | 2.9015 | ST6 (N) | 8.5737 | 5.6721 | 2023 | 2023 | CB2722_Fairlie
SubTransmission | ABY | FLE-OPU1 | ST6 (N) | 7 | ST6 (N) |  |  | N/A | N/A | 7
SubTransmission | BPD | BPD-CNR1 | ST6 (N) | 4.6062 | ST6 (N) | 28.1216 | 23.5154 | No breach | No breach | CB3602_CNR
SubTransmission | BPD | BPD-CNR2 | ST6 (N) | 4.6062 | ST6 (N) | 28.1216 | 23.5154 | No breach | No breach | CB3602_CNR
SubTransmission | TKA | TKA-TEK1 | ST1 (N-1) | 5.054 | ST6 (N) | 10.4599 | 5.4059 | 2021 | 2021 | TKA_GXP
SubTransmission | TIM | ATM_PAR1 | ST1 (N-1) | 9.9556 | ST3 (N-1 SW) | 10.7815 | 0.82588 | 2025 |  | L413_L418_Pareora
SubTransmission | TIM | ATM_PAR2 | ST1 (N-1) | 9.9556 | ST3 (N-1 SW) | 10.7815 | 0.82588 | 2025 |  | L413_L418_Pareora
SubTransmission | TIM | L269_PleasantPoint | ST5 (N-0.5 SW) | 5.47 | ST6 (N) | 9.7996 | 4.3296 | No breach | No breach | L269_PleasantPoint
SubTransmission | TIM | CB2692_North ST.1 | ST1 (N-1) | 3.43 | ST1 (N-1) | 15.3614 | 11.9314 | No breach | No breach | CB2692_North ST.1
SubTransmission | TIM | CB2982_North ST.2 | ST1 (N-1) | 3.34 | ST1 (N-1) | 15.3614 | 12.0214 | No breach | No breach | CB2982_North ST.2
SubTransmission | TIM | TIM_GRM_SUBTRANS | ST1 (N-1) | 5.9377 | ST1 (N-1) | 7.8604 | 1.9227 |  |  | TIM_GRM_SUBTRANS
SubTransmission | TIM | TIM_GRM_SUBTRANS | ST1 (N-1) | 5.9377 | ST1 (N-1) | 7.8604 | 1.9227 |  |  | TIM_GRM_SUBTRANS
SubTransmission | TIM | TIM_GRM_SUBTRANS | ST1 (N-1) | 5.9377 | ST1 (N-1) | 7.8604 | 1.9227 |  |  | TIM_GRM_SUBTRANS
SubTransmission | TIM | TIM_GRM_SUBTRANS | ST1 (N-1) | 5.9377 | ST1 (N-1) | 7.8604 | 1.9227 |  |  | TIM_GRM_SUBTRANS
SubTransmission | TIM | GRM_NST_SUBTRANS | ST1 (N-1) | 4.8111 | ST1 (N-1) | 5.6675 | 0.85636 |  |  | GRM_NST_SUBTRANS
SubTransmission | TIM | GRM_NST_SUBTRANS | ST1 (N-1) | 4.8111 | ST1 (N-1) | 5.6675 | 0.85636 |  |  | GRM_NST_SUBTRANS
SubTransmission | TIM | CB4_GRM-HNT A | ST1 (N-1) | 4.87 | ST1 (N-1) | 5.6675 | 0.79745 |  |  | CB4_GRM-HNT A
SubTransmission | TIM | CB13_GRM-HNT B | ST1 (N-1) | 5.01 | ST1 (N-1) | 5.6675 | 0.65745 |  |  | CB13_GRM-HNT B
SubTransmission | TIM | CB6_HNT-NST A | ST1 (N-1) | 2.6 | ST1 (N-1) | 5.5589 | 2.9589 | No breach | No breach | CB6_HNT-NST A
SubTransmission | TIM | CB15_HNT-NST B | ST1 (N-1) | 2.31 | ST1 (N-1) | 5.5589 | 3.2489 | No breach | No breach | CB15_HNT-NST B
SubTransmission | TIM | CB2662_Waipopo | ST2 (N-1) | 2.28 | ST3 (N-1 SW) | 5.264 | 2.984 | No breach | No breach | CB2662_Waipopo
SubTransmission | TIM | CB2672_Washdyke | ST2 (N-1) | 2.75 | ST3 (N-1 SW) | 5.264 | 2.514 | 2019 |  | CB2672_Washdyke
SubTransmission | TIM | CB3002_Elginshire | ST2 (N-1) | 5.39 | ST3 (N-1 SW) | 4.4965 | -0.89353 | 2019 |  | CB3002_Elginshire
SubTransmission | TIM | CB3012_Arowhenua | ST2 (N-1) | 1.19 | ST3 (N-1 SW) | 3.7612 | 2.5712 | No breach | No breach | CB3012_Arowhenua
SubTransmission | TKA | TEK-DHS1 | ST6 (N) | 1.5708 | ST6 (N) | 8.5737 | 7.0029 | No breach | No breach | TKA_M11
SubTransmission | TKA | DHS-FRH1 | ST6 (N) | 0.27634 | ST6 (N) |  |  | No breach | No breach | 0.27634
SubTransmission | TKA | DHS-UHT1 | ST6 (N) | 5.054 | ST6 (N) | 10.4599 | 5.4059 | No breach | No breach | SBT_33kV
SubTransmission | TMK | TMK-CDY1 | ST1 (N-1) | 8.6999 | ST1 (N-1) | 23.6932 | 14.9933 | No breach | No breach | CB1192_Clandeboye No.1
SubTransmission | TMK | TMK-CNL | ST1 (N-1) | 10.6588 | ST1 (N-1) | 28.864 | 18.2053 | No breach | No breach | CB1272_Clandeboye No.2
SubTransmission | TMK | CNL-CDY2 | ST1 (N-1) |  | ST1 (N-1) |  |  | No breach | No breach
SubTransmission | TMK | TMK-CDY3 | ST1 (N-1) | 8.8727 | ST1 (N-1) | 23.6932 | 14.8205 | 2021 | No breach | CB1222_Clandeboye No.3
SubTransmission | TMK | TMK-CDY4 | ST1 (N-1) | 11.8111 | ST1 (N-1) | 23.6932 | 11.8821 | 2021 | No breach | CB1282_Clandeboye No.4
SubTransmission | TMK | CNL-RGA1 | ST1 (N-1) | 5.1316 | ST6 (N) | 10 | 4.8684 | 2035 | 2035 | RGA_T1
SubTransmission | TMK | TMK-RGA2 | ST1 (N-1) | 5.6463 | ST6 (N) | 12.058 | 6.4118 | 2050 | 2050 | CB1202_Rangitata
SubTransmission | TMK | TMK-GLD1 | ST4 (N-0.75 SW) | 6.9138 | ST6 (N) | 14.9457 | 8.0319 | 2045 | 2045 | CB1292_Geraldine
SubTransmission | TWZ | TWZ-TVS1 | ST1 (N-1) | 4.02 | ST6 (N) | 6.8589 | 2.8389 | 2043 | 2043 | TWZ_GXP
ZoneSubstation | ABY | ABY | ZS6 (N) | 4.3 | ZS6 (N) | 6.9161 | 2.6161 | 2022 | 2022 | ABY
ZoneSubstation | ABY | FLE | ZS5 (N-0.5 SW) | 2.9821 | ZS6 (N) | 5.3833 | 2.4012 | 2037 | 2037 | FLE
ZoneSubstation | BPD | BPD (11 kV) | ZS1 (N-1) | 15.05 | ZS1 (N-1) | 17.4902 | 2.4402 | 2023 | 2023 | BPD
ZoneSubstation | BPD | BPD (33 kV) | ZS4 (N-1 SW) | 4.6062 | ZS4 (N-1 SW) | 28.1216 | 23.5154 | No breach | No breach | CB3602_CNR
ZoneSubstation | BPD | CNR | ZS5 (N-0.5 SW) | 4.6384 | ZS5 (N-0.5 SW) | 21.034 | 16.3957 | No breach | No breach | CNR
ZoneSubstation | STU | STU_GXP | ZS2 (N-1) | 15.132 | ZS5 (N-0.5 SW) | 11.6373 | -3.4947 | 2002 | 2023 | STU_GXP
ZoneSubstation | TKA | TEK | ZS1 (N-1) | 4.6532 | ZS6 (N) | 7.621 | 2.9678 | 2020 | 2020 | TEK
ZoneSubstation | TKA | UHT | ZS6 (N) | 1.02 | ZS6 (N) | 2.8579 | 1.8379 | No breach | No breach | UHT
ZoneSubstation | TKA | OMR | ZS6 (N) | 0.38 | ZS6 (N) | 1.4044 | 1.0244 | 2019 | 2019 | OMR
ZoneSubstation | TKA | HLB | ZS6 (N) | 0.47648 | ZS6 (N) | 1.1432 | 0.66667 | 2034 | 2034 | HLB
ZoneSubstation | TIM | ATM | ZS1 (N-1) | 6.9 | ZS4 (N-1 SW) | 13.7178 | 6.8178 | 2025 | No breach | ATM
ZoneSubstation | TIM | PAR | ZS2 (N-1) | 9.68 | ZS5 (N-0.5 SW) | 16.4991 | 6.8191 | 2025 | No breach | PAR
ZoneSubstation | TIM | PLP | ZS5 (N-0.5 SW) | 4.96 | ZS6 (N) | 6.7629 | 1.8029 | No breach | No breach | PLP
ZoneSubstation | TMK | TMK | ZS1 (N-1) | 14.5497 | ZS1 (N-1) | 19.8525 | 5.3029 | 2031 | No breach | TMK
ZoneSubstation | TMK | CD_1 | ZS1 (N-1) | 13.96 | ZS1 (N-1) | 20.2319 | 6.2719 | 2021 | No breach | CD_1
ZoneSubstation | TMK | CD_2 | ZS1 (N-1) | 20.07 | ZS1 (N-1) | 23.6932 | 3.6232 | Possible breach 2021 | No breach | CD_2
ZoneSubstation | TMK | GLD | ZS5 (N-0.5 SW) | 6.869 | ZS6 (N) | 12.0631 | 5.1941 | 2014 | 2014 | GLD
ZoneSubstation | TMK | RGA | ZS1 (N-1) |  | ZS4 (N-1 SW) | 12.058 |  | 2032 | 2036 | RGA
ZoneSubstation | TWZ | TVS | ZS3 (N-1 SW) | 3.99 | ZS5 (N-0.5 SW) | 6.2523 | 2.2623 | 2036 | 2036 | TVS
SwitchingStation | STU | 1: STU Fonterra; 2: ZS4 (N-1 SW); 4: ZS4 (N-1 SW)
SwitchingStation | TIM | ATM | ZS4 (N-1 SW) | 6.9 | ZS4 (N-1 SW) | 13.7178 | 6.8178 |  |  | ATM
SwitchingStation | TIM | PAR | ZS4 (N-1 SW) | 9.68 | ZS4 (N-1 SW) | 16.4991 | 6.8191 |  |  | PAR
SwitchingStation | TIM | PLP | ZS4 (N-1 SW) | 4.96 | ZS4 (N-1 SW) | 6.7629 | 1.8029 |  |  | PLP
SwitchingStation | TIM | WSS | ZS3 (N-1 SW) | 2.9843 | ZS3 (N-1 SW) | 7.621 | 4.6367 | No breach | No breach | WSS
DistributionFeeder | ABY | CB2732_Raincliff | DF6 (N) | 0.89 | DF6 (N) | 4.2868 | 3.3968 | No breach | No breach | CB2732_Raincliff
DistributionFeeder | ABY | CB2742_Cave | DF5 (N) | 1.33 | DF5 (N) | 4.2868 | 2.9568 | No breach | No breach | CB2742_Cave
DistributionFeeder | ABY | CB2722_Fairlie | DF3 (N-1 SW) | 2.9015 | DF3 (N-1 SW) | 8.5737 | 5.6721 | 2026 | 2026 | CB2722_Fairlie
DistributionFeeder | ABY | F374_Cricklewood | DF5 (N) | 0.55 | DF5 (N) | 3.6265 | 3.0765 | No breach | No breach | F374_Cricklewood
DistributionFeeder | ABY | F380_Fairlie Rural | DF5 (N) | 1.9526 | DF5 (N) | 3.6914 | 1.7388 | 2036 | 2036 | F380_Fairlie Rural
DistributionFeeder | ABY | F383_Fairlie Township | DF3 (N-1 SW) | 1.0989 | DF3 (N-1 SW) | 3.2831 | 2.1842 | No breach | No breach | F383_Fairlie Township
DistributionFeeder | BPD | CB11_Waihao Downs | DF4 (N-0.5 SW) | 3.9702 | DF4 (N-0.5 SW) | 4.6582 | 0.68808 | No breach | No breach | CB11_Waihao Downs
DistributionFeeder | BPD | CB12_Ikawai | DF4 (N-0.5 SW) | 2.3902 | DF4 (N-0.5 SW) | 6.5909 | 4.2007 | No breach | No breach | CB12_Ikawai
DistributionFeeder | BPD | CB13_Waikakahi | DF4 (N-0.5 SW) | 1.0475 | DF4 (N-0.5 SW) | 6.5909 | 5.5434 | No breach | No breach | CB13_Waikakahi
DistributionFeeder | BPD | CB2_Tawai | DF4 (N-0.5 SW) | 2.7193 | DF4 (N-0.5 SW) | 7.5194 | 4.8001 | No breach | No breach | CB2_Tawai
DistributionFeeder | BPD | CB1_Waihuna | DF2 (N-1 SW) | 2.7641 | DF2 (N-1 SW) | 7.5194 | 4.7553 | No breach | No breach | CB1_Waihuna
DistributionFeeder | BPD | CB8_Drier 2 | DF1 (N-1 SW) | 1.2443 | DF1 (N-1 SW) | 7.2192 | 5.9748 | No breach | No breach | CB8_Drier 2
DistributionFeeder | BPD | CB9_WetProcess | DF1 (N-1 SW) | 2.0003 | DF1 (N-1 SW) | 7.5199 | 5.5196 | No breach | No breach | CB9_WetProcess
DistributionFeeder | BPD | CB11_Boiler/Chiller 1 | DF1 (N-1 SW) | 1.3027 | DF1 (N-1 SW) | 7.2192 | 5.9164 | No breach | No breach | CB11_Boiler/Chiller 1
DistributionFeeder | BPD | CB12_Office | DF1 (N-1 SW) | 0.4318 | DF1 (N-1 SW) | 7.5199 | 7.0882 | No breach | No breach | CB12_Office
DistributionFeeder | STU | CB1_Otaio | DF4 (N-0.5 SW) | 4.4032 | DF4 (N-0.5 SW) | 6.8454 | 2.4422 | Breach 2027 | Breach 2027 | CB1_Otaio
DistributionFeeder | STU | CB2_Glenavy | DF4 (N-0.5 SW) | 2.153 | DF4 (N-0.5 SW) | 5.8187 | 3.6657 | No Breach | No Breach | CB2_Glenavy
DistributionFeeder | STU | CB3_Waimate | DF3 (N-1 SW) | 4.3734 | DF3 (N-1 SW) | 5.8187 | 1.4453 | Breach 2023 | Breach 2023 | CB3_Waimate
DistributionFeeder | STU | CB7_Waihaorunga | DF6 (N) | 0.83807 | DF6 (N) | 6.8454 | 6.0074 | No breach | No breach | CB7_Waihaorunga
DistributionFeeder | STU | CB8_Mt Studholme | DF4 (N-0.5 SW) | 3.799 | DF4 (N-0.5 SW) | 4.7907 | 0.99172 | Breach 2023 | Breach 2023 | CB8_Mt Studholme
DistributionFeeder | STU | CB9_Morven | DF4 (N-0.5 SW) | 3.969 | DF4 (N-0.5 SW) | 5.8187 | 1.8497 | Breach 2024 | Breach 2024 | CB9_Morven
DistributionFeeder | TIM | CB2_White St | DF3 (N-1 SW) | 1.32 | DF3 (N-1 SW) | 3.0598 | 1.7398 | 2019 | No breach | CB2_White St
DistributionFeeder | TIM | CB5_Nile St | DF3 (N-1 SW) | 1.54 | DF3 (N-1 SW) | 4.4472 | 2.9072 | 2019 | No breach | CB5_Nile St
DistributionFeeder | TIM | CB6_Parkview Terrace | DF1 (N-1 SW) | 1.82 | DF1 (N-1 SW) | 4.344 | 2.524 | 2024 | No breach | CB6_Parkview Terrace
DistributionFeeder | TIM | CB7_Douglas St | DF1 (N-1 SW) | 1.12 | DF1 (N-1 SW) | 4.4946 | 3.3746 | No breach | No breach | CB7_Douglas St
DistributionFeeder | TIM | CB10_Ashbury Park | DF2 (N-1 SW) | 1 | DF2 (N-1 SW) | 3.8372 | 2.8372 | No breach | No breach | CB10_Ashbury Park
DistributionFeeder | TIM | CB12_Selwyn St | DF2 (N-1 SW) | 1.67 | DF2 (N-1 SW) | 3.3553 | 1.6853 | 2019 | No breach | CB12_Selwyn St
DistributionFeeder | TIM | CB15_Park Lane | DF3 (N-1 SW) | 1.83 | DF3 (N-1 SW) | 3.2888 | 1.4588 | 2019 | No breach | CB15_Park Lane
DistributionFeeder | TIM | CB16_Evans St | DF2 (N-1 SW) | 1.97 | DF2 (N-1 SW) | 3.2001 | 1.2301 | 2024 | No breach | CB16_Evans St
DistributionFeeder | TIM | CB17_June St | DF3 (N-1 SW) | 1.1 | DF3 (N-1 SW) | 4.4309 | 3.3309 | No breach | No breach | CB17_June St
DistributionFeeder | TIM | CB20_Hobbs St | DF2 (N-1 SW) | 1.51 | DF2 (N-1 SW) | 3.8635 | 2.3535 | No breach | No breach | CB20_Hobbs St
DistributionFeeder | TIM | CB1_Harper St | DF3 (N-1 SW) | 1.04 | DF3 (N-1 SW) | 3.8105 | 2.7705 | No breach | No breach | CB1_Harper St
DistributionFeeder | TIM | CB2_Wilson St | DF3 (N-1 SW) | 0.94 | DF3 (N-1 SW) | 2.1035 | 1.1635 | No breach | No breach | CB2_Wilson St
DistributionFeeder | TIM | CB4_Baker St | DF3 (N-1 SW) | 1.23 | DF3 (N-1 SW) | 3.8105 | 2.5805 | No breach | No breach | CB4_Baker St
DistributionFeeder | TIM | CB5_Le Cren St | DF3 (N-1 SW) | 2.08 | DF3 (N-1 SW) | 3.4583 | 1.3783 | 2019 | No breach | CB5_Le Cren St
DistributionFeeder | TIM | CB7_Church St SS | DF2 (N-1 SW) | 0.84 | DF2 (N-1 SW) | 3.0574 | 2.2174 | No breach | No breach | CB7_Church St SS
DistributionFeeder | TIM | CB10_Gibson St | DF3 (N-1 SW) | 0.84 | DF3 (N-1 SW) | 3.8105 | 2.9705 | No breach | No breach | CB10_Gibson St
DistributionFeeder | TIM | CB11_Rhodes St | DF3 (N-1 SW) | 1.53 | DF3 (N-1 SW) | 3.155 | 1.625 | 2019 | No breach | CB11_Rhodes St
DistributionFeeder | TIM | CB13_Clifton Terrace | DF3 (N-1 SW) | 1.32 | DF3 (N-1 SW) | 3.8105 | 2.4905 | No breach | No breach | CB13_Clifton Terrace
DistributionFeeder | TIM | CB14_Church St NS | DF3 (N-1 SW) | 0.69 | DF3 (N-1 SW) | 2.9991 | 2.3091 | 2019 | No breach | CB14_Church St NS
DistributionFeeder | TIM | CB16_Arthur St | DF2 (N-1 SW) | 1.54 | DF2 (N-1 SW) | 3.8105 | 2.2705 | No breach | No breach | CB16_Arthur St
DistributionFeeder | TIM | CB3_Redruth 1 | DF2 (N-1 SW) | 0.41 | DF2 (N-1 SW) | 5.2076 | 4.7976 | No breach | No breach | CB3_Redruth 1
DistributionFeeder | TIM | CB4_Rose St | DF3 (N-1 SW) | 1.26 | DF3 (N-1 SW) | 4.3531 | 3.0931 | No breach | No breach | CB4_Rose St
DistributionFeeder | TIM | CB5_Craigie Ave | DF3 (N-1 SW) | 1.27 | DF3 (N-1 SW) | 3.8471 | 2.5771 | No breach | No breach | CB5_Craigie Ave
DistributionFeeder | TIM | CB8_Barnard St | DF1 (N-1 SW) | 1.23 | DF1 (N-1 SW) | 3.287 | 2.057 | 2020 | No breach | CB8_Barnard St
DistributionFeeder | TIM | CB9_Port 1 | DF1 (N-1 SW) | 3.52 | DF1 (N-1 SW) | 5.2076 | 1.6876 |  | No breach | CB9_Port 1
DistributionFeeder | TIM | CB10_Fraser St | DF1 (N-1 SW) | 0.99 | DF1 (N-1 SW) | 3.806 | 2.816 | No breach | No breach | CB10_Fraser St
DistributionFeeder | TIM | CB11_Hayes St | DF1 (N-1 SW) | 1.13 | DF1 (N-1 SW) | 3.9414 | 2.8114 |  | No breach | CB11_Hayes St
DistributionFeeder | TIM | CB12_High St | DF1 (N-1 SW) | 0.83 | DF1 (N-1 SW) | 3.9414 | 3.1114 | No breach | No breach | CB12_High St
DistributionFeeder | TIM | CB13_Port 2 | DF1 (N-1 SW) | 2.01 | DF1 (N-1 SW) | 5.2076 | 3.1976 |  | No breach | CB13_Port 2
DistributionFeeder | TIM | CB16_Victoria St | DF2 (N-1 SW) | 1.45 | DF2 (N-1 SW) | 3.9994 | 2.5494 | No breach | No breach | CB16_Victoria St
DistributionFeeder | TIM | CB17_Stafford St | DF2 (N-1 SW) | 1.13 | DF2 (N-1 SW) | 2.5879 | 1.4579 | 2020 | No breach | CB17_Stafford St
DistributionFeeder | TIM | CB18_Redruth 2 | DF2 (N-1 SW) | 1.34 | DF2 (N-1 SW) | 5.2076 | 3.8676 | No breach | No breach | CB18_Redruth 2
DistributionFeeder | TIM | CB3_Works No. 1 | DF1 (N-1 SW) | 2.56 | DF1 (N-1 SW) | 5.8301 | 3.2701 | No breach | No breach | CB3_Works No. 1
DistributionFeeder | TIM | CB4_St Andrews | DF5 (N) | 3.04 | DF5 (N) | 4.8973 | 1.8573 | No breach | No breach | CB4_St Andrews
DistributionFeeder | TIM | CB5_Works No. 2 | DF1 (N-1 SW) | 2.58 | DF1 (N-1 SW) | 5.8301 | 3.2501 | No breach | No breach | CB5_Works No. 2
DistributionFeeder | TIM | CB6_Normanby | DF5 (N) | 2.06 | DF5 (N) | 3.9652 | 1.9052 | No breach | No breach | CB6_Normanby
DistributionFeeder | TIM | CB7_Holmestation | DF4 (N-0.5 SW) | 1.69 | DF4 (N-0.5 SW) | 3.6657 | 1.9757 |  | No breach | CB7_Holmestation
DistributionFeeder | TIM | CB1_Waitawa | DF4 (N-0.5 SW) | 1.64 | DF4 (N-0.5 SW) | 2.8762 | 1.2362 |  | No breach | CB1_Waitawa
DistributionFeeder | TIM | CB2_Sutherlands | DF4 (N-0.5 SW) | 0.62 | DF4 (N-0.5 SW) | 3.8869 | 3.2669 |  | No breach | CB2_Sutherlands
DistributionFeeder | TIM | CB4_Totara Valley | DF3 (N-1 SW) | 2.25 | DF3 (N-1 SW) | 3.673 | 1.423 |  | No breach | CB4_Totara Valley
DistributionFeeder | TIM | CB5_Pleasant Point Township | DF3 (N-1 SW) | 1.25 | DF3 (N-1 SW) | 2.5458 | 1.2958 |  | No breach | CB5_Pleasant Point Township
DistributionFeeder | TIM | CB2702_Morgans Rd | DF3 (N-1 SW) | 2.6 | DF3 (N-1 SW) | 3.5825 | 0.98249 |  | No breach | CB2702_Morgans Rd
DistributionFeeder | TIM | CB2712_Mountain View Rd | DF3 (N-1 SW) | 4 | DF3 (N-1 SW) | 7.02 | 3.02 |  | No breach | CB2712_Mountain View Rd
DistributionFeeder | TIM | CB2742_Levels Plain | DF2 (N-1 SW) | 1.57 | DF2 (N-1 SW) | 7.5161 | 5.9461 |  | No breach | CB2742_Levels Plain
DistributionFeeder | TIM | CB2762_AEL Yard | DF1 (N-1 SW) | 1.3 | DF1 (N-1 SW) | 5.3353 | 4.0353 |  | No breach | CB2762_AEL Yard
DistributionFeeder | TIM | CB2832_Grants Rd | DF1 (N-1 SW) | 2.64 | DF1 (N-1 SW) | 5.3353 | 2.6953 |  | No breach | CB2832_Grants Rd
DistributionFeeder | TIM | CB2852_Hadlow | DF4 (N-0.5 SW) | 2.94 | DF4 (N-0.5 SW) | 4.9614 | 2.0214 |  | No breach | CB2852_Hadlow
DistributionFeeder | TIM | CB2862_Meadows Rd | DF2 (N-1 SW) | 0.87 | DF2 (N-1 SW) | 7.5161 | 6.6461 | No breach | No breach | CB2862_Meadows Rd
DistributionFeeder | TIM | CB2942_Old North Rd | DF1 (N-1 SW) | 4.06 | DF1 (N-1 SW) | 5.3501 | 1.2901 | 2025 | 2025 | CB2942_Old North Rd
DistributionFeeder | TIM | CB2952_Highfield | DF3 (N-1 SW) | 2.79 | DF3 (N-1 SW) | 5.3353 | 2.5453 |  | No breach | CB2952_Highfield
DistributionFeeder | TIM | CB2972_Smithfield | DF1 (N-1 SW) | 3.87 | DF1 (N-1 SW) | 5.3501 | 1.4801 |  | No breach | CB2972_Smithfield
DistributionFeeder | TIM | CB2992_Ripple Plant | DF2 (N-1 SW) | 0.64 | DF2 (N-1 SW) | 6.5731 | 5.9331 | No breach | No breach | CB2992_Goulds Road
DistributionFeeder | TKA | M200_Haldon_Lilybank | DF2 (N-1 SW) | 1.34 | DF2 (N-1 SW) | 3.5556 | 2.2156 | 2050 | 2050 | M200_Haldon_Lilybank
DistributionFeeder | TKA | M201_Simons | DF4 (N-0.5 SW) | 0.55 | DF4 (N-0.5 SW) | 1.4044 | 0.85435 | 2020 | 2020 | M201_Simons
DistributionFeeder | TKA | M205_Godley | DF6 (N) | 0.2525 | DF6 (N) | 1.4044 | 1.1519 | No breach | No breach | M205_Godley
DistributionFeeder | TKA | M206_Tekapo Township | DF2 (N-1 SW) | 3.07 | DF2 (N-1 SW) | 3.5556 | 0.48556 | 2019 | 2019 | M206_Tekapo Township
DistributionFeeder | TKA | M338_Old Man Range | DF4 (N-0.5 SW) | 0.38 | DF4 (N-0.5 SW) | 2.2863 | 1.9063 | 2019 | 2019 | M338_Old Man Range
DistributionFeeder | TKA | M32_Lilybank | DF6 (N) | 0.1763 | DF6 (N) | 2.8087 | 2.6324 | No breach | No breach | M32_Lilybank
DistributionFeeder | TKA | M33_Haldon | DF4 (N-0.5 SW) | 0.30495 | DF4 (N-0.5 SW) | 2.8087 | 2.5038 | No breach | No breach | M33_Haldon
DistributionFeeder | TKA | M158_Village | DF3 (N-1 SW) | 0.71 | DF3 (N-1 SW) | 1.9053 | 1.1953 | No breach | No breach | M158_Village
DistributionFeeder | TKA | M159_Village | DF3 (N-1 SW) | 0.32 | DF3 (N-1 SW) | 1.9053 | 1.5853 | No breach | No breach | M159_Village
DistributionFeeder | TMK | T600_Tie to Milk Powder 2 | DF1 (N-1 SW) | 0 | DF1 (N-1 SW) | 5.7761 | 5.7761 | No breach | No breach | T600_Tie to Milk Powder 2
DistributionFeeder | TMK | T601_Fire Services | DF1 (N-1 SW) | 3.856 | DF1 (N-1 SW) | 5.7761 | 1.9201 | No breach | No breach | T601_Fire Services
DistributionFeeder | TMK | T602_Whey Processing | DF1 (N-1 SW) | 3.0704 | DF1 (N-1 SW) | 4.5641 | 1.4936 | No breach | No breach | T602_Whey Processing
DistributionFeeder | TMK | T603_Lactose Plant | DF1 (N-1 SW) | 0 | DF1 (N-1 SW) | 6.5163 | 6.5163 | No breach | No breach | T603_Lactose Plant
DistributionFeeder | TMK | T605_Tie to Milford | DF5 (N) | 0 | DF5 (N) | 2.3391 | 2.3391 | No breach | No breach | T605_Tie to Milford
DistributionFeeder | TMK | T609_Milk Reception | DF1 (N-1 SW) | 0.74515 | DF1 (N-1 SW) | 5.7761 | 5.0309 | No breach | No breach | T609_Milk Reception
DistributionFeeder | TMK | T610_Chilled Water 1 | DF1 (N-1 SW) | 2.5186 | DF1 (N-1 SW) | 3.423 | 0.90445 | No breach | No breach | T610_Chilled Water 1
DistributionFeeder | TMK | T611_Effluent Plant | DF1 (N-1 SW) | 1.8472 | DF1 (N-1 SW) | 3.423 | 1.5759 | No breach | No breach | T611_Effluent Plant
DistributionFeeder | TMK | T612_Milk Treatment | DF1 (N-1 SW) | 1.006 | DF1 (N-1 SW) | 2.3391 | 1.3331 | No breach | No breach | T612_Milk Treatment
DistributionFeeder | TMK | T613_Rolleston Rd | DF4 (N-0.5 SW) | 2.5287 | DF4 (N-0.5 SW) | 3.423 | 0.89439 | No breach | No breach | T613_Rolleston Rd
DistributionFeeder | TMK | T614_Tie to Powder Handling | DF1 (N-1 SW) | 1.1523 | DF5 (N) | 6.1209 | 4.9686 | 2020 | No breach | T614_Tie to Powder Handling
DistributionFeeder | TMK | T650_Tie to Milk Powder 1 | DF1 (N-1 SW) | 0 | DF1 (N-1 SW) | 5.4312 | 5.4312 | No breach | No breach | T650_Tie to Milk Powder 1
DistributionFeeder | TMK | T651_Milk Powder 3 | DF1 (N-1 SW) | 5.6642 | DF5 (N) | 6.2933 | 0.62915 | 2020 | No breach | T651_Milk Powder 3
DistributionFeeder | TMK | T652_Tie to WPC | DF1 (N-1 SW) | 1.0751 | DF1 (N-1 SW) | 4.1875 | 3.1124 | No breach | No breach | T652_Tie to WPC
DistributionFeeder | TMK | T653_Chilled Water 3 | DF1 (N-1 SW) | 1.1613 | DF1 (N-1 SW) | 6.0347 | 4.8734 | No breach | No breach | T653_Chilled Water 3
DistributionFeeder | TMK | T654_Tie to Boiler House | DF1 (N-1 SW) | 3.2923 | DF1 (N-1 SW) | 5.8909 | 2.5986 | No breach | No breach | T654_Tie to Boiler House
DistributionFeeder | TMK | T658_Milk Powder 2 | DF1 (N-1 SW) | 3.2848 | DF1 (N-1 SW) | 5.4312 | 2.1465 | No breach | No breach | T658_Milk Powder 2
DistributionFeeder | TMK | T659_Tie to Energy Centre 1 | DF1 (N-1 SW) | 1.3535 | DF1 (N-1 SW) | 5.8308 | 4.4773 | No breach | No breach | T659_Tie to Energy Centre 1
DistributionFeeder | TMK | T660_Refrigeration | DF1 (N-1 SW) | 0.69504 | DF1 (N-1 SW) | 5.4312 | 4.7362 | No breach | No breach | T660_Refrigeration
DistributionFeeder | TMK | T661_Laboratory | DF1 (N-1 SW) | 0.53042 | DF1 (N-1 SW) | 5.4312 | 4.9008 | No breach | No breach | T661_Laboratory
DistributionFeeder | TMK | G194_Speechly | DF5 (N) | 2.1032 | DF5 (N) | 3.6118 | 1.5086 | 2035 | 2035 | G194_Speechly
DistributionFeeder | TMK | G191_Geraldine Township | DF3 (N-1 SW) | 4.0239 | DF3 (N-1 SW) | 4.6146 | 0.59072 | 2024 | 2024 | G191_Geraldine Township
DistributionFeeder | TMK | G156_Woodbury | DF4 (N-0.5 SW) | 2.4692 | DF4 (N-0.5 SW) | 4.6146 | 2.1454 | No breach | No breach | G156_Woodbury
DistributionFeeder | TMK | CB2_Arundel | DF4 (N-0.5 SW) | 1.8392 | DF4 (N-0.5 SW) | 4.9917 | 3.1525 | No breach | No breach | CB2_Arundel
DistributionFeeder | TMK | CB3_Mahan Road | DF4 (N-0.5 SW) | 2.9188 | DF4 (N-0.5 SW) | 4.0457 | 1.1269 | 2026 | 2026 | CB3_Mahan Road
DistributionFeeder | TMK | CB4_Main South Road | DF4 (N-0.5 SW) | 1.7075 | DF4 (N-0.5 SW) | 4.9917 | 3.2842 | No breach | No breach | CB4_Main South Road
DistributionFeeder | TMK | CB11_Belfield | DF4 (N-0.5 SW) | 2.4006 | DF4 (N-0.5 SW) | 5.3518 | 2.9511 | No breach | No breach | CB11_Belfield
DistributionFeeder | TMK | CB12_Orton | DF4 (N-0.5 SW) | 0.64657 | DF4 (N-0.5 SW) | 5.3518 | 4.7052 | No breach | No breach | CB12_Orton
DistributionFeeder | TMK | CB13_Rangitata Island | DF4 (N-0.5 SW) | 1.5634 | DF4 (N-0.5 SW) | 4.9917 | 3.4283 | No breach | No breach | CB13_Rangitata Island
DistributionFeeder | TMK | CB1_Temuka West | DF3 (N-1 SW) | 3.3779 | DF3 (N-1 SW) | 4.9407 | 1.5628 | No breach | No breach | CB1_Temuka West
DistributionFeeder | TMK | CB2_Milford | DF4 (N-0.5 SW) | 2.6 | DF4 (N-0.5 SW) | 3.0371 | 0.43713 | 2038 | 2038 | CB2_Milford
DistributionFeeder | TMK | CB3_Winchester | DF3 (N-1 SW) | 3.0726 | DF3 (N-1 SW) | 5.7158 | 2.6432 | 2039 | 2039 | CB3_Winchester
DistributionFeeder | TMK | CB7_Rangitata | DF4 (N-0.5 SW) | 3.1628 | DF4 (N-0.5 SW) | 5.7158 | 2.553 | 2039 | 2039 | CB7_Rangitata
DistributionFeeder | TMK | CB8_Temuka East | DF3 (N-1 SW) | 3.6548 | DF3 (N-1 SW) | 4.5917 | 0.93687 | 2020 | 2020 | CB8_Temuka East
DistributionFeeder | TMK | CB9_Waitohi | DF4 (N-0.5 SW) | 1.8768 | DF4 (N-0.5 SW) | 3.3533 | 1.4765 | 2043 | 2043 | CB9_Waitohi
DistributionFeeder | TWZ | Z1_Urban No. 1 | DF3 (N-1 SW) | 1.76 | DF3 (N-1 SW) | 2.896 | 1.136 | 2040 | 2040 | Z1_Urban No. 1
DistributionFeeder | TWZ | Z2_Urban No. 2 | DF3 (N-1 SW) | 1.64 | DF3 (N-1 SW) | 2.896 | 1.256 | 2042 | 2042 | Z2_Urban No. 2
DistributionFeeder | TWZ | Z3_Industrial | DF2 (N-1 SW) | 0.01 | DF2 (N-1 SW) | 1.6269 | 1.6169 | No breach | No breach | Z3_Industrial
DistributionFeeder | TWZ | Z4_Twizel Rural | DF5 (N) | 0.8 | DF5 (N) | 2.896 | 2.096 | No breach | No breach | Z4_Twizel Rural
DistributionFeeder | TWZ | Z9_Local Service | DF2 (N-1 SW) |  | DF2 (N-1 SW) |  |  | No breach | No breach | Z9_Local Service
Note on J1: Author: Link to Service and Asset Health Engagement paper attached
Note on E18: Author: OPU gen rated at 7 MW
Note on E27: Author: For TIM to GRM demand is divided by 4
Note on E28: Author: For TIM to GRM demand is divided by 4
Note on E29: Author: For TIM to GRM demand is divided by 4
Note on E30: Author: For TIM to GRM demand is divided by 4

## Switching Diagram Tables-Major
SCADA Levels Percentages of Lowest Rating
| Emergency | 90% | Meeting minutes of values agreed upon
| Pre-Emergency | 80%
ALBURY SUBSTATION (C251) | [11 empty] | Supporting info | [7 empty] | ALBURY SUBSTATION (C251)-OLD | [14 empty] | Total Capacity Increase/Decrease Assessment
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER | Station | Load Capability | [5 empty] | OC Pick Up Protection
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED | [24 empty] | A Up | A Down | A Balance | MVA Up | MVA Down | MVA Balance | A Up | A Down | A Balance | MVA Up | MVA Down | MVA Balance
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down |  | Total | 3906.3321 | 12094.158 | -8187.8259 | 125.1551 | 296.1398 | -170.9846 | 4116 | 802 | 3314 | 109.039 | 25.947 | 83.0919 | -87.8927
CB62 | TRANSPOWER INCOMER | 110 | 105 | 199 | 80 | 15.242 | 90 | 17.1473 | POWER TRANSFORMER RATING AT 20.01 MVA | NO | N/A | ABY-CB62 | GXP | ABY_GXP |  | 110 | YES | YES |  | New | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | N/A | ABY | 20 | 361.529 | -341.529 | 0.38105 | 6.8881 | -6.507 | 0 | 0 | 0 | 0 | 0 | 0
CB2712 | TRANSPOWER INCOMER | 11 | 600 | 1635 | 480 | 9.1452 | 540 | 10.2884 | CIRCUIT BREAKER-ABY-CB2712-OTHER EQUIPMENT | NO | N/A | ABY-CB2712 | GXP | ABY_GXP |  | 11 | YES | YES |  | CB2712 | TRANSPOWER INCOMER |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO | FLE | 107.6266 | 254.1533 | -146.5267 | 3.852 | 10.1968 | -6.3448 | 20 | 0 | 20 | 0.38452 | 0 | 0.38452
CB4242 | FAIRLIE | 33 | 172.8371 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-PETREL | NO | N/A | ABY-CB4242 | SubTransmission | CB2722_Fairlie |  | 33 | NO | NO |  | CB4242 | FAIRLIE (33kV) |  | p | 0 | 0 | 0 | 0 | 150 | u | 0 | 0 | 0 | 0 | NO | BPD | 641.6496 | 1047.5057 | -405.8561 | 33.889 | 45.1791 | -11.2901 | 30 | 4 | 26 | 0.58301 | 0.077734 | 0.50527
CB2722 | FAIRLIE | 11 | 450 | 450 | 360 | 6.8589 | 405 | 7.7163 | CIRCUIT BREAKER-ABY-CB2722-PROTECTION | NO | N/A | ABY-CB2722 | SubTransmission | CB2722_Fairlie |  | 11 | YES | NO |  | CB2722 | FAIRLIE (11kV) | 430 | p | 20 | 0.38105 | 0 | 0 | 450 | u | 0 | 0 | 0 | 0 | NO | CNR | 195.7931 | 1233.4998 | -1037.7067 | 11.1911 | 23.5013 | -12.3102 | 144 | 18 | 126 | 2.7436 | 0.34295 | 2.4006
CB2732 | RAINCLIFF | 11 | 241.6125 | 225 | 180 | 3.4295 | 200 | 3.8105 | OH LINE-19/14 CU | YES | YES | ABY-CB2732 | DistributionFeeder | CB2732_Raincliff |  | 11 | NO | NO |  | CB2732 | RAINCLIFF | 430 | q | 0 | 0 | 188.3875 | 3.5893 | 225 | u | 0 | 0 | 0 | 0 | YES | STU | 14.6938 | 103 | -88.3062 | 0.28499 | 1.9977 | -1.7127 | 0 | 12 | -12 | 0 | 0.23275 | -0.23275
CB2742 | CAVE | 11 | 256.8585 | 225 | 180 | 3.4295 | 200 | 3.8105 | OH LINE-DOG | YES | YES | ABY-CB2742 | DistributionFeeder | CB2742_Cave |  | 11 | NO | NO |  | CB2742 | CAVE | 430 | q | 0 | 0 | 173.1415 | 3.2988 | 225 | u | 0 | 0 | 0 | 0 | YES | TIM | 178.9342 | 2801.4782 | -2622.544 | 3.4092 | 53.3753 | -49.9662 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | ABY |  |  |  | 20 | 0.38105 | 361.529 | 6.8881 |  |  | 0 | 0 | 0 | 0 |  | GRM | 114.3814 | 744.384 | -630.0026 | 2.1793 | 14.1824 | -12.0032 | 140 | 0 | 140 | 2.6674 | 0 | 2.6674
FAIRLIE SUBSTATION (C1) | [11 empty] | Supporting info | [7 empty] | FAIRLIE SUBSTATION (C1)-OLD | [14 empty] | HNT | 50.0696 | 31.0605 | 19.0091 | 0.95395 | 0.59178 | 0.36217 | 0 | 0 | 0 | 0 | 0 | 0
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER | NST | 55.7128 | 459.2406 | -403.5278 | 1.0615 | 8.7497 | -7.6882 | 376 | 0 | 376 | 7.1638 | 0 | 7.1638
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED | [23 empty] | ATM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down |  | PAR | 186.64 | 721.5311 | -534.8911 | 10.5525 | 29.6689 | -19.1164 | 0 | 244 | -244 | 0 | 4.7418 | -4.7418
F400 | OPU 33 kV RECLOSER | 33 | 247 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-70 MM² CU | NO | N/A | OPU-F400 | SubTransmission | OPU |  | 33 | NO | NO |  | F400 | ABY-OPU 33KV RECLOSER | 200 | p | 47 | 2.6864 | 0 | 0 | 150 | u | 0 | 0 | 0 | 0 | NO | PLP | 60.4582 | 127.3922 | -66.9341 | 3.3044 | 2.4757 | 0.82872 | 208 | 262 | -54 | 4.0422 | 7.0533 | -3.0111
F323 | T1 HV CB | 33 | 150 | 100 | 80 | 4.5726 | 90 | 5.1442 | CIRCUIT BREAKER-ABY-CB4242-PROTECTION | NO | N/A | FLE-F323 | SubTransmission | CB2722_Fairlie |  | 33 | NO | YES |  | F323 | T1 HV CB | 290 | q | 0 | 0 | 140 | 8.0021 | 100 | u | 0 | 0 | 0 | 0 | NO | TEK | 2.6554 | 23 | -20.3446 | 0.050592 | 1.3146 | -1.264 | 0 | 0 | 0 | 0 | 0 | 0
F377 | T1 LV INCOMER | 11 | 325.0817 | 280 | 220 | 4.2297 | 250 | 4.8065 | POWER TRANSFORMER RATING AT 6.25 MVA | YES | NO | FLE-F377 | ZoneSubstation | FLE |  | 11.1001 | NO | YES |  | F377 | T1 LV INCOMER | 420 | q | 0 | 0 | 94.9183 | 1.8249 | 260 | p | 20 | 0.38452 | 0 | 0 | YES (DISABLED) | UHT | 361.6432 | 0 | 361.6432 | 6.8995 | 0 | 6.8995 | 0 | 0 | 0 | 0 | 0 | 0
F374 | CRICKLEWOOD | 11 | 188.6266 | 192 | 150 | 2.8839 | 165 | 3.1723 | OH LINE-MINK | YES | YES | FLE-F374 | DistributionFeeder | F374_Cricklewood |  | 11.1001 | NO | NO |  | F374 | CRICKLEWOOD | 185 | p | 3.6266 | 0.069725 | 0 | 0 | 192 | u | 0 | 0 | 0 | 0 | YES | OMR | 0 | 5.0258 | -5.0258 | 0 | 0.096426 | -0.096426 | 0 | 0 | 0 | 0 | 0 | 0
F380 | FAIRLIE RURAL | 11 | 247 | 192 | 150 | 2.8839 | 170 | 3.2684 | OH LINE-70 MM² CU | YES | NO | FLE-F380 | DistributionFeeder | F380_Fairlie Rural |  | 11.1001 | NO | NO |  | F380 | FAIRLIE RURAL | 190 | p | 57 | 1.0959 | 0 | 0 | 192 | u | 0 | 0 | 0 | 0 | YES (DISABLED) | HLB | 0.043194 | 0.013612 | 0.029582 | 0.0016459 | 0.00025934 | 0.0013866 | 0 | 0 | 0 | 0 | 0 | 0
F383 | FAIRLIE TOWNSHIP | 11 | 170.765 | 192 | 135 | 2.5955 | 150 | 2.8839 | CABLE-1-3C 95 MM² AL PILC | YES | NO | FLE-F383 | DistributionFeeder | F383_Fairlie Township |  | 11.1001 | NO | NO |  | F383 | FAIRLIE TOWNSHIP | 190 | q | 0 | 0 | 19.235 | 0.36981 | 192 | u | 0 | 0 | 0 | 0 | YES (DISABLED) | TMK GXP | 41.0602 | 290.7575 | -249.6974 | 2.3891 | 16.9182 | -14.529 | 780 | 120 | 660 | 45.3855 | 6.9824 | 38.4031
[20 empty] | FLE |  |  |  | 107.6266 | 3.852 | 254.1533 | 10.1968 |  |  | 20 | 0.38452 | 0 | 0 |  | TMK | 823.9741 | 494.2734 | 329.7007 | 15.6988 | 9.4172 | 6.2816 | 492 | 0 | 492 | 9.3739 | 0 | 9.3739
BELLS POND SUBSTATION (A1067-T1) | [11 empty] | Supporting info | [7 empty] | BELLS POND SUBSTATION (A1067-T1)-OLD | [14 empty] | GLD | 370.2375 | 119.3734 | 250.8641 | 8.9185 | 2.2857 | 6.6328 | 0 | 2 | -2 | 0 | 0.038296 | -0.038296
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER | RGA | 110.5756 | 652.2364 | -541.6608 | 2.1489 | 18.2909 | -16.142 | 0 | 0 | 0 | 0 | 0 | 0
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED | [23 empty] | CNL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down |  | CD1 | 0 | 1663.5902 | -1663.5902 | 0 | 31.6957 | -31.6957 | 0 | 0 | 0 | 0 | 0 | 0
CB442 | T1 110 KV INCOMER | 110 | 209.9456 | 292 | 165 | 31.4367 | 185 | 35.2472 | POWER TRANSFORMER RATING AT 40 MVA | NO | N/A | BPD-T1-CB442 | ZoneSubstation | BPD | T1 | 110 | YES | YES |  | CB442 | 110 KV INCOMER | 310 | q | 0 | 0 | 100.0544 | 19.0629 | 292 | u | 0 | 0 | 0 | 0 | NO | CD2 | 131.5438 | 534.5006 | -402.9568 | 2.5062 | 11.1859 | -8.6797 | 1920 | 40 | 1880 | 36.5809 | 0.7621 | 35.8188
CB3602 | 33 KV TO CNR FROM T1 | 33 | 800 | 492 | 390 | 22.2915 | 440 | 25.1494 | AIR BREAK SWITCH-3604 ABS | NO | N/A | BPD-T1-CB3602 | SubTransmission | CB3602_CNR | T1 | 33 | NO | YES |  | CB3602 | 33 KV TO CNR | 345 | p | 455 | 26.0067 | 0 | 0 | 492 | u | 0 | 0 | 0 | 0 | NO | TWZ | 438.6399 | 426.6125 | 12.0274 | 15.4829 | 8.1281 | 7.3548 | 6 | 100 | -94 | 0.11432 | 5.7158 | -5.6015
CB35 | T1 BUS 11 KV INCOMER | 11 | 1543.7173 | 2208 | 1230 | 23.9033 | 1385 | 26.9155 | POWER TRANSFORMER RATING AT 30 MVA | NO | N/A | BPD-T1-CB35 | ZoneSubstation | BPD | T1 | 11.22 | YES | YES |  | CB35 | 11 KV INCOMER | 2186 | q | 0 | 0 | 642.2827 | 12.4819 | 2208 | u | 0 | 0 | 0 | 0 | NO |  | 5 | 7 |  | 6 | 8 |  | 11 | 13 |  | 12 | 14
CB31 | T1 BUS 11 KV BUS COUPLER | 11 | 1250 | 1000 | 800 | 15.5469 | 900 | 17.4902 | CABLE-6-1C 1000MM2 AL XLPE MDPE | NO | N/A | BPD-T1-CB31 | ZoneSubstation | BPD |  | 11.22 | NO | YES | Manual entry from previous Switching Digrams | CB31 | 11 KV BUS COUPLER | 1250 | u | 0 | 0 | 0 | 0 | 1000 | u | 0 | 0 | 0 | 0 | NO
CB1 | WAIHUNA | 11 | 386.9283 | 400 | 305 | 5.9273 | 345 | 6.7046 | OH LINE-JAGUAR | YES | YES | BPD-T1-CB1 | DistributionFeeder | CB1_Waihuna | T1 | 11.22 | NO | NO |  | CB1 | WAIHUNA | 350 | p | 36.9283 | 0.71765 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES
CB2 | TAWAI | 11 | 386.9283 | 400 | 305 | 5.9273 | 345 | 6.7046 | OH LINE-JAGUAR | YES | YES | BPD-T1-CB2 | DistributionFeeder | CB2_Tawai | T1 | 11.22 | NO | NO |  | CB2 | TAWAI | 350 | p | 36.9283 | 0.71765 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES
BELLS POND SUBSTATION (A1067-T2) | [11 empty] | Supporting info | [7 empty] | BELLS POND SUBSTATION (A1067-T2)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB482 | T2 110 KV INCOMER | 110 | 104.9728 | 146 | 80 | 15.242 | 90 | 17.1473 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | BPD-T2-CB482 | ZoneSubstation | BPD | T2 | 110 | NO | YES |  | CB482 | 110 KV INCOMER | 150 | q | 0 | 0 | 45.0272 | 8.5788 | 146 | u | 0 | 0 | 0 | 0 | NO
CB522 | 33 KV TO CNR FROM T2 | 33 | 582.7931 | 370 | 295 | 16.8615 | 330 | 18.862 | OH LINE-JAGUAR | NO | N/A | BPD-T2-CB522 | SubTransmission | CB522_CNR |  | 33 | NO | NO |  | CB522 | 33 KV TO CNR | 470 | p | 112.7931 | 6.447 | 0 | 0 | 370 | u | 0 | 0 | 0 | 0 | NO
CB36 | T2 BUS 11 KV INCOMER | 11 | 771.8586 | 1100 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | BPD-T2-CB36 | ZoneSubstation | BPD | T2 | 11.22 | NO | YES |  | CB36 | 11 KV INCOMER | 900 | q | 0 | 0 | 128.1414 | 2.4902 | 1104 | q | 0 | 0 | 4 | 0.077734 | NO
CB32 | T2 BUS 11 KV BUS COUPLER | 11 | 1250 | 1000 | 800 | 15.5469 | 900 | 17.4902 | CABLE-6-1C 1000MM2 AL XLPE MDPE | NO | N/A | BPD-T2-CB32 | ZoneSubstation | BPD |  | 11.22 | NO | YES | Manual entry from previous Switching Digrams | CB32 | 11 KV BUS COUPLER | 1250 | u | 0 | 0 | 0 | 0 | 1000 | u | 0 | 0 | 0 | 0 | NO
CB15 | T2 BUS INJECTION PLANT | 11 | 200 | 60 | 45 | 0.87451 | 50 | 0.97168 | CABLE-3C 185MM2 AL XLPE | NO | N/A | BPD-T2-CB15 | DistributionFeeder | Manual entry |  | 11.22 | NO | NO | Manual entry from previous Switching Digrams | CB15 | INJECTION PLANT | 200 | u | 0 | 0 | 0 | 0 | 30 | p | 30 | 0.58301 | 0 | 0 | NO
CB11 | WAIHAO DOWNS IRR. | 11 | 239.7 | 400 | 190 | 3.6924 | 215 | 4.1782 | CABLE - 3C 95MM2 AL XLPE CWS HDPE | YES | NO | BPD-T2-CB11 | DistributionFeeder | CB11_Waihao Downs | T2 | 11.22 | NO | NO |  | CB11 | WAIHAO DOWNS IRR. | 350 | q | 0 | 0 | 110.3 | 2.1435 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB12 | IKAWAI | 11 | 339.15 | 400 | 270 | 5.2471 | 305 | 5.9273 | CABLE-3C 300MM² AL XLPE MDPE | YES | YES | BPD-T2-CB12 | DistributionFeeder | CB12_Ikawai | T2 | 11.22 | NO | NO |  | CB12 | IKAWAI | 350 | q | 0 | 0 | 10.85 | 0.21085 | 400 | u | 0 | 0 | 0 | 0 | YES
CB13 | WAIKAKAHI | 11 | 339.15 | 400 | 270 | 5.2471 | 305 | 5.9273 | CABLE-3C 300MM² AL XLPE MDPE | YES | YES | BPD-T2-CB13 | DistributionFeeder | CB13_Waikakahi | T2 | 11.22 | NO | NO |  | CB13 | WAIKAKAHI | 350 | q | 0 | 0 | 10.85 | 0.21085 | 400 | u | 0 | 0 | 0 | 0 | YES
[20 empty] | BPD |  |  |  | 641.6496 | 33.889 | 1047.5057 | 45.1791 |  |  | 30 | 0.58301 | 4 | 0.077734
COONEY'S ROAD SUBSTATION (C1) | [11 empty] | Supporting info | [7 empty] | COONEY'S ROAD SUBSTATION (C1)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB642 | T1 HV 33 KV | 33 | 582.7931 | N/A | 465 | 26.5783 | 520 | 29.722 | OH LINE-JAGUAR | NO | N/A | CNR-CB642 | SubTransmission | CB642_CNR |  | 33 | NO | YES |  | CB642 | T1 HV 33 KV | 387 | p | 195.7931 | 11.1911 | 0 | 0 | 368 | p |  | 0 |  | 0 | NO
CB35 | T1 LV 11 KV | 11 | 787.2958 | 1104 | 625 | 11.9078 | 705 | 13.4321 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | CNR-CB35 | SecondarySubstation | CNR |  | 11 | NO | YES |  | CB35 | T1 LV 11 KV | 1160 | q | 0 | 0 | 372.7042 | 7.101 | 960 | p | 144 | 2.7436 | 0 | 0 | NO
CB36 | STU ALTERNATE FEED | 11 | 125 | 144 | 100 | 1.9053 | 85 | 1.6195 | 1.8 MVA WINTER | NO | N/A | CNR-CB36 | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement | CB36 | STU ALTERNATE FEED | 125 | u | 0 | 0 | 0 | 0 | 150 | q | 0 | 0 | 6 | 0.11432 | NO
|  | 11 | 125 | 144 | 100 | 1.9053 | 35 | 0.66684 | 0.8 MVA SUMMER | - | - |  | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement |  |  | 125 | u | 0 | 0 | 0 | 0 | 150 | q | 0 | 0 | 6 | 0.11432
|  | 11 | 125 | 144 | 100 | 1.9053 | 25 | 0.47631 | 0.6 MW BPD OFFLOAD | - | - |  | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement |  |  | 125 | u | 0 | 0 | 0 | 0 | 150 | q | 0 | 0 | 6 | 0.11432
CB31 | BUS COUPLER BUS A | 11 | 1104 | 1200 | 880 | 16.7663 | 990 | 18.862 | CIRCUIT BREAKER-CNR-CB35-PROTECTION | NO | N/A | CNR-CB31 | SecondarySubstation | CNR |  | 11 | NO | NO |  | CB31 | BUS COUPLER BUS A | 1250 | q | 0 | 0 | 146 | 2.7817 |  |  | 0 | 0 | 0 | 0
CB32 | BUS COUPLER BUS B | 11 | 1104 | 1200 | 880 | 16.7663 | 990 | 18.862 | CIRCUIT BREAKER-CNR-CB35-PROTECTION | NO | N/A | CNR-CB32 | SecondarySubstation | CNR |  | 11 | NO | NO |  | CB32 | BUS COUPLER BUS B | 1250 | q | 0 | 0 | 146 | 2.7817 |  |  | 0 | 0 | 0 | 0
CB8 | CANNING PLANT | 11 | 378.9072 | 402 | 300 | 5.7158 | 340 | 6.4779 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB8 | DistributionFeeder | CB8_Drier 2 |  | 11 | NO | NO |  | CB8 | CANNING PLANT | 529 | q | 0 | 0 | 150.0928 | 2.8597 | 402 | u | 0 | 0 | 0 | 0 | NO
CB9 | WET PROCESS | 11 | 394.695 | 402 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB9 | DistributionFeeder | CB9_WetProcess |  | 11 | NO | NO |  | CB9 | WET PROCESS | 529 | q | 0 | 0 | 134.305 | 2.5589 | 402 | u | 0 | 0 | 0 | 0 | NO
CB11 | BOILER_CHILLER NO. 1 | 11 | 378.9072 | 402 | 300 | 5.7158 | 340 | 6.4779 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB11 | DistributionFeeder | CB11_Boiler/Chiller 1 |  | 11 | NO | NO |  | CB11 | BOILER_CHILLER NO. 1 | 529 | q | 0 | 0 | 150.0928 | 2.8597 | 402 | u | 0 | 0 | 0 | 0 | NO
CB12 | OFFICE | 11 | 394.695 | 402 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB12 | DistributionFeeder | CB12_Office |  | 11 | NO | NO |  | CB12 | OFFICE | 529 | q | 0 | 0 | 134.305 | 2.5589 | 402 | u | 0 | 0 | 0 | 0 | NO
[20 empty] | CNR |  |  |  | 195.7931 | 11.1911 | 1233.4998 | 23.5013 |  |  | 144 | 2.7436 | 18 | 0.34295
STUDHOLME GXP (T5 & T6) | [11 empty] | Supporting info | [7 empty] | STUDHOLME GXP (T5 & T6)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1 | OTAIO | 11 | 352.9388 | 360 | 280 | 5.4307 | 315 | 6.1096 | CABLE-3C-300MM² AL XLPE HDPE | YES | NO | STU-CB1 | DistributionFeeder | CB1_Otaio |  | 11.198 | NO | NO |  | CB1 | OTAIO | 350 | p | 2.9388 | 0.056999 | 0 | 0 | 360 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2 | GLENAVY | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | YES | YES | STU-CB2 | DistributionFeeder | CB2_Glenavy |  | 11.198 | NO | NO |  | CB2 | GLENAVY | 350 | p | 2.9388 | 0.056999 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES
CB3 | WAIMATE | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | YES | NO | STU-CB3 | DistributionFeeder | CB3_Waimate |  | 11.198 | NO | NO |  | CB3 | WAIMATE | 350 | p | 2.9388 | 0.056999 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB4 | (AEL)-T/P CB2812 INCOMER FROM T5 | 11 | 524 | 900 | 415 | 8.0491 | 470 | 9.1159 | POWER TRANSFORMER RATING AT 10.16 MVA | NO | N/A | STU-CB4 | GXP | STU_GXP | T5 | 11.198 | NO | YES |  | CB4 | (AEL)-T/P CB2812 INCOMER FROM T5 |  | p | 0 | 0 | 0 | 0 | 900 | u | 0 | 0 | 0 | 0 | NO
CB5 | BUS COUPLER | 11 | 744 | 744 | 595 | 11.5403 | 665 | 12.898 | CIRCUIT BREAKER-STU-CB5-PROTECTION | NO | N/A | STU-CB5 | GXP | STU |  | 11.198 | YES | NO |  | CB5 | BUS COUPLER |  | p | 0 | 0 | 0 | 0 | 756 | q | 0 | 0 | 12 | 0.23275 | NO
CB6 | (AEL)-T/P CB2812 INCOMER FROM T6 | 11 | 524 | 900 | 415 | 8.0491 | 470 | 9.1159 | POWER TRANSFORMER RATING AT 10.16 MVA | NO | N/A | STU-CB6 | GXP | STU_GXP | T6 | 11.198 | NO | YES |  | CB6 | (AEL)-T/P CB2812 INCOMER FROM T6 |  | p | 0 | 0 | 0 | 0 | 900 | u | 0 | 0 | 0 | 0 | NO
CB7 | WAIHAORUNGA | 11 | 352.9388 | 360 | 280 | 5.4307 | 315 | 6.1096 | CABLE-3C-300MM² AL XLPE HDPE | YES | YES | STU-CB7 | DistributionFeeder | CB7_Waihaorunga |  | 11.198 | NO | NO |  | CB7 | WAIHAORUNGA | 350 | p | 2.9388 | 0.056999 | 0 | 0 | 360 | u | 0 | 0 | 0 | 0 | YES
CB8 | MT. STUDHOLME | 11 | 247 | 360 | 195 | 3.7821 | 220 | 4.267 | OH LINE-70MM² CU | YES | NO | STU-CB8 | DistributionFeeder | CB8_Mt Studholme |  | 11.198 | NO | NO |  | CB8 | MT. STUDHOLME | 350 | q | 0 | 0 | 103 | 1.9977 | 360 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB9 | MORVEN | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | YES | YES | STU-CB9 | DistributionFeeder | CB9_Morven |  | 11.198 | NO | NO |  | CB9 | MORVEN | 350 | p | 2.9388 | 0.056999 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES
[20 empty] | STU |  |  |  | 14.6938 | 0.28499 | 103 | 1.9977 |  |  | 0 | 0 | 12 | 0.23275
TIMARU GXP (TP-TIM T3, T4 & T6) | [11 empty] | Supporting info | [7 empty] | TIMARU GXP (TP-TIM T3, T4 & T6)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB2662 | WAIPOPO | 11 | 276.287 | 400 | 220 | 4.1916 | 245 | 4.6679 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB2662 | DistributionFeeder | CB2662_Waipopo |  | 11 | NO | NO |  | CB2662 | WAIPOPO | 945 | q | 0 | 0 | 668.713 | 12.7407 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2672 | WASHDYKE | 11 | 276.287 | 400 | 220 | 4.1916 | 245 | 4.6679 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB2672 | DistributionFeeder | CB2672_Washdyke |  | 11 | NO | NO |  | CB2672 | WASHDYKE | 945 | q | 0 | 0 | 668.713 | 12.7407 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2682 | SHOWGROUNDS HILL & RIPPLE PLANT 1 | 11 | 345 | 400 | 275 | 5.2395 | 310 | 5.9063 | CABLE-3X 1C 400MM2 AL XLPE HDPE | YES | NO | TIM-CB2682 | DistributionFeeder | CB2682_Showgrounds Hill |  | 11 | YES | NO |  | CB2682 | Showgrounds HILL | 345 | u | 0 | 0 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2692 | TIM - NST 1 | 11 | 806.265 | 1184 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | TIM-CB2692 | SubTransmission | CB2692_North ST.1 |  | 11 | NO | NO |  | CB2692 | NORTH ST. 1 | 810 | q | 0 | 0 | 3.735 | 0.071161 | 1184 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2702 | MORGANS ROAD | 11 | 188.0321 | 400 | 150 | 2.8579 | 165 | 3.1437 | CABLE-3C 150MM² AL PILC STA | YES | NO | TIM-CB2702 | DistributionFeeder | CB2702_Morgans Rd |  | 11 | NO | NO |  | CB2702 | Morgans Road | 180 | p | 8.0321 | 0.15303 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2712 | MOUNTAIN VIEW ROAD | 11 | 368.4526 | 400 | 290 | 5.5252 | 330 | 6.2873 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | TIM-CB2712 | DistributionFeeder | CB2712_Mountain View Rd |  | 11 | NO | NO |  | CB2712 | Mountainview | 360 | p | 8.4526 | 0.16104 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2728 | BUS A-C COUPLER | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2728 - PROTECTION | YES | NO | TIM-CB2728 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB | CB2728 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2732 | ALPINE TIMARU (ATM) T1 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2732 | SubTransmission | CB2732_ATM_T1 |  | 11 | NO | YES |  | CB2732 | AEL T1 | 1110 | p | 10.544 | 0.20089 | 0 | 0 | 1068 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2742 | LEVELS PLAIN | 11 | 394.4936 | 400 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | TIM-CB2742 | DistributionFeeder | CB2742_Levels Plain |  | 11 | NO | NO |  | CB2742 | LEVELS PLAIN | 390 | p | 4.4936 | 0.085614 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2752 | TRANSPOWER T3 INCOMER | 11 | 2534 | 1544 | 1235 | 23.5299 | 1385 | 26.3878 | CABLE-TIM-CBL-T3-CB2752-CABLE | YES | NO | TIM-CB2752 | GXP | TIM_GXP | T3 | 11 | NO | NO |  | CB2752 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2762 | AEL YARD | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2762 | DistributionFeeder | CB2762_AEL Yard |  | 11 | NO | NO |  | CB2762 | AEL Yard | 280 | p | 0.0296 | 0.00056396 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2772 | TIM - GRM D | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2772 | SubTransmission | TIM_GRMD_SUBTRANS |  | 11 | NO | NO |  | CB2772 | GRM - TIM D | 410 | p | 2.566 | 0.048889 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2788 | BUS A-B COUPLER | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2788 - PROTECTION | YES | NO | TIM-CB2788 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB | CB2788 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2812 | TIM - GRM C | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2812 | SubTransmission | TIM_GRMC_SUBTRANS |  | 11 | NO | NO |  | CB2812 | GRM - TIM C | 410 | p | 2.566 | 0.048889 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2822 | TIM - GRM B | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2822 | SubTransmission | TIM_GRMB_SUBTRANS |  | 11 | NO | NO |  | CB2822 | GRM - TIM B | 410 | p | 2.566 | 0.048889 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2832 | GRANTS ROAD | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2832 | DistributionFeeder | CB2832_Grants Rd |  | 11 | NO | NO |  | CB2832 | Grants RD | 280 | p | 0.0296 | 0.00056396 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2842 | TRANSPOWER T4 INCOMER | 11 | 2466.8602 | 1544 | 1235 | 23.5299 | 1385 | 26.3878 | POWER TRANSFORMER RATING AT 47 MVA | YES | NO | TIM-CB2842 | GXP | TIM_GXP | T4 | 11 | NO | YES |  | CB2842 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2852 | HADLOW | 11 | 260.4067 | 400 | 205 | 3.9058 | 230 | 4.3821 | CABLE-3C 185MM² AL XLPE HDPE | YES | NO | TIM-CB2852 | DistributionFeeder | CB2852_Hadlow |  | 11 | NO | NO |  | CB2852 | HADLOW | 260 | p | 0.40669 | 0.0077484 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2862 | MEADOWS ROAD | 11 | 394.4936 | 400 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3C 300MM² AL XLPE HDPE | YES | NO | TIM-CB2862 | DistributionFeeder | CB2862_Meadows Rd |  | 11 | NO | NO |  | CB2862 | Meadows RD | 390 | p | 4.4936 | 0.085614 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2878 | BUS B-C COUPLER | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2878 - PROTECTION | YES | NO | TIM-CB2878 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB | CB2878 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2912 | TIM - GRM A | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2912 | SubTransmission | TIM_GRMA_SUBTRANS |  | 11 | NO | NO |  | CB2912 | GRM - TIM A | 410 | p | 2.566 | 0.048889 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2922 | ALPINE TIMARU (ATM) T2 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2922 | SubTransmission | CB2922_ATM_T2 |  | 11 | NO | YES |  | CB2922 | AEL T2 | 990 | p | 130.544 | 2.4872 | 0 | 0 | 1068 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2932 | TRANSPOWER T6 INCOMER | 11 | 2534 | 1544 | 1235 | 23.5299 | 1385 | 26.3878 | CABLE-TIM-CBL-T3-CB2752-CABLE | YES | NO | TIM-CB2932 | GXP | TIM_GXP | T6 | 11 | NO | NO |  | CB2932 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2942 | OLD NORTH ROAD | 11 | 280.8075 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | TIM-CB2942 | DistributionFeeder | CB2942_Old North Rd |  | 11 | NO | NO |  | CB2942 | Old North Road | 280 | p | 0.80746 | 0.015384 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2952 | HIGHFIELD | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2952 | DistributionFeeder | CB2952_Highfield |  | 11 | NO | NO |  | CB2952 | Highfield | 280 | p | 0.0296 | 0.00056396 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2968 | BUS C-A COUPLER | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2968 - PROTECTION | YES | NO | TIM-CB2968 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB | CB2968 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2972 | SMITHFIELD | 11 | 280.8075 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | TIM-CB2972 | DistributionFeeder | CB2972_Smithfield |  | 11 | NO | NO |  | CB2972 | Smithfield | 280 | p | 0.80746 | 0.015384 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2982 | TIM - NST 2 | 11 | 806.265 | 1184 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | TIM-CB2982 | SubTransmission | CB2982_North ST.2 |  | 11 | NO | NO |  | CB2982 | NORTH ST. 2 | 810 | q | 0 | 0 | 3.735 | 0.071161 | 1184 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB2992 | GOULDS ROAD & RIPPLE PLANT 2 | 11 | 345 | 400 | 275 | 5.2395 | 310 | 5.9063 | CABLE-TIM-CB2992 | YES | NO | TIM-CB2992 | DistributionFeeder | CB2992_Goulds Road |  | 11 | YES | NO |  | CB2992 | Goulds Road | 345 | u | 0 | 0 | 0 | 0 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB3002 | ELGINSHIRE | 11 | 236.0033 | 400 | 185 | 3.5247 | 210 | 4.001 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB3002 | DistributionFeeder | CB3002_Elginshire |  | 11 | NO | NO |  | CB3002 | Elginshire | 945 | q | 0 | 0 | 708.9967 | 13.5082 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB3012 | AROWHENUA | 11 | 197.4144 | 400 | 155 | 2.9531 | 175 | 3.3342 | CABLE - 3C 150MM² AL PILC STA | YES | NO | TIM-CB3012 | DistributionFeeder | CB3012_Arowhenua |  | 11 | NO | NO |  | CB3012 | Arowhenua | 945 | q | 0 | 0 | 747.5856 | 14.2434 | 400 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
[20 empty] | TIM |  |  |  | 178.9342 | 3.4092 | 2801.4782 | 53.3753 |  |  | 0 | 0 | 0 | 0
GRASMERE STREET SWITCHING STATION (TE901) | [11 empty] | Supporting info | [7 empty] | GRASMERE STREET SWITCHING STATION (TE901)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB2 | WHITE STREET | 11 | 160.5975 | 304 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 0.15IN² CU PILC STAS | YES | NO | GRM-CB2 | DistributionFeeder | CB2_White St |  | 11 | NO | NO |  | CB2 | WHITE STREET | 152 | p | 8.5975 | 0.1638 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB3 | GRM - TIM A & VT3 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB3 | SubTransmission | TIM_GRMA_SUBTRANS |  | 11 | NO | NO |  | CB3 | TIM - GRM A & VT3 | 550 | q | 0 | 0 | 137.434 | 2.6185 | 600 | u | 0 | 0 | 0 | 0 | NO
CB4 | GRM - HNT A | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWA | YES | NO | GRM-CB4 | SubTransmission | CB4_GRM-HNT A |  | 11 | NO | NO |  | CB4 | GRM - HNT A | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB5 | NILE STREET & LS1 | 11 | 233.415 | 304 | 185 | 3.5247 | 210 | 4.001 | CABLE-3C 300MM² AL PILC SWAS | YES | NO | GRM-CB5 | DistributionFeeder | CB5_Nile St |  | 11 | NO | NO |  | CB5 | NILE STREET & LS1 | 224 | p | 9.415 | 0.17938 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB6 | PARKVIEW TCE | 11 | 228 | 304 | 180 | 3.4295 | 205 | 3.9058 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | GRM-CB6 | DistributionFeeder | CB6_Parkview Terrace |  | 11 | NO | NO |  | CB6 | PARKVIEW TCE | 224 | p | 4 | 0.07621 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB7 | DOUGLAS STREET | 11 | 235.904 | 304 | 185 | 3.5247 | 210 | 4.001 | CABLE-3C 185MM² AL XLPE HDPE | YES | NO | GRM-CB7 | DistributionFeeder | CB7_Douglas St |  | 11 | NO | NO |  | CB7 | DOUGLAS STREET | 196 | p | 39.904 | 0.76027 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB8 | GRM - TIM B & VT8 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB8 | SubTransmission | TIM_GRMB_SUBTRANS |  | 11 | NO | NO |  | CB8 | TIM - GRM B & VT8 | 550 | q | 0 | 0 | 137.434 | 2.6185 | 600 | u | 0 | 0 | 0 | 0 | NO
CB9 | GRM - NST A | 11 | 115 | 400 | 90 | 1.7147 | 100 | 1.9053 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | GRM-CB9 | SubTransmission | CB9_GRM-NST A |  | 11 | NO | NO |  | CB9 | GRM - NST A | 300 | q | 0 | 0 | 185 | 3.5247 | 400 | u | 0 | 0 | 0 | 0 | NO
CB10 | ASHBURY PARK | 11 | 201.4 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.25IN² AL PILC STAS | YES | NO | GRM-CB10 | DistributionFeeder | CB10_Ashbury Park |  | 11 | NO | NO |  | CB10 | ASHBURY PARK | 196 | p | 5.4 | 0.10288 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB12 | SELWYN STREET | 11 | 176.1066 | 304 | 140 | 2.6674 | 155 | 2.9531 | CABLE-3C 300MM² AL PILC | YES | NO | GRM-CB12 | DistributionFeeder | CB12_Selwyn St |  | 11 | NO | NO |  | CB12 | SELWYN STREET | 152 | p | 24.1066 | 0.45929 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB13 | GRM - HNT B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | GRM-CB13 | SubTransmission | CB13_GRM-HNT B |  | 11 | NO | NO |  | CB13 | GRM - HNT B | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB14 | GRM - TIM C & VT14 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB14 | SubTransmission | TIM_GRMC_SUBTRANS |  | 11 | NO | NO |  | CB14 | TIM - GRM C & VT14 | 550 | q | 0 | 0 | 137.434 | 2.6185 | 600 | u | 0 | 0 | 0 | 0 | NO
CB15 | PARK LANE | 11 | 172.6194 | 304 | 135 | 2.5721 | 155 | 2.9531 | CABLE-3C 300MM² AL PILC SWA | YES | NO | GRM-CB15 | DistributionFeeder | CB15_Park Lane |  | 11 | NO | NO |  | CB15 | PARK LANE | 165 | p | 7.6194 | 0.14517 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB16 | EVANS STREET | 11 | 167.96 | 304 | 130 | 2.4768 | 150 | 2.8579 | CABLE-3C 0.15IN² CU PILC STAS | YES | NO | GRM-CB16 | DistributionFeeder | CB16_Evans St |  | 11 | NO | NO |  | CB16 | EVANS STREET | 170 | q | 0 | 0 | 2.04 | 0.038867 | 200 | p | 104 | 1.9815 | 0 | 0 | NO
CB17 | JUNE STREET & LS2 | 11 | 232.56 | 304 | 185 | 3.5247 | 205 | 3.9058 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | GRM-CB17 | DistributionFeeder | CB17_June St |  | 11 | NO | NO |  | CB17 | JUNE STREET & LS2 | 224 | p | 8.56 | 0.16309 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB18 | GRM - NST B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | GRM-CB18 | SubTransmission | CB18_GRM-NST B |  | 11 | NO | NO |  | CB18 | GRM - NST B | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB19 | GRM - TIM D & VT19 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB19 | SubTransmission | TIM_GRMD_SUBTRANS |  | 11 | NO | NO |  | CB19 | TIM - GRM D & VT19 | 550 | q | 0 | 0 | 137.434 | 2.6185 | 600 | u | 0 | 0 | 0 | 0 | NO
CB20 | HOBBS STREET | 11 | 202.7789 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.4IN² AL PILC DSTA | YES | NO | GRM-CB20 | DistributionFeeder | CB20_Hobbs St |  | 11 | NO | NO |  | CB20 | HOBBS STREET | 196 | p | 6.7789 | 0.12915 | 0 | 0 | 300 | p | 4 | 0.07621 | 0 | 0 | NO
CB31 | BUS COUPLER BUS A | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - GRM-CB31 - RATING | YES | NO | GRM-CB31 | DistributionFeeder | CB2_White St |  | 11 | NO | NO | Manual entry based on substation drawing T269-01 rating of the CB | CB31 | BUS COUPLER BUS A | 3000 | u | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
CB32 | BUS COUPLER BUS B | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - GRM-CB32 - RATING | YES | NO | GRM-CB32 | DistributionFeeder | CB2_White St |  | 11 | NO | NO | Manual entry based on substation drawing T269-01 rating of the CB | CB32 | BUS COUPLER BUS B | 3000 | u | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
[20 empty] | GRM |  |  |  | 114.3814 | 2.1793 | 744.384 | 14.1824 |  |  | 140 | 2.6674 | 0 | 0
HUNT STREET SWITCHING STATION (TE903) | [11 empty] | Supporting info | [7 empty] | HUNT STREET SWITCHING STATION (TE903)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1 | HARPER STREET | 11 | 224.4375 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB1 | DistributionFeeder | CB1_Harper St |  | 11 | NO | NO |  | CB1 | HARPER STREET | 220 | p | 4.4375 | 0.084546 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB2 | WILSON STREET | 11 | 110.4061 | 200 | 85 | 1.6195 | 95 | 1.81 | OH LINE-GOPHER | YES | NO | HNT-CB2 | DistributionFeeder | CB2_Wilson St |  | 11 | NO | NO |  | CB2 | WILSON STREET | 104 | p | 6.4061 | 0.12205 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB3 | GRM - HNT A & VT3 | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWA | YES | NO | HNT-CB3 | SubTransmission | CB3_HNT-GRM A |  | 11 | NO | NO |  | CB3 | GRM - HNT A & VT3 | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB4 | BAKER STREET | 11 | 209.304 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.25IN² AL PILC DSTA | YES | NO | HNT-CB4 | DistributionFeeder | CB4_Baker St |  | 11 | NO | NO |  | CB4 | BAKER STREET | 200 | p | 9.304 | 0.17727 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB5 | LE CREN STREET | 11 | 181.5117 | 200 | 145 | 2.7626 | 160 | 3.0484 | CABLE-3C 0.25IN² AL PILC SWA | YES | NO | HNT-CB5 | DistributionFeeder | CB5_Le Cren St |  | 11 | NO | NO |  | CB5 | LE CREN STREET | 175 | p | 6.5117 | 0.12407 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB6 | HNT - NST A & VT6 | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | HNT-CB6 | SubTransmission | CB6_HNT-NST A |  | 11 | NO | NO |  | CB6 | HNT - NST A & VT6 | 300 | q | 0 | 0 | 8.2313 | 0.15683 | 400 | u | 0 | 0 | 0 | 0 | NO
CB7 | CHURCH STREET -SOUTH SIDE | 11 | 160.474 | 200 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 0.15IN² AL PILC STAS | YES | NO | HNT-CB7 | DistributionFeeder | CB7_Church St SS |  | 11 | NO | NO |  | CB7 | CHURCH STREET -SOUTH SIDE | 170 | q | 0 | 0 | 9.526 | 0.18149 | 200 | u | 0 | 0 | 0 | 0 | NO
CB8 | SPARE (TEST CUBICLE ONLY) | 11 | N/A | 200 | 160 | 3.0484 | 180 | 3.4295 | NA | YES | NO | HNT-CB8 | DistributionFeeder | CB8_Spare |  | 11 | NO | NO |  | CB8 | SPARE (TEST CUBICLE ONLY) |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
CB9 | BUS COUPLER | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - HNT-CB9 - RATING | YES | NO | HNT-CB9 | DistributionFeeder | CB9_Bus coupler |  | 11 | NO | NO | Manual entry based on substation drawing T269-02 rating of the CB | CB9 | BUS COUPLER |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
CB10 | GIBSON STREET | 11 | 209.475 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB10 | DistributionFeeder | CB10_Gibson St |  | 11 | NO | NO |  | CB10 | GIBSON STREET | 200 | p | 9.475 | 0.18052 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB11 | RHODES STREET | 11 | 165.5937 | 200 | 130 | 2.4768 | 145 | 2.7626 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB11 | DistributionFeeder | CB11_Rhodes St |  | 11 | NO | NO |  | CB11 | RHODES STREET | 165 | p | 0.59374 | 0.011312 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB12 | GRM - HNT B & VT12 | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | HNT-CB12 | SubTransmission | CB12_HNT-GRM B |  | 11 | NO | NO |  | CB12 | GRM - HNT B & VT12 | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB13 | CLIFTON TCE | 11 | 203.49 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB13 | DistributionFeeder | CB13_Clifton Terrace |  | 11 | NO | NO |  | CB13 | CLIFTON TCE | 200 | p | 3.49 | 0.066493 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB14 | CHURCH STREET -NORTH SIDE | 11 | 157.4141 | 200 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 95MM² AL PILC SWAS | YES | NO | HNT-CB14 | DistributionFeeder | CB14_Church St NS |  | 11 | NO | NO |  | CB14 | CHURCH STREET -NORTH SIDE | 152 | p | 5.4141 | 0.10315 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB15 | HNT - NST B & VT15 | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | HNT-CB15 | SubTransmission | CB15_HNT-NST B |  | 11 | NO | NO |  | CB15 | HNT - NST B & VT15 | 300 | q | 0 | 0 | 8.2313 | 0.15683 | 400 | u | 0 | 0 | 0 | 0 | NO
CB16 | ARTHUR STREET | 11 | 224.4375 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB16 | DistributionFeeder | CB16_Arthur St |  | 11 | NO | NO |  | CB16 | ARTHUR STREET | 220 | p | 4.4375 | 0.084546 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB17 | SPARE | 11 | N/A | 200 | 160 | 3.0484 | 180 | 3.4295 | NA | YES | NO | HNT-CB17 | DistributionFeeder | CB17_Spare |  | 11 | NO | NO |  | CB17 | SPARE |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
[20 empty] | HNT |  |  |  | 50.0696 | 0.95395 | 31.0605 | 0.59178 |  |  | 0 | 0 | 0 | 0
NORTH STREET SWITCHING STATION (TE902) | [11 empty] | Supporting info | [7 empty] | NORTH STREET SWITCHING STATION (TE902)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB3 | REDRUTH NO. 1 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3/1C 300MM² AL CWS | YES | NO | NST-CB3 | DistributionFeeder | CB3_Redruth 1 |  | 11 | NO | NO |  | CB3 | REDRUTH 1 | 270 | p | 3.3264 | 0.063376 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB4 | ROSE STREET & VT4 | 11 | 228.48 | 304 | 180 | 3.4295 | 205 | 3.9058 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB4 | DistributionFeeder | CB4_Rose St |  | 11 | NO | NO |  | CB4 | ROSE STREET & VT4 | 220 | p | 8.48 | 0.16157 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB5 | CRAIGIE AVE & LS1 | 11 | 201.9192 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB5 | DistributionFeeder | CB5_Craigie Ave |  | 11 | NO | NO |  | CB5 | CRAIGIE AVE & LS1 | 200 | p | 1.9192 | 0.036566 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB6 | GRM - NST A | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | NST-CB6 | SubTransmission | CB9_GRM-NST A |  | 11 | NO | NO |  | CB6 | GRM - NST A | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB7 | HNT - NST A | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB7 | SubTransmission | CB6_HNT-NST A |  | 11 | NO | NO |  | CB7 | HNT - NST A | 300 | q | 0 | 0 | 8.2313 | 0.15683 | 400 | u | 0 | 0 | 0 | 0 | NO
CB8 | BARNARD STREET | 11 | 172.5214 | 200 | 135 | 2.5721 | 155 | 2.9531 | CABLE-3C 0.15IN² CU PILC STA | YES | NO | NST-CB8 | DistributionFeeder | CB8_Barnard St |  | 11 | NO | NO |  | CB8 | BARNARD STREET | 170 | p | 2.5214 | 0.04804 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB9 | PORT NO. 1 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | NST-CB9 | DistributionFeeder | CB9_Port 1 |  | 11 | NO | NO |  | CB9 | PORT 1 | 270 | p | 3.3264 | 0.063376 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB10 | FRASER STREET | 11 | 199.7639 | 304 | 155 | 2.9531 | 175 | 3.3342 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB10 | DistributionFeeder | CB10_Fraser St |  | 11 | NO | NO |  | CB10 | FRASER STREET | 200 | q | 0 | 0 | 0.23613 | 0.0044988 | 304 | u | 0 | 0 | 0 | 0 | NO
CB11 | HAYES STREET | 11 | 206.8696 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 0.25IN² AL PILC STAS | YES | NO | NST-CB11 | DistributionFeeder | CB11_Hayes St |  | 11 | NO | NO |  | CB11 | HAYES STREET | 200 | p | 6.8696 | 0.13088 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB12 | HIGH STREET | 11 | 206.8696 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 0.25IN² AL PILC SWA | YES | NO | NST-CB12 | DistributionFeeder | CB12_High St |  | 11 | NO | NO |  | CB12 | HIGH STREET | 200 | p | 6.8696 | 0.13088 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB13 | PORT NO. 2 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | NST-CB13 | DistributionFeeder | CB13_Port 2 |  | 11 | NO | NO |  | CB13 | PORT 2 | 270 | p | 3.3264 | 0.063376 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB14 | HNT - NST B | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB14 | SubTransmission | CB15_HNT-NST B |  | 11 | NO | NO |  | CB14 | HNT - NST B | 300 | q | 0 | 0 | 8.2313 | 0.15683 | 400 | u | 0 | 0 | 0 | 0 | NO
CB15 | GRM - NST B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB15 | SubTransmission | CB18_GRM-NST B |  | 11 | NO | NO |  | CB15 | GRM - NST B | 300 | q | 0 | 0 | 2.536 | 0.048317 | 400 | u | 0 | 0 | 0 | 0 | NO
CB16 | VICTORIA STREET & LS2 | 11 | 209.916 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB16 | DistributionFeeder | CB16_Victoria St |  | 11 | NO | NO |  | CB16 | VICTORIA STREET & LS2 | 200 | p | 9.916 | 0.18893 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB17 | STAFFORD STREET & VT17 | 11 | 135.8314 | 200 | 105 | 2.0005 | 120 | 2.2863 | CABLE-3C 0.075IN² CU PILC STAS | YES | NO | NST-CB17 | DistributionFeeder | CB17_Stafford St |  | 11 | NO | NO |  | CB17 | STAFFORD STREET & VT17 | 130 | p | 5.8314 | 0.1111 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | NO
CB18 | REDRUTH NO. 2 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE CWS MDPE | YES | NO | NST-CB18 | DistributionFeeder | CB18_Redruth 2 |  | 11 | NO | NO |  | CB18 | REDRUTH 2 | 270 | p | 3.3264 | 0.063376 | 0 | 0 | 304 | u | 0 | 0 | 0 | 0 | NO
CB31 | BUS COUPLER BUS A | 11 | 2500 | 1200 | 960 | 18.2905 | 1080 | 20.5768 | CIRCUIT BREAKER - NST-CB31 - PROTECTION | YES | NO | NST-CB31 | DistributionFeeder |  |  | 11 | NO | NO | Manual entry based on substation drawing T269-03 rating of the CB | CB31 | BUS COUPLER BUS A | 2500 | u | 0 | 0 | 0 | 0 | 1200 | u | 0 | 0 | 0 | 0 | NO
CB32 | BUS COUPLER BUS B | 11 | 2500 | 1200 | 960 | 18.2905 | 1080 | 20.5768 | CIRCUIT BREAKER - NST-CB32 - PROTECTION | YES | NO | NST-CB32 | DistributionFeeder |  |  | 11 | NO | NO | Manual entry based on substation drawing T269-03 rating of the CB | CB32 | BUS COUPLER BUS B | 2500 | u | 0 | 0 | 0 | 0 | 1200 | u | 0 | 0 | 0 | 0 | NO
CB35 | TIM - NST 1 & VT35 | 11 | 806.265 | 1188 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | NST-CB35 | SubTransmission | CB2692_North ST.1 |  | 11 | NO | NO |  | CB35 | NST - TIM 1 & VT35 | 1025 | q | 0 | 0 | 218.735 | 4.1675 | 1000 | p | 188 | 3.5819 | 0 | 0 | NO
CB36 | TIM - NST 2 & VT36 | 11 | 806.265 | 1188 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | NST-CB36 | SubTransmission | CB2982_North ST.2 |  | 11 | NO | NO |  | CB36 | NST - TIM 2 & VT36 | 1025 | q | 0 | 0 | 218.735 | 4.1675 | 1000 | p | 188 | 3.5819 | 0 | 0 | NO
[20 empty] | NST |  |  |  | 55.7128 | 1.0615 | 459.2406 | 8.7497 |  |  | 376 | 7.1638 | 0 | 0
ALPINE TIMARU (B774) | [11 empty] | Supporting info | [7 empty] | ALPINE TIMARU (B774)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB2732 | 11 KV INCOMER NO. 1 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | NO | N/A | TIM-CB2732 | SubTransmission | CB2732_ATM_T1 |  | 11 | NO | YES |  | CB2732 | 11 KV INCOMER NO. 1 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
CB2922 | 11 KV INCOMER NO. 2 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | NO | N/A | TIM-CB2922 | SubTransmission | CB2922_ATM_T2 |  | 11 | NO | YES |  | CB2922 | 11 KV INCOMER NO. 2 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
L406 | 33 KV INCOMER NO. 1 | 33 | 437.3866 | N/A | N/A | N/A | N/A | N/A | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | TIM-L406 | ZoneSubstation | ATM |  | 33 | NO | YES | Not a CB so no protection or SCADA alarms | L406 | 33 KV INCOMER NO. 1 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
L405 | 33 KV INCOMER NO. 2 | 33 | 437.3866 | N/A | N/A | N/A | N/A | N/A | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | TIM-L405 | ZoneSubstation | ATM_2 |  | 33 | NO | YES | Not a CB so no protection or SCADA alarms | L405 | 33 KV INCOMER NO. 2 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
L269 | SUBTRANSMISSION TO PLP | 33 | 171.4491 | 240 | 135 | 7.7163 | 150 | 8.5737 | CABLE-3/1C 95MM² AL XLPE PVC SCREENED | NO | N/A | TIM-L269 | SubTransmission | L269_PleasantPoint |  | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet | L269 | SUBTRANSMISSION TO PLP |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
L413 | SUBTRANSMISSION TO PAR NO. 1 | 33 | 196.6 | 240 | 155 | 8.8594 | 175 | 10.0026 | OH LINE-QUAIL | NO | N/A | TIM-L413 | SubTransmission | L413_L418_Pareora | T1 | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet | L413 | SUBTRANSMISSION TO PAR NO. 1 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
L418 | SUBTRANSMISSION TO PAR NO. 2 | 33 | 188.6266 | 240 | 150 | 8.5737 | 165 | 9.431 | OH LINE-MINK | NO | N/A | TIM-L418 | SubTransmission | L413_L418_Pareora | T2 | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet | L418 | SUBTRANSMISSION TO PAR NO. 2 |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
[20 empty] | ATM |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
PAREORA (B712) | [11 empty] | Supporting info | [7 empty] | PAREORA (B712)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB2332 | 33 KV TIM-PAR NO. 1 | 33 | 196.6 | 320 | 155 | 8.8594 | 175 | 10.0026 | OH LINE-QUAIL | NO | N/A | PAR-CB2332 | SubTransmission | L413_L418_Pareora | T1 | 33 | NO | NO |  | CB2332 | 33 KV TIM-PAR 1 | 400 | q | 0 | 0 | 203.4 | 11.6259 | 320 | u | 0 | 0 | 0 | 0 | NO
CB2342 | 33 KV INCOMER NO. 1 | 33 | 491.79 | 320 | 255 | 14.5752 | 285 | 16.2899 | CABLE-3/1C 400MM² AL XLPE HDPE SCREENED | NO | N/A | PAR-CB2342 | ZoneSubstation | PAR | T1 | 33 | NO | NO |  | CB2342 | 33 KV T1 | 400 | p | 91.79 | 5.2465 | 0 | 0 | 320 | u | 0 | 0 | 0 | 0 | NO
CB2358 | 33 KV BUS COUPLER NO. 1 | 33 | 400 | 320 | 255 | 14.5752 | 285 | 16.2899 | CIRCUIT BREAKER - PAR-CB2358 - PROTECTION | NO | N/A | PAR-CB2358 | ZoneSubstation | PAR |  | 33 | NO | NO | Manual entry from previous Switching Digrams | CB2358 | 33 KV BUS COUPLER 1 | 400 | u | 0 | 0 | 0 | 0 | 320 | u | 0 | 0 | 0 | 0 | NO
CB2368 | 33 KV BUS COUPLER NO. 2 | 33 | 400 | 320 | 255 | 14.5752 | 285 | 16.2899 | CIRCUIT BREAKER - PAR-CB2368 - PROTECTION | NO | N/A | PAR-CB2368 | ZoneSubstation | PAR |  | 33 | NO | NO | Manual entry from previous Switching Digrams | CB2368 | 33 KV BUS COUPLER 2 | 400 | u | 0 | 0 | 0 | 0 | 320 | u | 0 | 0 | 0 | 0 | NO
CB2372 | 33 KV INCOMER NO. 2 | 33 | 491.79 | 320 | 255 | 14.5752 | 285 | 16.2899 | CABLE-3/1C 400MM² AL XLPE HDPE SCREENED | NO | N/A | PAR-CB2372 | ZoneSubstation | PAR | T2 | 33 | NO | NO |  | CB2372 | 33 KV T2 | 400 | p | 91.79 | 5.2465 | 0 | 0 | 320 | u | 0 | 0 | 0 | 0 | NO
CB2382 | 33 KV TIM-PAR NO. 2 | 33 | 188.6266 | 320 | 150 | 8.5737 | 165 | 9.431 | OH LINE-MINK | NO | N/A | PAR-CB2382 | SubTransmission | L413_L418_Pareora | T2 | 33 | NO | NO |  | CB2382 | 33 KV TIM-PAR 2 | 400 | q | 0 | 0 | 211.3734 | 12.0816 | 320 | u | 0 | 0 | 0 | 0 | NO
CB31 | 11 KV BUS COUPLER | 11 | 1250 | 520 | 415 | 8.0649 | 465 | 9.0366 | CIRCUIT BREAKER - PAR-CB31 - PROTECTION | NO | N/A | PAR-CB31 | ZoneSubstation | PAR |  | 11.22 | NO | NO | Manual entry from previous Switching Digrams | CB31 | 11 KV BUS COUPLER | 1250 | u | 0 | 0 | 0 | 0 | 520 | u | 0 | 0 | 0 | 0 | NO
CB35 | 11 KV INCOMER NO. 1 | 11 | 771.8586 | 950 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | PAR-CB35 | ZoneSubstation | PAR | T1 | 11.22 | NO | YES |  | CB35 | 11 KV INCOMER NO. 1 | 800 | q | 0 | 0 | 28.1414 | 0.54689 | 950 | u | 0 | 0 | 0 | 0 | NO
CB36 | 11 KV INCOMER NO. 2 | 11 | 771.8586 | 950 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | PAR-CB36 | ZoneSubstation | PAR | T2 | 11.22 | NO | YES |  | CB36 | 11 KV INCOMER NO. 2 | 800 | q | 0 | 0 | 28.1414 | 0.54689 | 950 | u | 0 | 0 | 0 | 0 | NO
CB3 | WORKS NO. 1 | 11 | 301.53 | 300 | 240 | 4.6641 | 270 | 5.2471 | CABLE-3C 240MM² AL PILC DSTA | YES | NO | PAR-CB3 | DistributionFeeder | CB3_Works No. 1 |  | 11.22 | NO | NO |  | CB3 | WORKS NO. 1 | 300 | p | 1.53 | 0.029733 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | NO
CB4 | ST. ANDREWS | 11 | 256.8585 | 252 | 200 | 3.8867 | 225 | 4.3726 | OH LINE-DOG | YES | YES | PAR-CB4 | DistributionFeeder | CB4_St Andrews |  | 11.22 | NO | NO |  | CB4 | ST. ANDREWS | 300 | q | 0 | 0 | 43.1415 | 0.83839 | 300 | q | 0 | 0 | 48 | 0.93281 | YES
CB5 | WORKS NO. 2 | 11 | 301.53 | 300 | 240 | 4.6641 | 270 | 5.2471 | CABLE-3C 240MM² AL PILC DSTA | YES | NO | PAR-CB5 | DistributionFeeder | CB5_Works No. 2 |  | 11.22 | NO | NO |  | CB5 | WORKS NO. 2 | 300 | p | 1.53 | 0.029733 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | NO
CB6 | NORMANBY | 11 | 204.0399 | 252 | 160 | 3.1094 | 180 | 3.498 | OH LINE-RANGO | YES | YES | PAR-CB6 | DistributionFeeder | CB6_Normanby |  | 11.22 | NO | NO |  | CB6 | NORMANBY | 300 | q | 0 | 0 | 95.9601 | 1.8649 | 350 | q | 0 | 0 | 98 | 1.9045 | YES
CB7 | HOLMESTATION | 11 | 188.6266 | 252 | 150 | 2.915 | 165 | 3.2065 | OH LINE-MINK | YES | YES | PAR-CB7 | DistributionFeeder | CB7_Holmestation |  | 11.22 | NO | NO |  | CB7 | HOLMESTATION | 300 | q | 0 | 0 | 111.3734 | 2.1644 | 350 | q | 0 | 0 | 98 | 1.9045 | YES
[20 empty] | PAR |  |  |  | 186.64 | 10.5525 | 721.5311 | 29.6689 |  |  | 0 | 0 | 244 | 4.7418
PLEASANT POINT (B1212) | [11 empty] | Supporting info | [7 empty] | PLEASANT POINT (B1212)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
L250 | 33 KV TIM-PLP INCOMER | 33 | 171.4491 | 134 | 105 | 6.0016 | 120 | 6.8589 | CABLE-3/1C 95MM² AL XLPE PVC SCREENED | NO | N/A | PLP-L250 | SubTransmission | L269_PleasantPoint |  | 33 | NO | NO |  | L250 | 33 KV T1 INCOMER | 115 | p | 56.4491 | 3.2265 | 0 | 0 | 186 | q | 0 | 0 | 52 | 2.9722 | NO
CB1 | WAITAWA | 11 | 148 | 252 | 115 | 2.2349 | 130 | 2.5264 | OH LINE-FERRET | YES | YES | PLP-CB1 | DistributionFeeder | CB1_Waitawa |  | 11.22 | NO | NO |  | CB1 | WAITAWA | 180 | q | 0 | 0 | 32 | 0.62188 | 200 | p | 52 | 1.0105 | 0 | 0 | YES
CB2 | SUTHERLAND | 11 | 200.0091 | 252 | 160 | 3.1094 | 180 | 3.498 | CABLE-3C 150MM² AL PILC STA | YES | YES | PLP-CB2 | DistributionFeeder | CB2_Sutherlands |  | 11.22 | NO | NO |  | CB2 | SUTHERLAND | 196 | p | 4.0091 | 0.077911 | 0 | 0 | 200 | p | 52 | 1.0105 | 0 | 0 | YES
CB3 | 11 KV INCOMER | 11 | 321.6078 | 348 | 255 | 4.9556 | 285 | 5.5386 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | PLP-CB3 | ZoneSubstation | PLP |  | 11.22 | NO | YES |  | CB3 | 11 KV INCOMER | 345 | q | 0 | 0 | 23.3922 | 0.4546 | 558 | q | 0 | 0 | 210 | 4.0811 | NO
CB4 | TOTARA VALLEY | 11 | 189 | 252 | 150 | 2.915 | 170 | 3.3037 | OH LINE-MINK | YES | YES | PLP-CB4 | DistributionFeeder | CB4_Totara Valley |  | 11.22 | NO | NO |  | CB4 | TOTARA VALLEY | 196 | q | 0 | 0 | 7 | 0.13604 | 200 | p | 52 | 1.0105 | 0 | 0 | YES
CB5 | PLEASANT POINT TOWNSHIP | 11 | 131 | 252 | 100 | 1.9434 | 115 | 2.2349 | OH LINE-7/14 CU | YES | NO | PLP-CB5 | DistributionFeeder | CB5_Pleasant Point Township |  | 11.22 | NO | NO |  | CB5 | PLEASANT POINT TOWNSHIP | 196 | q | 0 | 0 | 65 | 1.2632 | 200 | p | 52 | 1.0105 | 0 | 0 | YES (DISABLED)
[20 empty] | PLP |  |  |  | 60.4582 | 3.3044 | 127.3922 | 2.4757 |  |  | 208 | 4.0422 | 262 | 7.0533
TEKAPO SUBSTATION (E197) | [11 empty] | Supporting info | [7 empty] | TEKAPO SUBSTATION (E197)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1042 | TRANSPOWER INCOMER | 33 | 242 | 183 | 145 | 8.2879 | 160 | 9.1452 | OH LINE-19/14 CU | NO | N/A | TKA-CB1042 | SubTransmission | SBT_33kV |  | 33 | NO | NO |  | CB1042 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
M346 | 33 KV MT COOK | 33 | 247 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE - 3-70MM2 CU | YES | YES | TKA_M11-M346 | SubTransmission | TKA_M11 |  | 33 | NO | NO |  | M346 | 33 KV MT COOK | 270 | q | 0 | 0 | 23 | 1.3146 | 150 | u | 0 | 0 | 0 | 0 | YES
M167 | 33 KV TEKAPO INCOMER | 33 | 183 | 150 | 120 | 6.8589 | 135 | 7.7163 | CIRCUIT BREAKER-TKA-CB1042-PROTECTION | NO | N/A | TEK-M167 | SubTransmission | SBT_33kV |  | 33 | NO | YES |  | M167 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
M202 | 11 KV TEKAPO INCOMER | 11 | 328.0399 | 400 | 260 | 4.9537 | 295 | 5.6205 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | TEK-M202 | ZoneSubstation | TEK |  | 11 | NO | YES |  | M202 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
M200 | HALDON-LILYBANK | 11 | 186.6183 | 276 | 145 | 2.7626 | 165 | 3.1437 | CABLE-1-3C 150 MM² AL PILC | YES | NO | TEK-M200 | DistributionFeeder | M200_Haldon_Lilybank |  | 11 | NO | NO |  | M200 | HALDON-LILYBANK | 186 | p | 0.6183 | 0.01178 | 0 | 0 | 276 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
M201 | SIMONS | 11 | 73.7094 | 250 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | YES | YES | TEK-M201 | DistributionFeeder | M201_Simons |  | 11 | NO | NO |  | M201 | SIMONS | 73 | p | 0.70939 | 0.013516 | 0 | 0 | 250 | u | 0 | 0 | 0 | 0 | YES
M205 | GODLEY | 11 | 73.7094 | 200 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | YES | YES | TEK-M205 | DistributionFeeder | M205_Godley |  | 11 | NO | NO |  | M205 | GODLEY | 73 | p | 0.70939 | 0.013516 | 0 | 0 | 200 | u | 0 | 0 | 0 | 0 | YES
M206 | TEKAPO TOWNSHIP | 11 | 186.6183 | 276 | 145 | 2.7626 | 165 | 3.1437 | CABLE-1-3C 150 MM² AL PILC | YES | NO | TEK-M206 | DistributionFeeder | M206_Tekapo Township |  | 11 | NO | NO |  | M206 | TEKAPO TOWNSHIP | 186 | p | 0.6183 | 0.01178 | 0 | 0 | 276 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
[20 empty] | TEK |  |  |  | 2.6554 | 0.050592 | 23 | 1.3146 |  |  | 0 | 0 | 0 | 0
UNWIN HUT SUBSTATION (E152) | [11 empty] | Supporting info | [7 empty] | UNWIN HUT SUBSTATION (E152)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
M302 | 33KV INCOMER | 33 | 26.2432 | 50 | 20 | 1.1432 | 20 | 1.1432 | POWER TRANSFORMER RATING AT 1.5 MVA | NO | N/A | UHT-M302 | ZoneSubstation | UHT |  | 33 | NO | YES |  | M302 | 33KV CB | 26 | p | 0.24319 | 0.0139 | 0 | 0 | 50 | u | 0 | 0 | 0 | 0 | NO
M158 | MT COOK VILLAGE 1 | 11 | 259.7 | 100 | 80 | 1.5242 | 90 | 1.7147 | CABLE-1-3C 150 MM² AL PILC | NO | N/A | UHT-M158 | DistributionFeeder | M158_Village |  | 11 | NO | NO |  | M158 | M158 11KV CB | 79 | p | 180.7 | 3.4428 | 0 | 0 | 100 | u | 0 | 0 | 0 | 0 | NO
M159 | MT COOK VILLAGE 2 | 11 | 259.7 | 100 | 80 | 1.5242 | 90 | 1.7147 | CABLE-1-3C 150 MM² AL PILC | NO | N/A | UHT-M159 | DistributionFeeder | M159_Village |  | 11 | NO | NO |  | M159 | M159 11KV CB | 79 | p | 180.7 | 3.4428 | 0 | 0 | 100 | u | 0 | 0 | 0 | 0 | NO
[20 empty] | UHT |  |  |  | 361.6432 | 6.8995 | 0 | 0 |  |  | 0 | 0 | 0 | 0
OLD MAN RANGE SUBSTATION (E352) | [11 empty] | Supporting info | [7 empty] | OLD MAN RANGE SUBSTATION (E352)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
M331 | 11KV RECLOSER | 11 | 73.7094 | 120 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | NO | N/A | OMR-M331 | SecondarySubstation | OMR |  | 11 | NO | YES |  | M331 | 11KV RECLOSER | 78.7 | q | 0 | 0 | 4.9906 | 0.095084 | 120 | u | 0 | 0 | 0 | 0 | YES
M338 | 22KV RECLOSER | 22 | 39.3648 | 60 | 30 | 1.1432 | 35 | 1.3337 | POWER TRANSFORMER RATING AT 1.5 MVA | YES | YES | OMR-M338 | DistributionFeeder | M338_Old Man Range |  | 22 | NO | YES |  | M338 | 22KV RECLOSER | 39.4 | q | 0 | 0 | 0.035209 | 0.0013416 | 60 | u | 0 | 0 | 0 | 0 | YES
[20 empty] | OMR |  |  |  | 0 | 0 | 5.0258 | 0.096426 |  |  | 0 | 0 | 0 | 0
HALDON/LILYBANK SUBSTATION (E117) | [11 empty] | Supporting info | [7 empty] | HALDON/LILYBANK SUBSTATION (E117)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
M82 | 11 KV RECLOSER | 11 | 52.4864 | 60 | 40 | 0.7621 | 45 | 0.85737 | POWER TRANSFORMER RATING AT 1 MVA | YES | NO | HLB-M82 | SecondarySubstation | HLB |  | 11 | NO | YES |  | M82 | 11 KV RECLOSER | 52.5 | q | 0 | 0 | 0.013612 | 0.00025934 | 60 | u | 0 | 0 | 0 | 0 | YES (DISBALED)
M86 | 22 KV RECLOSER | 22 | 26.2432 | 30 | 20 | 0.7621 | 20 | 0.7621 | POWER TRANSFORMER RATING AT 1 MVA | YES | YES | HLB-M86 | SecondarySubstation | HLB |  | 22 | NO | YES |  | M86 | 22 KV RECLOSER | 26.2 | p | 0.043194 | 0.0016459 | 0 | 0 | 30 | u | 0 | 0 | 0 | 0 | YES
M32 | LILYBANK | 22 | 73.7094 | N/A | N/A | N/A | N/A | N/A | OH LINE-HERRING | NO | N/A | HLB-M32 | DistributionFeeder | M32_Lilybank |  | 22 | NO | NO | Not a CB hence no SCADA alarms or protection | M32 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
M33 | HALDON | 22 | 73.7094 | N/A | N/A | N/A | N/A | N/A | OH LINE-HERRING | NO | N/A | HLB-M33 | DistributionFeeder | M33_Haldon |  | 22 | NO | NO | Not a CB hence no SCADA alarms or protection | M33 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
[20 empty] | HLB |  |  |  | 0.043194 | 0.0016459 | 0.013612 | 0.00025934 |  |  | 0 | 0 | 0 | 0
TEMUKA GXP (TP-TMK) | [11 empty] | Supporting info | [7 empty] | TEMUKA GXP (TP-TMK)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB132 | 110 KV TRANSPOWER T1 INCOMER | 110 | 283.4265 | 359 | 225 | 42.8683 | 255 | 48.584 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB132 | GXP | TMK_GXP | T1 | 110 | NO | YES |  | CB132 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
CB112 | 110 KV TRANSPOWER T2 INCOMER | 110 | 283.4265 | 358 | 225 | 42.8683 | 255 | 48.584 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB112 | GXP | TMK_GXP | T2 | 110 | NO | YES |  | CB112 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
CB1252 | 33 KV TRANSPOWER T1 INCOMER | 33 | 928.0501 | 496 | 395 | 22.9837 | 445 | 25.893 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB1252 | GXP | TMK_GXP | T1 | 33.594 | NO | YES |  | CB1252 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
CB1232 | 33 KV TRANSPOWER T2 INCOMER | 33 | 928.0501 | 496 | 395 | 22.9837 | 445 | 25.893 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB1232 | GXP | TMK_GXP | T2 | 33.594 | NO | YES |  | CB1232 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
CB1192 | CLANDEBOYE NO. 1 | 33 | 407.1941 | 510 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1192 | SubTransmission | CB1192_Clandeboye No.1 |  | 33.594 | NO | NO |  | CB1192 | CLANDEBOYE NO. 1 | 500 | q | 0 | 0 | 92.8059 | 5.4001 | 510 | u | 0 | 0 | 0 | 0 | NO
CB1202 | RANGITATA NO. 2 | 33 | 207.2308 | 462 | 165 | 9.6008 | 185 | 10.7645 | CABLE-1-3C 95 MM² AL XLPE | YES | NO | TMK-CB1202 | SubTransmission | CB1202_Rangitata |  | 33.594 | NO | NO |  | CB1202 | RANGITATA |  | p | 0 | 0 | 0 | 0 | 462 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
CB1212 | TEMUKA NO. 1 | 33 | 426.3301 | 582 | 340 | 19.7834 | 380 | 22.1109 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1212 | SubTransmission | CB1212_Temuka No.1 |  | 33.594 | NO | NO |  | CB1212 | TEMUKA NO. 1 | 455 | q | 0 | 0 | 28.6699 | 1.6682 | 252 | p | 330 | 19.2015 | 0 | 0 | NO
CB1222 | CLANDEBOYE NO. 3 | 33 | 407.1941 | 540 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1222 | SubTransmission | CB1222_Clandeboye No.3 |  | 33.594 | NO | NO |  | CB1222 | CLANDEBOYE NO. 3 | 455 | q | 0 | 0 | 47.8059 | 2.7817 | 660 | q | 0 | 0 | 120 | 6.9824 | NO
CB1262 | TEMUKA NO. 2 | 33 | 426.3301 | 582 | 340 | 19.7834 | 380 | 22.1109 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1262 | SubTransmission | CB1262_Temuka No.2 |  | 33.594 | NO | NO |  | CB1262 | TEMUKA NO. 2 | 455 | q | 0 | 0 | 28.6699 | 1.6682 | 252 | p | 330 | 19.2015 | 0 | 0 | NO
CB1272 | CLANDEBOYE NO. 2 & RANGITATA NO. 1 | 33 | 496.0602 | 510 | 395 | 22.9837 | 445 | 25.893 | OH LINE-WOLF | NO | N/A | TMK-CB1272 | SubTransmission | CB1272_Clandeboye No.2 |  | 33.594 | NO | NO |  | CB1272 | CLANDEBOYE NO. 2 | 455 | p | 41.0602 | 2.3891 | 0 | 0 | 510 | u | 0 | 0 | 0 | 0 | NO
CB1282 | CLANDEBOYE NO. 4 | 33 | 407.1941 | 660 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1282 | SubTransmission | CB1282_Clandeboye No.4 |  | 33.594 | NO | NO |  | CB1282 | CLANDEBOYE NO. 4 | 500 | q | 0 | 0 | 92.8059 | 5.4001 | 540 | p | 120 | 6.9824 | 0 | 0 | NO
CB1292 | GERALDINE | 33 | 256.8585 | 462 | 205 | 11.9282 | 230 | 13.3829 | OH LINE-DOG | YES | NO | TMK-CB1292 | SubTransmission | CB1292_Geraldine |  | 33.594 | NO | NO |  | CB1292 | GERALDINE |  | p | 0 | 0 | 0 | 0 | 462 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
[20 empty] | TMK GXP |  |  |  | 41.0602 | 2.3891 | 290.7575 | 16.9182 |  |  | 780 | 45.3855 | 120 | 6.9824
TEMUKA (D816) | [11 empty] | Supporting info | [7 empty] | TEMUKA (D816)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1 | TEMUKA WEST | 11 | 259.3186 | 402 | 205 | 3.9058 | 230 | 4.3821 | CABLE-1-3C 300 MM² AL XLPE HD | YES | NO | TMK-CB1 | DistributionFeeder | CB1_Temuka West |  | 11 | NO | NO |  | CB1 | TEMUKA WEST | 360 | q | 0 | 0 | 100.6814 | 1.9182 | 400 | p | 2 | 0.038105 | 0 | 0 | YES (DISABLED)
CB2 | MILFORD | 11 | 159.408 | 402 | 125 | 2.3816 | 140 | 2.6674 | CABLE-1-3C 150 MM² AL PILC | YES | YES | TMK-CB2 | DistributionFeeder | CB2_Milford |  | 11 | NO | NO |  | CB2 | MILFORD | 250 | q | 0 | 0 | 90.592 | 1.726 | 400 | p | 2 | 0.038105 | 0 | 0 | YES
CB3 | WINCHESTER | 11 | 300 | 402 | 240 | 4.5726 | 270 | 5.1442 | LINK-T546 | YES | YES | TMK-CB3 | DistributionFeeder | CB3_Winchester |  | 11 | NO | NO |  | CB3 | WINCHESTER | 250 | p | 50 | 0.95263 | 0 | 0 | 400 | p | 2 | 0.038105 | 0 | 0 | YES
CB4 | INCOMER NO. 1 | 11 | 1041.987 | 1080 | 830 | 15.8136 | 935 | 17.8141 | CABLE-6-1C 500 MM² CU XLPE | NO | N/A | TMK-CB4 | ZoneSubstation | TMK |  | 11 | NO | YES |  | CB4 | INCOMER NO. 1 | 680 | p | 361.987 | 6.8968 | 0 | 0 | 800 | p | 280 | 5.3347 | 0 | 0 | NO
CB5 | BUS COUPLER | 11 | 984 | 984 | 785 | 14.9563 | 885 | 16.8615 | CIRCUIT BREAKER-TMK-CB5-PROTECTION | NO | N/A | TMK-CB5 | ZoneSubstation | TMK |  | 11 | YES | NO | Load Capability equal protection OC due to lack of information | CB5 | BUS COUPLER |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
CB6 | INCOMER NO. 2 | 11 | 1041.987 | 1080 | 830 | 15.8136 | 935 | 17.8141 | CABLE-6-1C 500 MM² CU XLPE | NO | N/A | TMK-CB6 | ZoneSubstation | TMK |  | 11 | NO | YES |  | CB6 | INCOMER NO. 2 | 680 | p | 361.987 | 6.8968 | 0 | 0 | 880 | p | 200 | 3.8105 | 0 | 0 | NO
CB7 | RANGITATA | 11 | 300 | 402 | 240 | 4.5726 | 270 | 5.1442 | LINK-T547 | YES | YES | TMK-CB7 | DistributionFeeder | CB7_Rangitata |  | 11 | NO | NO |  | CB7 | RANGITATA | 250 | p | 50 | 0.95263 | 0 | 0 | 400 | p | 2 | 0.038105 | 0 | 0 | YES
CB8 | TEMUKA EAST | 11 | 241 | 402 | 190 | 3.62 | 215 | 4.0963 | OH LINE-7/0.136 CU | YES | NO | TMK-CB8 | DistributionFeeder | CB8_Temuka East |  | 11 | NO | NO |  | CB8 | TEMUKA EAST | 360 | q | 0 | 0 | 119 | 2.2673 | 400 | p | 2 | 0.038105 | 0 | 0 | YES (DISABLED)
CB9 | WAITOHI | 11 | 176 | 402 | 140 | 2.6674 | 155 | 2.9531 | OH LINE-19/16 CU | YES | YES | TMK-CB9 | DistributionFeeder | CB9_Waitohi |  | 11 | NO | NO |  | CB9 | WAITOHI | 360 | q | 0 | 0 | 184 | 3.5057 | 400 | p | 2 | 0.038105 | 0 | 0 | YES
[20 empty] | TMK |  |  |  | 823.9741 | 15.6988 | 494.2734 | 9.4172 |  |  | 492 | 9.3739 | 0 | 0
GERALDINE (D823) | [11 empty] | Supporting info | [7 empty] | GERALDINE (D823)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
G259 | 33 KV INCOMER | 33 | 256.8585 | 350 | 205 | 11.9282 | 230 | 13.3829 | OH LINE-DOG | NO | N/A | GLD-G259 | SubTransmission | GLD |  | 33.594 | NO | YES |  | G259 | T2 HV INCOMER | 210 | p | 46.8585 | 2.7265 | 0 | 0 | 350 | u | 0 | 0 | 0 | 0 | NO
G260 | 11 KV INCOMER | 11 | 783.3789 | 948 | 625 | 11.9674 | 705 | 13.4992 | POWER TRANSFORMER RATING AT 15 MVA | YES | NO | GLD-G260 | ZoneSubstation | GLD |  | 11.055 | NO | YES |  | G260 | T2 LV INCOMER | 460 | p | 323.3789 | 6.192 | 0 | 0 | 950 | q | 0 | 0 | 2 | 0.038296 | YES (DISABLED)
G156 | WOODBURY | 11 | 241 | 350 | 190 | 3.6381 | 215 | 4.1168 | OH LINE-7/0.136 CU | YES | YES | GLD-G156 | DistributionFeeder | G156_Woodbury |  | 11.055 | NO | NO |  | G156 | WOODBURY | 290 | q | 0 | 0 | 49 | 0.93824 | 350 | u | 0 | 0 | 0 | 0 | YES
G191 | GERALDINE TOWNSHIP | 11 | 241 | 350 | 190 | 3.6381 | 215 | 4.1168 | OH LINE-7/0.136 CU | YES | NO | GLD-G191 | DistributionFeeder | G191_Geraldine Township |  | 11.055 | NO | NO |  | G191 | GERALDINE TOWNSHIP | 310 | q | 0 | 0 | 69 | 1.3212 | 350 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
G194 | SPEECHLEY | 11 | 188.6266 | 350 | 150 | 2.8722 | 165 | 3.1594 | OH LINE-MINK | YES | YES | GLD-G194 | DistributionFeeder | G194_Speechly |  | 11.055 | NO | NO |  | G194 | SPEECHLEY | 190 | q | 0 | 0 | 1.3734 | 0.026297 | 350 | u | 0 | 0 | 0 | 0 | YES
[20 empty] | GLD |  |  |  | 370.2375 | 8.9185 | 119.3734 | 2.2857 |  |  | 0 | 0 | 2 | 0.038296
RANGITATA (D1479) | [11 empty] | Supporting info | [7 empty] | RANGITATA (D1479)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1522 | 33 KV INCOMER NO. 1 | 33 | 171.8611 | 402 | 135 | 7.8552 | 150 | 8.728 | AEL-FONTERRA CONTRACTUAL-10 MW LIMIT | NO | N/A | RGA_T1-CB1522 | SubTransmission | RGA_T1 |  | 33.594 | YES | YES |  | CB1522 | 33 KV T1 INCOMER | 262 | q | 0 | 0 | 90.1389 | 5.2449 | 402 | u | 0 | 0 | 0 | 0 | NO
CB1562 | 33 KV INCOMER NO. 2 | 33 | 207.2308 | 402 | 165 | 9.6008 | 185 | 10.7645 | CABLE-1-3C 95 MM² AL XLPE | NO | N/A | RGA_T2-CB1562 | SubTransmission | RGA_T2 |  | 33.594 | NO | YES |  | CB1562 | 33 KV T2 INCOMER | 262 | q | 0 | 0 | 54.7692 | 3.1868 | 402 | u | 0 | 0 | 0 | 0 | NO
CB35 | 11 KV INCOMER NO. 1 | 11 | 771.8586 | 1048 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | RGA_T1-CB35 | ZoneSubstation | RGA_T1 |  | 11.22 | NO | YES |  | CB35 | 11 KV T1 INCOMER | 810 | q | 0 | 0 | 38.1414 | 0.74122 | 1048 | u | 0 | 0 | 0 | 0 | NO
CB36 | 11 KV INCOMER NO. 2 | 11 | 771.8586 | 1048 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | RGA_T2-CB36 | ZoneSubstation | RGA_T2 |  | 11.22 | NO | YES |  | CB36 | 11 KV T2 INCOMER | 928 | q | 0 | 0 | 156.1414 | 3.0344 | 1048 | u | 0 | 0 | 0 | 0 | NO
CB31 | BUS COUPLER NO. 1 (N/O) | 11 | 800 | 600 | 480 | 9.3281 | 540 | 10.4941 | CABLE-3-1C 630MM2 AL XLPE HDPE | NO | N/A | RGA_T2-CB31 | ZoneSubstation | RGA_T2 |  | 11.22 | NO | NO | Manual entry based on tie cable rating | CB31 | BUS COUPLER (N/O) | 810 | q | 0 | 0 | 10 | 0.19434 | 600 | u | 0 | 0 | 0 | 0 | NO
CB32 | BUS COUPLER NO. 2 | 11 | 800 | 600 | 480 | 9.3281 | 540 | 10.4941 | CABLE-3-1C 630MM2 AL XLPE HDPE | NO | N/A | RGA_T2-CB32 | ZoneSubstation | RGA_T2 |  | 11.22 | NO | NO | Manual entry based on tie cable rating | CB32 | BUS COUPLER | 810 | q | 0 | 0 | 10 | 0.19434 | 600 | u | 0 | 0 | 0 | 0 | NO
CB2 | ARUNDEL | 11 | 256.8585 | 300 | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | YES | YES | RGA_T1-CB2 | DistributionFeeder | CB2_Arundel |  | 11.22 | NO | NO |  | CB2 | ARUNDEL | 220 | p | 36.8585 | 0.71629 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES
CB3 | MAHAN ROAD | 11 | 208.1814 | 300 | 165 | 3.2065 | 185 | 3.5952 | CABLE-1-3C 95 MM² XLPE | YES | YES | RGA_T1-CB3 | DistributionFeeder | CB3_Mahan Road |  | 11.22 | NO | NO |  | CB3 | MAHAN ROAD | 220 | q | 0 | 0 | 11.8186 | 0.22968 | 300 | u | 0 | 0 | 0 | 0 | YES
CB4 | OLD MAIN SOUTH ROAD | 11 | 256.8585 | 300 | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | YES | YES | RGA_T2-CB4 | DistributionFeeder | CB4_Main South Road |  | 11.22 | NO | NO |  | CB4 | OLD MAIN SOUTH ROAD | 220 | p | 36.8585 | 0.71629 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES
CB11 | BELFIELD | 11 | 275.3865 | 300 | 220 | 4.2754 | 245 | 4.7612 | OH LINE-IODINE | YES | YES | RGA_T2-CB11 | DistributionFeeder | CB11_Belfield |  | 11.22 | NO | NO |  | CB11 | BELFIELD | 537 | q | 0 | 0 | 261.6135 | 5.0841 | 300 | u | 0 | 0 | 0 | 0 | YES
CB12 | ORTON | 11 | 275.3865 | 300 | 220 | 4.2754 | 245 | 4.7612 | OH LINE-IODINE | YES | YES | RGA_T2-CB12 | DistributionFeeder | CB12_Orton |  | 11.22 | NO | NO |  | CB12 | ORTON | 295 | q | 0 | 0 | 19.6135 | 0.38116 | 300 | u | 0 | 0 | 0 | 0 | YES
CB13 | RANGITATA ISLAND | 11 | 256.8585 | 300 | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | YES | YES | RGA_T2-CB13 | DistributionFeeder | CB13_Rangitata Island |  | 11.22 | NO | NO |  | CB13 | RANGITATA ISLAND | 220 | p | 36.8585 | 0.71629 | 0 | 0 | 300 | u | 0 | 0 | 0 | 0 | YES
[20 empty] | RGA |  |  |  | 110.5756 | 2.1489 | 652.2364 | 18.2909 |  |  | 0 | 0 | 0 | 0
CANAL ROAD (CB1412) | [11 empty] | Supporting info | [7 empty] | CANAL ROAD (CB1412)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB1412 | 33 KV CIRCUIT BREAKER | 33 | 171.8611 | 423 | 135 | 7.8552 | 150 | 8.728 | AEL-FONTERRA CONTRACTUAL-10 MW LIMIT | YES | NO | CNL-RGA-CB1412 | SwitchingStation | CNL-RGA |  | 33.594 | YES | NO |  | CB1412 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0
[20 empty] | CNL |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
CLANDEBOYE NO. 1 (D1246) | [11 empty] | Supporting info | [7 empty] | CLANDEBOYE NO. 1 (D1246)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
T615 | 33 KV INCOMER NO. 1 | 33 | 407.1941 | 512 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD1-T615 | SubTransmission | CD_1 | T1 | 33.594 | NO | NO |  | T615 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
T616 | 33 KV INCOMER NO. 2 | 33 | 347.7083 | 512 | 275 | 16.0013 | 310 | 18.0378 | CABLE-3-1C 300 MM² AL XLPE | NO | N/A | CD1-T616 | SubTransmission | CD_1 | T2 | 33.594 | NO | NO |  | T616 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
T600 | MILK POWDER NO. 2 | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T600 | DistributionFeeder | T600_Tie to Milk Powder 2 |  | 11 | NO | NO |  | T600 | MILK POWDER 2 | 420 | q | 0 | 0 | 116.8346 | 2.226 | 480 | u | 0 | 0 | 0 | 0 | NO
T601 | FIRE SERVICES | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T601 | DistributionFeeder | T601_Fire Services |  | 11 | NO | NO |  | T601 | FIRE SERVICES | 420 | q | 0 | 0 | 116.8346 | 2.226 | 480 | u | 0 | 0 | 0 | 0 | NO
T602 | WHEY PROCESSING | 11 | 239.5512 | 480 | 190 | 3.62 | 215 | 4.0963 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T602 | DistributionFeeder | T602_Whey Processing |  | 11 | NO | NO |  | T602 | WHEY PROCESSING | 367 | q | 0 | 0 | 127.4488 | 2.4282 | 480 | u | 0 | 0 | 0 | 0 | NO
T603 | LACTOSE PLANT | 11 | 342.0164 | 480 | 270 | 5.1442 | 305 | 5.811 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD1-T603 | DistributionFeeder | T603_Lactose Plant |  | 11 | NO | NO |  | T603 | LACTOSE PLANT | 367 | q | 0 | 0 | 24.9836 | 0.476 | 480 | u | 0 | 0 | 0 | 0 | NO
T604 | SPARE | 11 | 239.5512 | 480 | 190 | 3.62 | 215 | 4.0963 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T604 | DistributionFeeder | T603_Lactose Plant |  | 11 | NO | NO | Manual entry from previous Switching Digrams | T604 | SPARE | 367 | q | 0 | 0 | 127.4488 | 2.4282 | 480 | u | 0 | 0 | 0 | 0 | NO
T605 | TIE TO MILFORD CLANDEBOYE ROAD | 11 | 122.77 | 252 | 95 | 1.81 | 110 | 2.0958 | CABLE-1-3C 95 MM² AL PILC | YES | NO | CD1-T605 | DistributionFeeder | T605_Tie to Milford |  | 11 | NO | NO |  | T605 | TIE TO MILFORD CLANDEBOYE ROAD | 253 | q | 0 | 0 | 130.23 | 2.4812 | 252 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
T606 | 11 KV INCOMER NO. 1 | 11 | 1049.7278 | 1440 | 835 | 15.9089 | 940 | 17.9094 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | CD1-T606 | ZoneSubstation | CD_1 | T1 | 11 | NO | YES |  | T606 | MAIN INCOMING - T1 |  | p | 0 | 0 | 0 | 0 | 1440 | u | 0 | 0 | 0 | 0 | NO
T607 | BUS COUPLER | 11 | 1250 | 1440 | 1000 | 19.0526 | 1125 | 21.4341 | CIRCUIT BREAKER-CD1-T607-RATING | NO | N/A | CD1-T607 | ZoneSubstation | CD_1 |  | 11 | NO | NO | Manual entry from previous Switching Digrams | T607 | BUS COUPLER | 1250 | u | 0 | 0 | 0 | 0 | 1440 | u | 0 | 0 | 0 | 0 | NO
T608 | 11 KV INCOMER NO. 2 | 11 | 1049.7278 | 1440 | 835 | 15.9089 | 940 | 17.9094 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | CD1-T608 | ZoneSubstation | CD_1 | T2 | 11 | NO | YES |  | T608 | MAIN INCOMING - T2 |  | p | 0 | 0 | 0 | 0 | 1440 | u | 0 | 0 | 0 | 0 | NO
T609 | MILK RECEPTION | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T609 | DistributionFeeder | T609_Milk Reception |  | 11 | NO | NO |  | T609 | MILK RECEPTION | 476 | q | 0 | 0 | 172.8346 | 3.2929 | 480 | u | 0 | 0 | 0 | 0 | NO
T610 | CHILLED WATER NO. 1 | 11 | 179.6634 | 480 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T610 | DistributionFeeder | T610_Chilled Water 1 |  | 11 | NO | NO |  | T610 | CHILLED WATER NO. 1 | 367 | q | 0 | 0 | 187.3366 | 3.5692 | 480 | u | 0 | 0 | 0 | 0 | NO
T611 | EFFLUENT PLANT | 11 | 179.6634 | 480 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T611 | DistributionFeeder | T611_Effluent Plant |  | 11 | NO | NO |  | T611 | EFFLUENT PLANT | 367 | q | 0 | 0 | 187.3366 | 3.5692 | 480 | u | 0 | 0 | 0 | 0 | NO
T612 | MILK TREATMENT | 11 | 122.77 | 480 | 95 | 1.81 | 110 | 2.0958 | CABLE-1-3C 95 MM² AL PILC | NO | N/A | CD1-T612 | DistributionFeeder | T612_Milk Treatment |  | 11 | NO | NO |  | T612 | MILK TREATMENT | 253 | q | 0 | 0 | 130.23 | 2.4812 | 480 | u | 0 | 0 | 0 | 0 | NO
T613 | ROLLESTON ROAD | 11 | 179.6634 | 360 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | YES | NO | CD1-T613 | DistributionFeeder | T613_Rolleston Rd |  | 11 | NO | NO |  | T613 | ROLLESTON ROAD | 367 | q | 0 | 0 | 187.3366 | 3.5692 | 360 | u | 0 | 0 | 0 | 0 | YES (DISABLED)
T614 | POWDER HANDELING | 11 | 321.2648 | 480 | 255 | 4.8584 | 285 | 5.43 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T614 | DistributionFeeder | T614_Tie to Powder Handling |  | 11 | NO | NO |  | T614 | POWDER HANDELING | 476 | q | 0 | 0 | 154.7352 | 2.9481 | 480 | u | 0 | 0 | 0 | 0 | NO
[20 empty] | CD1 |  |  |  | 0 | 0 | 1663.5902 | 31.6957 |  |  | 0 | 0 | 0 | 0
CLANDEBOYE NO. 2 (D1462) | [11 empty] | Supporting info | [7 empty] | CLANDEBOYE NO. 2 (D1462)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
T662 | 33 KV INCOMER NO. 3 | 33 | 407.1941 | 540 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD2-T662 | SubTransmission | CD_2 | T3 | 33.594 | NO | NO |  | T662 | 33 KV INC TO T3 OFF CABLE | 420 | q | 0 | 0 | 12.8059 | 0.74513 |  | p | 0 | 0 | 0 | 0 | NO
T663 | 33 KV INCOMER NO. 4 | 33 | 407.1941 | 660 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD2-T663 | SubTransmission | CD_2 | T4 | 33.594 | NO | NO |  | T663 | 33 KV INC TO T4 OFF CABLE | 420 | q | 0 | 0 | 12.8059 | 0.74513 |  | p | 0 | 0 | 0 | 0 | NO
T650 | MILK POWDER NO. 1 | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T650 | DistributionFeeder | T650_Tie to Milk Powder 1 |  | 11 | NO | NO |  | T650 | MILK POWDER 1 | 310 | q | 0 | 0 | 24.9341 | 0.47506 | 420 | p | 60 | 1.1432 | 0 | 0 | NO
T651 | MILK POWDER NO. 3 | 11 | 330.3145 | 480 | 260 | 4.9537 | 295 | 5.6205 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T651 | DistributionFeeder | T651_Milk Powder 3 |  | 11 | NO | NO |  | T651 | MILK POWDER 3 | 310 | p | 20.3145 | 0.38704 | 0 | 0 | 420 | p | 60 | 1.1432 | 0 | 0 | NO
T652 | WPC | 11 | 219.7882 | 1200 | 175 | 3.3342 | 195 | 3.7152 | CABLE-1-3C 185 MM² XLPE | NO | N/A | CD2-T652 | DistributionFeeder | T652_Tie to WPC |  | 11 | NO | NO |  | T652 | WPC | 240 | q | 0 | 0 | 20.2118 | 0.38509 | 320 | p | 880 | 16.7663 | 0 | 0 | NO
T653 | CHILLED WATER NO. 3 | 11 | 316.7399 | 480 | 250 | 4.7631 | 285 | 5.43 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T653 | DistributionFeeder | T653_Chilled Water 3 |  | 11 | NO | NO |  | T653 | CHILLED WATER 3 | 330 | q | 0 | 0 | 13.2601 | 0.25264 | 320 | p | 160 | 3.0484 | 0 | 0 | NO
T654 | R22 REPLACEMENT | 11 | 309.1922 | 480 | 245 | 4.6679 | 275 | 5.2395 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T654 | DistributionFeeder | T654_Tie to Boiler House |  | 11 | NO | NO |  | T654 | R22 REPLACEMENT | 260 | p | 49.1922 | 0.93724 | 0 | 0 | 320 | p | 160 | 3.0484 | 0 | 0 | NO
T655 | 11 KV INCOMER NO. 4 | 11 | 1312.1597 | 1600 | 1045 | 19.9099 | 1180 | 22.482 | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | CD2-T655 | ZoneSubstation | CD_2 | T4 | 11 | NO | YES |  | T655 | MAIN INCOMER - T4 | 1500 | q | 0 | 0 | 187.8403 | 3.5788 | 1440 | p | 160 | 3.0484 | 0 | 0 | NO
T656 | BUS COUPLER | 11 | 1250 | 1400 | 1000 | 19.0526 | 1125 | 21.4341 | CIRCUIT BREAKER-CD2-T656-RATING | NO | N/A | CD2-T656 | ZoneSubstation | CD_2 |  | 11 | NO | NO | Manual entry from previous Switching Digrams | T656 | BUS COUPLER | 1250 | u | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
T657 | 11 KV INCOMER NO. 3 | 11 | 1312.1597 | 1400 | 1045 | 19.9099 | 1180 | 22.482 | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | CD2-T657 | ZoneSubstation | CD_2 | T3 | 11 | NO | YES |  | T657 | MAIN INCOMER - T3 | 1500 | q | 0 | 0 | 187.8403 | 3.5788 | 1440 | q | 0 | 0 | 40 | 0.7621 | NO
T658 | MILK POWDER NO. 2 | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T658 | DistributionFeeder | T658_Milk Powder 2 |  | 11 | NO | YES |  | T658 | MILK POWDER 2 | 310 | q | 0 | 0 | 24.9341 | 0.47506 | 420 | p | 60 | 1.1432 | 0 | 0 | NO
T659 | MOZZ REFRIG/MOZZ NO. 1 | 11 | 306.0371 | 480 | 240 | 4.5726 | 275 | 5.2395 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T659 | DistributionFeeder | T659_Tie to Energy Centre 1 |  | 11 | NO | NO |  | T659 | MOZZ REFRIG/MOZZ 1 | 270 | p | 36.0371 | 0.6866 | 0 | 0 | 320 | p | 160 | 3.0484 | 0 | 0 | NO
T660 | REFIGERATION | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T660 | DistributionFeeder | T660_Refrigeration |  | 11 | NO | NO |  | T660 | REFIGERATION | 310 | q | 0 | 0 | 24.9341 | 0.47506 | 320 | p | 160 | 3.0484 | 0 | 0 | NO
T661 | LABORATORY | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T661 | DistributionFeeder | T661_Laboratory |  | 11 | NO | NO |  | T661 | LABORATORY | 310 | q | 0 | 0 | 24.9341 | 0.47506 | 420 | p | 60 | 1.1432 | 0 | 0 | NO
CB2 | MOZZ NO. 3 PACKING | 11 | 630 | 600 | 480 | 9.1452 | 540 | 10.2884 | RMU SWITCH-T708 | NO | N/A | CD2-CB2 | DistributionFeeder | CB2_Mozz3_1 |  | 11 | NO | NO |  | CB2 | MOZZ 3 PACKING | 617 | p | 13 | 0.24768 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | NO
CB15 | MOZZ NO. 3 MAIN PROCESS | 11 | 630 | 600 | 480 | 9.1452 | 540 | 10.2884 | RMU SWITCH-T737 | NO | N/A | CD2-CB15 | DistributionFeeder | CB15_Mozz3_2 |  | 11 | NO | NO |  | CB15 | MOZZ 3 MAIN PROCESS | 617 | p | 13 | 0.24768 | 0 | 0 | 600 | u | 0 | 0 | 0 | 0 | NO
[20 empty] | CD2 |  |  |  | 131.5438 | 2.5062 | 534.5006 | 11.1859 |  |  | 1920 | 36.5809 | 40 | 0.7621
TWIZEL (E120) | [11 empty] | Supporting info | [7 empty] | TWIZEL (E120)-OLD
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes | CB ID | DESIGNATION | LOAD CAPABILITY | [5 empty] | OC PICKUP | [5 empty] | RECLOSER
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA) | [13 empty] | (A) | Moved | A Up | MVA Up | A Down | MVA Down | (A) | Moved | A Up | MVA Up | A Down | MVA Down
CB6312 | 33 KV TP INCOMER | 33 | 120 | 252 | 95 | 5.43 | 105 | 6.0016 | CIRCUIT BREAKER-TWZ-CB6312-OTHER EQUIPMENT | NO | N/A | TWZ-CB6312 | GXP | TWZ_GXP |  | 33 | YES | NO |  | CB6312 | NEW |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
Z68 | 33 KV AEL INCOMER | 33 | 296 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-WAXWING | NO | N/A | TVS-Z68 | SubTransmission | TWZ_GXP |  | 33 | YES | NO |  | Z68 | HV CB AT 33 KV | 109 | p | 187 | 10.6885 | 0 | 0 | 250 | q | 0 | 0 | 100 | 5.7158 | NO
Z1 | URBAN NO. 1 | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE - MINK | NO | N/A | TVS-Z1 | DistributionFeeder | Z1_Urban No. 1 |  | 11 | NO | NO |  | Z1 | URBAN NO. 1 | 300 | q | 0 | 0 | 111 | 2.1148 | 150 | p | 2 | 0.038105 | 0 | 0 | NO
Z2 | URBAN NO. 2 | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE-MINK | NO | N/A | TVS-Z2 | DistributionFeeder | Z2_Urban No. 2 |  | 11 | NO | NO |  | Z2 | URBAN NO. 2 | 160 | p | 29 | 0.55252 | 0 | 0 | 150 | p | 2 | 0.038105 | 0 | 0 | NO
Z3 | INDUSTRIAL | 11 | 85.3875 | 150 | 65 | 1.2384 | 75 | 1.4289 | CABLE-1-3C 35 MM² AL PILC | NO | N/A | TVS-Z3 | DistributionFeeder | Z3_Industrial |  | 11 | NO | NO |  | Z3 | INDUSTRIAL | 295 | q | 0 | 0 | 209.6125 | 3.9937 | 150 | u | 0 | 0 | 0 | 0 | NO
Z4 | TWIZEL RURAL | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE - MINK | YES | YES | TVS-Z4 | DistributionFeeder | Z4_Twizel Rural |  | 11 | NO | NO |  | Z4 | TWIZEL RURAL | 295 | q | 0 | 0 | 106 | 2.0196 | 150 | p | 2 | 0.038105 | 0 | 0 | YES
Z5 | SPARE | 11 | N/A | N/A | 0 | 0 | N/A | N/A | N/A | NO | N/A | TVS-Z5 | DistributionFeeder | Z5_Spare |  | 11 | NO | NO | Spare i.e. not utilised | Z5 | SPARE |  | p | 0 | 0 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
Z6 | 11 KV INCOMER NO. 1 | 11 | 328.0399 | N/A | 260 | 4.9537 | 295 | 5.6205 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | TVS-Z6 | ZoneSubstation | TVS |  | 11 | NO | YES |  | Z6 | NO. 1 INCOMER | 327 | p | 1.0399 | 0.019813 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
Z7 | 11 KV INCOMER NO. 2 | 11 | N/A | N/A | 0 | 0 | N/A | N/A | N/A | NO | N/A | TVS-Z7 | ZoneSubstation | TVS |  | 11 | NO | NO | Spare i.e. not utilised | Z7 | NO. 2 INCOMER | 327 | p |  | 0 |  | 0 |  | p | 0 | 0 | 0 | 0 | NO
Z9 | LOCAL SERVICE | 11 | 251.6 | 30 | 20 | 0.38105 | 25 | 0.47631 | CABLE - 1-3C 95 MM² CU XLPE | NO | N/A | TVS-Z9 | DistributionFeeder | Z9_Local Supply |  | 11 | NO | NO |  | Z9 | LOCAL SERVICE | 30 | p | 221.6 | 4.222 | 0 | 0 |  | p | 0 | 0 | 0 | 0 | NO
[20 empty] | TWZ |  |  |  | 438.6399 | 15.4829 | 426.6125 | 8.1281 |  |  | 6 | 0.11432 | 100 | 5.7158
Note on D2: Author: As agreed upon by Network Departments on the 01/03/2021 During SCADA Alarams proposal session
Note on D3: Author: As agreed upon by Network Departments on the 01/03/2021 During SCADA Alarams proposal session
Note on R6: Author: Leave blank if not used
Note on E34: Author: Manual entry from previous Switching Digrams
Note on F34: Author: Manual entry from previous Switching Digrams
Note on K34: Author: Manual entry
Note on E44: Author: Manual entry from previous Switching Diagrams
Note on K44: Author: Manual entry
Note on E45: Author: Manual entry from previous Switching Diagrams
Note on K45: Author: Manual entry
Note on M46: Author: Based on Survalent comment "Normally Disabled"
Note on E56: Author: Manual entry from previous Switching Diagrams
Note on I56: Author: Manual entry from previous Switching Diagrams
Note on K56: Author: Manual entry from previous Switching Diagrams
Note on E57: Author: Manual entry from previous Switching Diagrams
Note on F57: Author: Equal value above
Note on I57: Author: Manual entry from previous Switching Diagrams
Note on K57: Author: Manual entry from previous Switching Diagrams
Note on E58: Author: Manual entry from previous Switching Diagrams
Note on F58: Author: Equal value above
Note on I58: Author: Manual entry from previous Switching Diagrams
Note on K58: Author: Manual entry from previous Switching Diagrams
Note on E90: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K90: Author: Manual entry
Note on E96: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K96: Author: Manual entry
Note on E103: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K103: Author: Manual entry
Note on E109: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K109: Author: Manual entry
Note on E138: Author: Manual entry based on substation drawing T269-01 rating of the CB
Note on F138: Author: No OC protection, only EF
Note on K138: Author: Manual entry
Note on E139: Author: Manual entry based on substation drawing T269-01 rating of the CB
Note on F139: Author: No OC protection, only EF
Note on K139: Author: Manual entry
Note on E152: Author: NA as it does not have any backbone assets asscoiated with it
Note on K152: Author: NA as it does not have any backbone assets asscoiated with it
Note on E153: Author: Manual entry based on substation drawing T269-02 rating of the CB
Note on F153: Author: No protection seetings set
Note on K153: Author: Manual entry
Note on E161: Author: NA as it does not have any backbone assets asscoiated with it
Note on K161: Author: NA as it does not have any backbone assets asscoiated with it
Note on E183: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on F183: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on K183: Author: Manual entry
Note on E184: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on F184: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on K184: Author: Manual entry
Note on F194: Author: Not a CB so no protection or SCADA alarms
Note on G194: Author: Not a CB so no protection or SCADA alarms
Note on H194: Author: Not a CB so no protection or SCADA alarms
Note on I194: Author: Not a CB so no protection or SCADA alarms
Note on J194: Author: Not a CB so no protection or SCADA alarms
Note on F195: Author: Not a CB so no protection or SCADA alarms
Note on G195: Author: Not a CB so no protection or SCADA alarms
Note on H195: Author: Not a CB so no protection or SCADA alarms
Note on I195: Author: Not a CB so no protection or SCADA alarms
Note on J195: Author: Not a CB so no protection or SCADA alarms
Note on F196: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on F197: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on F198: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on E206: Author: Manual entry from previous switching digram
Note on K206: Author: Manual entry
Note on E207: Author: Manual entry from previous switching digram
Note on K207: Author: Manual entry
Note on E210: Author: Manual entry from previous switching digram
Note on K210: Author: Manual entry
Note on M239: Author: Disabled due to fire risk as of 01/04/21
Note on M240: Author: Disabled due to fire risk as of 01/04/21
Note on M256: Author: Diabled due to fire risk as of 01/04/21
Note on M263: Author: Diabled due to fire risk as of 01/04/21
Note on F264: Author: Not a CB so no protection or SCADA alarms
Note on G264: Author: Not a CB so no protection or SCADA alarms
Note on H264: Author: Not a CB so no protection or SCADA alarms
Note on I264: Author: Not a CB so no protection or SCADA alarms
Note on J264: Author: Not a CB so no protection or SCADA alarms
Note on F265: Author: Not a CB so no protection or SCADA alarms
Note on G265: Author: Not a CB so no protection or SCADA alarms
Note on H265: Author: Not a CB so no protection or SCADA alarms
Note on I265: Author: Not a CB so no protection or SCADA alarms
Note on J265: Author: Not a CB so no protection or SCADA alarms
Note on E292: Author: Manual entry. =OC limit
Note on K292: Author: Manual entry
Note on E316: Author: Manual entry
Note on K316: Author: Manual entry
Note on E317: Author: Manual entry
Note on K317: Author: Manual entry
Note on E341: Author: Set to equal T602 for now
Note on K341: Author: Set to equal T602 for now
Note on E344: Author: Manual entry based on previous switching diagram
Note on K344: Author: Manual entry
Note on E365: Author: Manual entry based on previous switching diagram
Note on K365: Author: Manual entry
Note on E384: Author: Not Utilised at the moment
Note on F384: Author: Not Utilised at the moment
Note on I384: Author: Not Utilised at the moment
Note on J384: Author: Not Utilised at the moment
Note on K384: Author: Not Utilised at the moment
Note on F385: Author: No protection information in AEL protection database
Note on E386: Author: Not Utilised at the moment
Note on F386: Author: Not Utilised at the moment
Note on I386: Author: Not Utilised at the moment
Note on J386: Author: Not Utilised at the moment
Note on K386: Author: Not Utilised at the moment

## Switching Diagram Tables-Field (hidden)
SCADA Factor Levels Percentages
| Emergency | 90% | Meeting minutes of values agreed upon
| Pre-Emergency | 80%
ALBURY SUBSTATION (C251) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB62 | TRANSPOWER INCOMER | 110 | 105 | 199 | 80 | 15.242 | 90 | 17.1473 | POWER TRANSFORMER RATING AT 20.01 MVA | NO | N/A | ABY-CB62 | GXP | ABY_GXP |  | 110 | YES | YES
CB2712 | TRANSPOWER INCOMER | 11 | 600 | 1635 | 480 | 9.1452 | 540 | 10.2884 | CIRCUIT BREAKER-ABY-CB2712-OTHER EQUIPMENT | NO | N/A | ABY-CB2712 | GXP | ABY_GXP |  | 11 | YES | YES
CB4242 | FAIRLIE | 33 | 172.8371 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-PETREL | NO | N/A | ABY-CB4242 | SubTransmission | CB2722_Fairlie |  | 33 | NO | NO
CB2722 | FAIRLIE | 11 | 450 | 450 | 360 | 6.8589 | 405 | 7.7163 | CIRCUIT BREAKER-ABY-CB2722-PROTECTION | NO | N/A | ABY-CB2722 | SubTransmission | CB2722_Fairlie |  | 11 | YES | NO
CB2732 | RAINCLIFF | 11 | 241.6125 | 225 | 180 | 3.4295 | 200 | 3.8105 | OH LINE-19/14 CU | YES | YES | ABY-CB2732 | DistributionFeeder | CB2732_Raincliff |  | 11 | NO | NO
CB2742 | CAVE | 11 | 256.8585 | 225 | 180 | 3.4295 | 200 | 3.8105 | OH LINE-DOG | YES | YES | ABY-CB2742 | DistributionFeeder | CB2742_Cave |  | 11 | NO | NO
FAIRLIE SUBSTATION (C1) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
F400 | OPU 33 kV RECLOSER | 33 | 247 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-70 MM² CU | NO | N/A | OPU-F400 | SubTransmission | OPU |  | 33 | NO | NO
F323 | T1 HV CB | 33 | 150 | 100 | 80 | 4.5726 | 90 | 5.1442 | CIRCUIT BREAKER-ABY-CB4242-PROTECTION | NO | N/A | FLE-F323 | SubTransmission | CB2722_Fairlie |  | 33 | NO | YES
F377 | T1 LV INCOMER | 11 | 325.0817 | 280 | 220 | 4.2297 | 250 | 4.8065 | POWER TRANSFORMER RATING AT 6.25 MVA | YES | NO | FLE-F377 | ZoneSubstation | FLE |  | 11.1001 | NO | YES
F374 | CRICKLEWOOD | 11 | 188.6266 | 192 | 150 | 2.8839 | 165 | 3.1723 | OH LINE-MINK | YES | YES | FLE-F374 | DistributionFeeder | F374_Cricklewood |  | 11.1001 | NO | NO
F380 | FAIRLIE RURAL | 11 | 247 | 192 | 150 | 2.8839 | 170 | 3.2684 | OH LINE-70 MM² CU | YES | NO | FLE-F380 | DistributionFeeder | F380_Fairlie Rural |  | 11.1001 | NO | NO
F383 | FAIRLIE TOWNSHIP | 11 | 170.765 | 192 | 135 | 2.5955 | 150 | 2.8839 | CABLE-1-3C 95 MM² AL PILC | YES | NO | FLE-F383 | DistributionFeeder | F383_Fairlie Township |  | 11.1001 | NO | NO
BELLS POND SUBSTATION (A1067-T1) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB442 | T1 110 KV INCOMER | 110 | 209.9456 | 292 | 165 | 31.4367 | 185 | 35.2472 | POWER TRANSFORMER RATING AT 40 MVA | NO | N/A | BPD-T1-CB442 | ZoneSubstation | BPD | T1 | 110 | YES | YES
CB3602 | 33 KV TO CNR FROM T1 | 33 | 800 | 492 | 390 | 22.2915 | 440 | 25.1494 | AIR BREAK SWITCH-3604 ABS | NO | N/A | BPD-T1-CB3602 | SubTransmission | CB3602_CNR | T1 | 33 | NO | YES
CB35 | T1 BUS 11 KV INCOMER | 11 | 1543.7173 | 2208 | 1230 | 23.9033 | 1385 | 26.9155 | POWER TRANSFORMER RATING AT 30 MVA | NO | N/A | BPD-T1-CB35 | ZoneSubstation | BPD | T1 | 11.22 | YES | YES
CB31 | T1 BUS 11 KV BUS COUPLER | 11 | 1250 | 1000 | 800 | 15.5469 | 900 | 17.4902 | CABLE-6-1C 1000MM2 AL XLPE MDPE | NO | N/A | BPD-T1-CB31 | ZoneSubstation | BPD |  | 11.22 | NO | YES | Manual entry from previous Switching Digrams
CB1 | WAIHUNA | 11 | 386.9283 | 400 | 305 | 5.9273 | 345 | 6.7046 | OH LINE-JAGUAR | YES | YES | BPD-T1-CB1 | DistributionFeeder | CB1_Waihuna | T1 | 11.22 | NO | NO
CB2 | TAWAI | 11 | 386.9283 | 400 | 305 | 5.9273 | 345 | 6.7046 | OH LINE-JAGUAR | YES | YES | BPD-T1-CB2 | DistributionFeeder | CB2_Tawai | T1 | 11.22 | NO | NO
BELLS POND SUBSTATION (A1067-T2) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB482 | T2 110 KV INCOMER | 110 | 104.9728 | 146 | 80 | 15.242 | 90 | 17.1473 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | BPD-T2-CB482 | ZoneSubstation | BPD | T2 | 110 | NO | YES
CB522 | 33 KV TO CNR FROM T2 | 33 | #N/A | 370 |  | #VALUE! |  | #VALUE! | #N/A | NO | N/A | BPD-T2-CB522 | SubTransmission | CB522_CNR |  | 33 | NO | YES
CB36 | T2 BUS 11 KV INCOMER | 11 | 771.8586 | 1100 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | BPD-T2-CB36 | ZoneSubstation | BPD | T2 | 11.22 | NO | YES
CB32 | T2 BUS 11 KV BUS COUPLER | 11 | 1250 | 1000 | 800 | 15.5469 | 900 | 17.4902 | CABLE-6-1C 1000MM2 AL XLPE MDPE | NO | N/A | BPD-T2-CB32 | ZoneSubstation | BPD |  | 11.22 | NO | YES | Manual entry from previous Switching Digrams
CB15 | T2 BUS INJECTION PLANT | 11 | 200 | 60 | 45 | 0.87451 | 50 | 0.97168 | CABLE-3C 185MM2 AL XLPE | NO | N/A | BPD-T2-CB15 | DistributionFeeder | Manual entry |  | 11.22 | NO | NO | Manual entry from previous Switching Digrams
CB11 | WAIHAO DOWNS IRR. | 11 | 239.7 | 400 | 190 | 3.6924 | 215 | 4.1782 | CABLE - 3C 95MM2 AL XLPE CWS HDPE | YES | YES | BPD-T2-CB11 | DistributionFeeder | CB11_Waihao Downs | T2 | 11.22 | NO | NO
CB12 | IKAWAI | 11 | 339.15 | 400 | 270 | 5.2471 | 305 | 5.9273 | CABLE-3C 300MM² AL XLPE MDPE | YES | YES | BPD-T2-CB12 | DistributionFeeder | CB12_Ikawai | T2 | 11.22 | NO | NO
CB13 | WAIKAKAHI | 11 | 339.15 | 400 | 270 | 5.2471 | 305 | 5.9273 | CABLE-3C 300MM² AL XLPE MDPE | YES | YES | BPD-T2-CB13 | DistributionFeeder | CB13_Waikakahi | T2 | 11.22 | NO | NO
COONEY'S ROAD SUBSTATION (C1) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB642 | T1 HV 33 KV | 33 | 582.7931 | N/A | 465 | 26.5783 | 520 | 29.722 | OH LINE-JAGUAR | NO | N/A | CNR-CB642 | SubTransmission | CB642_CNR |  | 33 | NO | YES
CB35 | T1 LV 11 KV | 11 | 787.2958 | 1104 | 625 | 11.9078 | 705 | 13.4321 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | CNR-CB35 | SecondarySubstation | CNR |  | 11 | NO | YES
CB36 | STU ALTERNATE FEED | 11 | 125 | 144 | 100 | 1.9053 | 85 | 1.6195 | 1.8 MVA WINTER | NO | N/A | CNR-CB36 | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement
|  | 11 | 125 | 144 | 100 | 1.9053 | 35 | 0.66684 | 0.8 MVA SUMMER | NO | N/A |  | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement
|  | 11 | 125 | 144 | 100 | 1.9053 | 25 | 0.47631 | 0.6 MW BPD OFFLOAD | NO | N/A |  | SecondarySubstation | CNR |  | 11 | NO | NO | Manual entry to reflect contractual agreement
CB31 | BUS COUPLER BUS A | 11 | 1104 | 1200 | 880 | 16.7663 | 990 | 18.862 | CIRCUIT BREAKER-CNR-CB35-PROTECTION | NO | N/A | CNR-CB31 | SecondarySubstation | CNR |  | 11 | NO | NO
CB32 | BUS COUPLER BUS B | 11 | 1104 | 1200 | 880 | 16.7663 | 990 | 18.862 | CIRCUIT BREAKER-CNR-CB35-PROTECTION | NO | N/A | CNR-CB32 | SecondarySubstation | CNR |  | 11 | NO | NO
CB8 | CANNING PLANT | 11 | 378.9072 | 402 | 300 | 5.7158 | 340 | 6.4779 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB8 | DistributionFeeder | CB8_Drier 2 |  | 11 | NO | NO
CB9 | WET PROCESS | 11 | 394.695 | 402 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB9 | DistributionFeeder | CB9_WetProcess |  | 11 | NO | NO
CB11 | BOILER_CHILLER #1 | 11 | 378.9072 | 402 | 300 | 5.7158 | 340 | 6.4779 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB11 | DistributionFeeder | CB11_Boiler/Chiller 1 |  | 11 | NO | NO
CB12 | OFFICE | 11 | 394.695 | 402 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3-1C 400MM² AL XLPE CWS MDPE | NO | N/A | CNR-CB12 | DistributionFeeder | CB12_Office |  | 11 | NO | NO
STUDHOLME GXP (T5 & T6) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB1 | OTAIO | 11 | 352.9388 | 360 | 280 | 5.4307 | 315 | 6.1096 | CABLE-3C-300MM² AL XLPE HDPE | NO | N/A | STU-CB1 | DistributionFeeder | CB1_Otaio |  | 11.198 | NO | NO
CB2 | GLENAVY | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | NO | N/A | STU-CB2 | DistributionFeeder | CB2_Glenavy |  | 11.198 | NO | NO
CB3 | WAIMATE | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | NO | N/A | STU-CB3 | DistributionFeeder | CB3_Waimate |  | 11.198 | NO | NO
CB4 | (AEL)-T/P CB2812 INCOMER FROM T5 | 11 | 524 | 900 | 415 | 8.0491 | 470 | 9.1159 | POWER TRANSFORMER RATING AT 10.16 MVA | NO | N/A | STU-CB4 | GXP | STU_GXP | T5 | 11.198 | NO | YES
CB5 | BUS COUPLER | 11 | 744 | 744 | 595 | 11.5403 | 665 | 12.898 | CIRCUIT BREAKER-STU-CB5-PROTECTION | NO | N/A | STU-CB5 | GXP | STU |  | 11.198 | YES | NO
CB6 | (AEL)-T/P CB2812 INCOMER FROM T6 | 11 | 524 | 900 | 415 | 8.0491 | 470 | 9.1159 | POWER TRANSFORMER RATING AT 10.16 MVA | NO | N/A | STU-CB6 | GXP | STU_GXP | T6 | 11.198 | NO | YES
CB7 | WAIHAORUNGA | 11 | 352.9388 | 360 | 280 | 5.4307 | 315 | 6.1096 | CABLE-3C-300MM² AL XLPE HDPE | NO | N/A | STU-CB7 | DistributionFeeder | CB7_Waihaorunga |  | 11.198 | NO | NO
CB8 | MT. STUDHOLME | 11 | 247 | 360 | 195 | 3.7821 | 220 | 4.267 | OH LINE-70MM² CU | NO | N/A | STU-CB8 | DistributionFeeder | CB8_Mt Studholme |  | 11.198 | NO | NO
CB9 | MORVEN | 11 | 352.9388 | 300 | 240 | 4.6549 | 270 | 5.2368 | CABLE-3C-300MM² AL XLPE HDPE | NO | N/A | STU-CB9 | DistributionFeeder | CB9_Morven |  | 11.198 | NO | NO
TIMARU GXP (TP-TIM T3, T4 & T6) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB2662 | Waipopo | 11 | 276.287 | 400 | 220 | 4.1916 | 245 | 4.6679 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB2662 | DistributionFeeder | CB2662_Waipopo |  | 11 | NO | NO
CB2672 | Washdyke | 11 | 276.287 | 400 | 220 | 4.1916 | 245 | 4.6679 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB2672 | DistributionFeeder | CB2672_Washdyke |  | 11 | NO | NO
CB2682 | Ripple Plant 1/Showgrounds | 11 | 345 | 400 | 275 | 5.2395 | 310 | 5.9063 | CABLE-3X 1C 400MM2 AL XLPE HDPE | YES | NO | TIM-CB2682 | DistributionFeeder | CB2682_Showgrounds Hill |  | 11 | YES | NO
CB2692 | NST - TIM NO. 1 | 11 | 806.265 | 1184 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | TIM-CB2692 | SubTransmission | CB2692_North ST.1 |  | 11 | NO | NO | Standardised numbering to have "NO." before it
CB2702 | Morgans Road | 11 | 188.0321 | 400 | 150 | 2.8579 | 165 | 3.1437 | CABLE-3C 150MM² AL PILC STA | YES | NO | TIM-CB2702 | DistributionFeeder | CB2702_Morgans Rd |  | 11 | NO | NO
CB2712 | Mountainview Road | 11 | 368.4526 | 400 | 290 | 5.5252 | 330 | 6.2873 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | TIM-CB2712 | DistributionFeeder | CB2712_Mountain View Rd |  | 11 | NO | NO
CB2728 | Bus Coupler | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2728 - PROTECTION | YES | NO | TIM-CB2728 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB
CB2732 | Transformer T1 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2732 | SubTransmission | CB2732_ATM_T1 |  | 11 | NO | YES
CB2742 | Seadown | 11 | 394.4936 | 400 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | TIM-CB2742 | DistributionFeeder | CB2742_Levels Plain |  | 11 | NO | NO
CB2752 | 11 kV incomer T3 | 11 | 1544 | 1800 | 1235 | 23.5299 | 1385 | 26.3878 | CIRCUIT BREAKER-TIM-CB2752-PROTECTION | YES | NO | TIM-CB2752 | GXP | TIM_GXP | T3 | 11 | YES | YES
CB2762 | AEL Yard | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2762 | DistributionFeeder | CB2762_AEL Yard |  | 11 | NO | NO
CB2772 | GRM - TIM D | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2772 | SubTransmission | TIM_GRMD_SUBTRANS |  | 11 | NO | NO
CB2788 | Bus Coupler | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2788 - PROTECTION | YES | NO | TIM-CB2788 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB
CB2812 | GRM - TIM C | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2812 | SubTransmission | TIM_GRMC_SUBTRANS |  | 11 | NO | NO
CB2822 | GRM - TIM B | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2822 | SubTransmission | TIM_GRMB_SUBTRANS |  | 11 | NO | NO
CB2832 | Grants Road | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2832 | DistributionFeeder | CB2832_Grants Rd |  | 11 | NO | NO
CB2842 | 11 kV incomer T4 | 11 | 2466.8602 | 1800 | 1440 | 27.4357 | 1620 | 30.8651 | POWER TRANSFORMER RATING AT 47 MVA | YES | NO | TIM-CB2842 | GXP | TIM_GXP | T4 | 11 | NO | YES
CB2852 | Levels | 11 | 260.4067 | 400 | 205 | 3.9058 | 230 | 4.3821 | CABLE-3C 185MM² AL XLPE HDPE | YES | NO | TIM-CB2852 | DistributionFeeder | CB2852_Hadlow |  | 11 | NO | NO
CB2862 | Meadows Road | 11 | 394.4936 | 400 | 315 | 6.0016 | 355 | 6.7637 | CABLE-3C 300MM² AL XLPE HDPE | YES | NO | TIM-CB2862 | DistributionFeeder | CB2862_Meadows Rd |  | 11 | NO | NO
CB2878 | Bus Coupler | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2878 - PROTECTION | YES | NO | TIM-CB2878 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB
CB2912 | GRM - TIM A | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2912 | SubTransmission | TIM_GRMA_SUBTRANS |  | 11 | NO | NO
CB2922 | Transformer T2 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2922 | SubTransmission | CB2922_ATM_T2 |  | 11 | NO | YES
CB2932 | 11 kV incomer T6 | 11 | 2534 | 1800 | 1440 | 27.4357 | 1620 | 30.8651 | CABLE-TIM-CBL-T3-CB2752-CABLE | YES | NO | TIM-CB2932 | GXP | TIM_GXP | T6 | 11 | NO | NO
CB2942 | Old North Road | 11 | 280.8075 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | TIM-CB2942 | DistributionFeeder | CB2942_Old North Rd |  | 11 | NO | NO
CB2952 | Highfield | 11 | 280.0296 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 240MM² AL PILC STA | YES | NO | TIM-CB2952 | DistributionFeeder | CB2952_Highfield |  | 11 | NO | NO
CB2968 | Bus Coupler | 11 | 2500 | 2496 | 1995 | 38.0099 | 2245 | 42.773 | CIRCUIT BREAKER - TIM-CB2968 - PROTECTION | YES | NO | TIM-CB2968 | GXP | TIM_GXP |  | 11 | YES | NO | Manual entry based on substation drawing 12528 rating of the CB
CB2972 | Smithfield | 11 | 280.8075 | 400 | 220 | 4.1916 | 250 | 4.7631 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | TIM-CB2972 | DistributionFeeder | CB2972_Smithfield |  | 11 | NO | NO
CB2982 | NST - TIM NO. 2 | 11 | 412.566 | 1184 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | TIM-CB2982 | SubTransmission | TIM_GRMD_SUBTRANS |  | 11 | NO | NO | Standardised numbering to have "NO." before it
CB2992 | Ripple Plant 2/Goulds Road | 11 | 345 | 400 | 275 | 5.2395 | 310 | 5.9063 | CABLE-TIM-CB2992 | YES | NO | TIM-CB2992 | DistributionFeeder | CB2992_Goulds Road |  | 11 | YES | NO
CB3002 | Elginshire | 11 | 236.0033 | 400 | 185 | 3.5247 | 210 | 4.001 | CABLE - 3C 240MM² AL PILC | YES | NO | TIM-CB3002 | DistributionFeeder | CB3002_Elginshire |  | 11 | NO | NO
CB3012 | Arowhenua | 11 | 197.4144 | 400 | 155 | 2.9531 | 175 | 3.3342 | CABLE - 3C 150MM² AL PILC STA | YES | NO | TIM-CB3012 | DistributionFeeder | CB3012_Arowhenua |  | 11 | NO | NO
GRASMERE STREET SWITCHING STATION (TE901) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB2 | WHITE STREET | 11 | 160.5975 | 304 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 0.15IN² CU PILC STAS | YES | NO | GRM-CB2 | DistributionFeeder | CB2_White St |  | 11 | NO | NO
CB3 | GRM - TIM A & VT3 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB3 | SubTransmission | TIM_GRMA_SUBTRANS |  | 11 | NO | NO
CB4 | GRM - HNT A | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWA | YES | NO | GRM-CB4 | SubTransmission | CB4_GRM-HNT A |  | 11 | NO | NO
CB5 | NILE STREET & LS1 | 11 | 233.415 | 304 | 185 | 3.5247 | 210 | 4.001 | CABLE-3C 300MM² AL PILC SWAS | YES | NO | GRM-CB5 | DistributionFeeder | CB5_Nile St |  | 11 | NO | NO
CB6 | PARKVIEW TCE | 11 | 228 | 304 | 180 | 3.4295 | 205 | 3.9058 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | GRM-CB6 | DistributionFeeder | CB6_Parkview Terrace |  | 11 | NO | NO
CB7 | DOUGLAS STREET | 11 | 235.904 | 304 | 185 | 3.5247 | 210 | 4.001 | CABLE-3C 185MM² AL XLPE HDPE | YES | NO | GRM-CB7 | DistributionFeeder | CB7_Douglas St |  | 11 | NO | NO
CB8 | GRM - TIM B & VT8 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB8 | SubTransmission | TIM_GRMB_SUBTRANS |  | 11 | NO | NO
CB9 | GRM - NST A | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | GRM-CB9 | SubTransmission | CB9_GRM-NST A |  | 11 | NO | NO
CB10 | ASHBURY PARK | 11 | 201.4 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.25IN² AL PILC STAS | YES | NO | GRM-CB10 | DistributionFeeder | CB10_Ashbury Park |  | 11 | NO | NO
CB12 | SELWYN STREET | 11 | 176.1066 | 304 | 140 | 2.6674 | 155 | 2.9531 | CABLE-3C 300MM² AL PILC | YES | NO | GRM-CB12 | DistributionFeeder | CB12_Selwyn St |  | 11 | NO | NO
CB13 | GRM - HNT B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | GRM-CB13 | SubTransmission | CB13_GRM-HNT B |  | 11 | NO | NO
CB14 | GRM - TIM C & VT14 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB14 | SubTransmission | TIM_GRMC_SUBTRANS |  | 11 | NO | NO
CB15 | PARK LANE | 11 | 172.6194 | 304 | 135 | 2.5721 | 155 | 2.9531 | CABLE-3C 300MM² AL PILC SWA | YES | NO | GRM-CB15 | DistributionFeeder | CB15_Park Lane |  | 11 | NO | NO
CB16 | EVANS STREET | 11 | 167.96 | 304 | 130 | 2.4768 | 150 | 2.8579 | CABLE-3C 0.15IN² CU PILC STAS | YES | NO | GRM-CB16 | DistributionFeeder | CB16_Evans St |  | 11 | NO | NO
CB17 | JUNE STREET & LS2 | 11 | 232.56 | 304 | 185 | 3.5247 | 205 | 3.9058 | CABLE-3C 0.4IN² AL PILC SWA | YES | NO | GRM-CB17 | DistributionFeeder | CB17_June St |  | 11 | NO | NO
CB18 | GRM - NST B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | GRM-CB18 | SubTransmission | CB18_GRM-NST B |  | 11 | NO | NO
CB19 | GRM - TIM D & VT19 | 11 | 412.566 | 600 | 330 | 6.2873 | 370 | 7.0494 | CABLE-3C 400MM² CU PILC SWA | YES | NO | GRM-CB19 | SubTransmission | TIM_GRMD_SUBTRANS |  | 11 | NO | NO
CB20 | HOBBS STREET | 11 | 202.7789 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.4IN² AL PILC DSTA | YES | NO | GRM-CB20 | DistributionFeeder | CB20_Hobbs St |  | 11 | NO | NO
CB31 | BUS COUPLER BUS A | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - GRM-CB31 - RATING | YES | NO | GRM-CB31 | DistributionFeeder | CB2_White St |  | 11 | NO | NO | Manual entry based on substation drawing T269-01 rating of the CB
CB32 | BUS COUPLER BUS B | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - GRM-CB32 - RATING | YES | NO | GRM-CB32 | DistributionFeeder | CB2_White St |  | 11 | NO | NO | Manual entry based on substation drawing T269-01 rating of the CB
HUNT STREET SWITCHING STATION (TE903) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB1 | HARPER STREET | 11 | 224.4375 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB1 | DistributionFeeder | CB1_Harper St |  | 11 | NO | NO
CB2 | WILSON STREET | 11 | 110.4061 | 200 | 85 | 1.6195 | 95 | 1.81 | OH LINE-GOPHER | YES | NO | HNT-CB2 | DistributionFeeder | CB2_Wilson St |  | 11 | NO | NO
CB3 | GRM - HNT A & VT3 | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWA | YES | NO | HNT-CB3 | SubTransmission | CB3_HNT-GRM A |  | 11 | NO | NO
CB4 | BAKER STREET | 11 | 209.304 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 0.25IN² AL PILC DSTA | YES | NO | HNT-CB4 | DistributionFeeder | CB4_Baker St |  | 11 | NO | NO
CB5 | LE CREN STREET | 11 | 181.5117 | 200 | 145 | 2.7626 | 160 | 3.0484 | CABLE-3C 0.25IN² AL PILC SWA | YES | NO | HNT-CB5 | DistributionFeeder | CB5_Le Cren St |  | 11 | NO | NO
CB6 | HNT - NST A & VT6 | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | HNT-CB6 | SubTransmission | CB6_HNT-NST A |  | 11 | NO | NO
CB7 | CHURCH STREET -SOUTH SIDE | 11 | 160.474 | 200 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 0.15IN² AL PILC STAS | YES | NO | HNT-CB7 | DistributionFeeder | CB7_Church St SS |  | 11 | NO | NO
CB8 | SPARE (TEST CUBICLE ONLY) | 11 | 0 | 200 | 0 | 0 | 0 | 0 | #N/A | YES | NO | HNT-CB8 | DistributionFeeder | CB8_Spare |  | 11 | NO | NO
CB9 | BUS COUPLER | 11 | 3000 | N/A | 2400 | 45.7261 | 2700 | 51.4419 | CIRCUIT BREAKER - HNT-CB9 - RATING | YES | NO | HNT-CB9 | DistributionFeeder | CB9_Bus coupler |  | 11 | NO | NO | Manual entry based on substation drawing T269-02 rating of the CB
CB10 | GIBSON STREET | 11 | 209.475 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB10 | DistributionFeeder | CB10_Gibson St |  | 11 | NO | NO
CB11 | RHODES STREET | 11 | 165.5937 | 200 | 130 | 2.4768 | 145 | 2.7626 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB11 | DistributionFeeder | CB11_Rhodes St |  | 11 | NO | NO
CB12 | GRM - HNT B & VT12 | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | HNT-CB12 | SubTransmission | CB12_HNT-GRM B |  | 11 | NO | NO
CB13 | CLIFTON TCE | 11 | 203.49 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB13 | DistributionFeeder | CB13_Clifton Terrace |  | 11 | NO | NO
CB14 | CHURCH STREET -NORTH SIDE | 11 | 157.4141 | 200 | 125 | 2.3816 | 140 | 2.6674 | CABLE-3C 95MM² AL PILC SWAS | YES | NO | HNT-CB14 | DistributionFeeder | CB14_Church St NS |  | 11 | NO | NO
CB15 | HNT - NST B & VT15 | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | HNT-CB15 | SubTransmission | CB15_HNT-NST B |  | 11 | NO | NO
CB16 | ARTHUR STREET | 11 | 224.4375 | 200 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | HNT-CB16 | DistributionFeeder | CB16_Arthur St |  | 11 | NO | NO
CB17 | SPARE | 11 | 0 | 200 | 0 | 0 | 0 | 0 | #N/A | YES | NO | HNT-CB17 | DistributionFeeder | CB17_Spare |  | 11 | NO | NO
NORTH STREET SWITCHING STATION (TE902) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB3 | REDRUTH NO. 1 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3/1C 300MM² AL CWS | YES | NO | NST-CB3 | DistributionFeeder | CB3_Redruth 1 |  | 11 | NO | NO
CB4 | ROSE STREET & VT4 | 11 | 228.48 | 304 | 180 | 3.4295 | 205 | 3.9058 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB4 | DistributionFeeder | CB4_Rose St |  | 11 | NO | NO
CB5 | CRAIGIE AVE & LS1 | 11 | 201.9192 | 304 | 160 | 3.0484 | 180 | 3.4295 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB5 | DistributionFeeder | CB5_Craigie Ave |  | 11 | NO | NO
CB6 | GRM - NST A | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC STAS | YES | NO | NST-CB6 | SubTransmission | CB9_GRM-NST A |  | 11 | NO | NO
CB7 | HNT - NST A | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB7 | SubTransmission | CB6_HNT-NST A |  | 11 | NO | NO
CB8 | BARNARD STREET | 11 | 172.5214 | 200 | 135 | 2.5721 | 155 | 2.9531 | CABLE-3C 0.15IN² CU PILC STA | YES | NO | NST-CB8 | DistributionFeeder | CB8_Barnard St |  | 11 | NO | NO
CB9 | PORT NO. 1 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | NST-CB9 | DistributionFeeder | CB9_Port 1 |  | 11 | NO | NO
CB10 | FRASER STREET | 11 | 199.7639 | 304 | 155 | 2.9531 | 175 | 3.3342 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB10 | DistributionFeeder | CB10_Fraser St |  | 11 | NO | NO
CB11 | HAYES STREET | 11 | 206.8696 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 0.25IN² AL PILC STAS | YES | NO | NST-CB11 | DistributionFeeder | CB11_Hayes St |  | 11 | NO | NO
CB12 | HIGH STREET | 11 | 206.8696 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 0.25IN² AL PILC SWA | YES | NO | NST-CB12 | DistributionFeeder | CB12_High St |  | 11 | NO | NO
CB13 | PORT NO. 2 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE MDPE | YES | NO | NST-CB13 | DistributionFeeder | CB13_Port 2 |  | 11 | NO | NO
CB14 | HNT - NST B | 11 | 291.7687 | 400 | 230 | 4.3821 | 260 | 4.9537 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB14 | SubTransmission | CB15_HNT-NST B |  | 11 | NO | NO
CB15 | GRM - NST B | 11 | 297.464 | 400 | 235 | 4.4774 | 265 | 5.0489 | CABLE-3C 0.3IN² CU PILC SWAS | YES | NO | NST-CB15 | SubTransmission | CB18_GRM-NST B |  | 11 | NO | NO
CB16 | VICTORIA STREET & LS2 | 11 | 209.916 | 304 | 165 | 3.1437 | 185 | 3.5247 | CABLE-3C 185MM² AL PILC SWAS | YES | NO | NST-CB16 | DistributionFeeder | CB16_Victoria St |  | 11 | NO | NO
CB17 | STAFFORD STREET & VT17 | 11 | 135.8314 | 200 | 105 | 2.0005 | 120 | 2.2863 | CABLE-3C 0.075IN² CU PILC STAS | YES | NO | NST-CB17 | DistributionFeeder | CB17_Stafford St |  | 11 | NO | NO
CB18 | REDRUTH NO. 2 | 11 | 273.3264 | 304 | 215 | 4.0963 | 245 | 4.6679 | CABLE-3C 300MM² AL XLPE CWS MDPE | YES | NO | NST-CB18 | DistributionFeeder | CB18_Redruth 2 |  | 11 | NO | NO
CB31 | BUS COUPLER BUS A | 11 | 2500 | 1200 | 960 | 18.2905 | 1080 | 20.5768 | CIRCUIT BREAKER - NST-CB31 - PROTECTION | YES | NO | NST-CB31 | DistributionFeeder |  |  | 11 | NO | NO | Manual entry based on substation drawing T269-03 rating of the CB
CB32 | BUS COUPLER BUS B | 11 | 2500 | 1200 | 960 | 18.2905 | 1080 | 20.5768 | CIRCUIT BREAKER - NST-CB32 - PROTECTION | YES | NO | NST-CB32 | DistributionFeeder |  |  | 11 | NO | NO | Manual entry based on substation drawing T269-03 rating of the CB
CB35 | NST - TIM NO. 1 & VT35 | 11 | 806.265 | 1188 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | NST-CB35 | SubTransmission | CB2692_North ST.1 |  | 11 | NO | NO
CB36 | NST - TIM NO. 1 & VT36 | 11 | 806.265 | 1188 | 645 | 12.2889 | 725 | 13.8131 | CABLE-3/1C 1200MM² AL XLPE CWS MDPE | YES | NO | NST-CB36 | SubTransmission | CB2982_North ST.2 |  | 11 | NO | NO
ALPINE TIMARU (B774) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
2732 | 11 KV INCOMER NO. 1 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2732 | SubTransmission | CB2732_ATM_T1 |  | 11 | NO | YES
2922 | 11 KV INCOMER NO. 2 | 11 | 1120.544 | 1068 | 850 | 16.1947 | 960 | 18.2905 | CABLE-2 X 3/1C 630MM² CU | YES | NO | TIM-CB2922 | SubTransmission | CB2922_ATM_T2 |  | 11 | NO | YES
L406 | 33 KV INCOMER NO. 1 | 33 | 437.3866 | N/A | N/A | N/A | N/A | N/A | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | TIM-L406 | ZoneSubstation | ATM |  | 33 | NO | YES | Not a CB so no protection or SCADA alarms
L405 | 33 KV INCOMER NO. 2 | 33 | 437.3866 | N/A | N/A | N/A | N/A | N/A | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | TIM-L405 | ZoneSubstation | ATM_2 |  | 33 | NO | YES | Not a CB so no protection or SCADA alarms
L269 | SUBTRANSMISSION TO PLP | 33 | 171.4491 | 240 | 135 | 7.7163 | 150 | 8.5737 | CABLE-3/1C 95MM² AL XLPE PVC SCREENED | NO | N/A | TIM-L269 | SubTransmission | L269_PleasantPoint |  | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet
L413 | SUBTRANSMISSION TO PAR NO. 1 | 33 | 196.6 | 240 | 155 | 8.8594 | 175 | 10.0026 | OH LINE-QUAIL | NO | N/A | TIM-L413 | SubTransmission | L413_L418_Pareora | T1 | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet
L418 | SUBTRANSMISSION TO PAR NO. 2 | 33 | 188.6266 | 240 | 150 | 8.5737 | 165 | 9.431 | OH LINE-MINK | NO | N/A | TIM-L418 | SubTransmission | L413_L418_Pareora | T2 | 33 | NO | NO | Manual entry from AEL protection database under TIM GXP sheet
PAREORA (B712) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
2332 | 33 KV TIM-PAR NO. 1 | 33 | 196.6 | 320 | 155 | 8.8594 | 175 | 10.0026 | OH LINE-QUAIL | NO | N/A | PAR-CB2332 | SubTransmission | L413_L418_Pareora | T1 | 33 | NO | NO
2342 | 33 KV INCOMER NO. 1 | 33 | 491.79 | 320 | 255 | 14.5752 | 285 | 16.2899 | CABLE-3/1C 400MM² AL XLPE HDPE SCREENED | NO | N/A | PAR-CB2342 | ZoneSubstation | PAR | T1 | 33 | NO | NO
2358 | 33 KV BUS COUPLER NO. 1 | 33 | 400 | 320 | 255 | 14.5752 | 285 | 16.2899 | CIRCUIT BREAKER - PAR-CB2358 - PROTECTION | NO | N/A | PAR-CB2358 | ZoneSubstation | PAR |  | 33 | NO | NO | Manual entry from previous Switching Digrams
2368 | 33 KV BUS COUPLER NO. 2 | 33 | 400 | 320 | 255 | 14.5752 | 285 | 16.2899 | CIRCUIT BREAKER - PAR-CB2368 - PROTECTION | NO | N/A | PAR-CB2368 | ZoneSubstation | PAR |  | 33 | NO | NO | Manual entry from previous Switching Digrams
2372 | 33 KV INCOMER NO. 2 | 33 | 491.79 | 320 | 255 | 14.5752 | 285 | 16.2899 | CABLE-3/1C 400MM² AL XLPE HDPE SCREENED | NO | N/A | PAR-CB2372 | ZoneSubstation | PAR | T2 | 33 | NO | NO
2382 | 33 KV TIM-PAR NO. 2 | 33 | 188.6266 | 320 | 150 | 8.5737 | 165 | 9.431 | OH LINE-MINK | NO | N/A | PAR-CB2382 | SubTransmission | L413_L418_Pareora | T2 | 33 | NO | NO
CB31 | 11 KV BUS COUPLER | 11 | 1250 | 520 | 415 | 8.0649 | 465 | 9.0366 | CIRCUIT BREAKER - PAR-CB31 - PROTECTION | NO | N/A | PAR-CB31 | ZoneSubstation | PAR |  | 11.22 | NO | NO | Manual entry from previous Switching Digrams
CB35 | 11 KV INCOMER NO. 1 | 11 | 771.8586 | 950 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | PAR-CB35 | ZoneSubstation | PAR | T1 | 11.22 | NO | YES
CB36 | 11 KV INCOMER NO. 2 | 11 | 771.8586 | 950 | 615 | 11.9517 | 690 | 13.4092 | POWER TRANSFORMER RATING AT 15 MVA | NO | N/A | PAR-CB36 | ZoneSubstation | PAR | T2 | 11.22 | NO | YES
CB3 | WORKS NO. 1 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | #N/A | YES | NO | PAR-CB3 | DistributionFeeder | CB3_SFF No. 1 |  | 11.22 | NO | NO
CB4 | ST. ANDREWS | 11 | 256.8585 | 252 | 200 | 3.8867 | 225 | 4.3726 | OH LINE-DOG | YES | YES | PAR-CB4 | DistributionFeeder | CB4_St Andrews |  | 11.22 | NO | NO
CB5 | WORKS NO. 2 | 11 | 0 | 300 | 0 | 0 | 0 | 0 | #N/A | YES | NO | PAR-CB5 | DistributionFeeder | CB5_SFF No. 2 |  | 11.22 | NO | NO
CB6 | NORMANBY | 11 | 204.0399 | 252 | 160 | 3.1094 | 180 | 3.498 | OH LINE-RANGO | YES | YES | PAR-CB6 | DistributionFeeder | CB6_Normanby |  | 11.22 | NO | NO
CB7 | HOLMESTATION | 11 | 188.6266 | 252 | 150 | 2.915 | 165 | 3.2065 | OH LINE-MINK | YES | YES | PAR-CB7 | DistributionFeeder | CB7_Holmestation |  | 11.22 | NO | NO
PLEASANT POINT (B1212) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
L250 | 33 KV TIM-PLP INCOMER | 33 | 171.4491 | 134 | 105 | 6.0016 | 120 | 6.8589 | CABLE-3/1C 95MM² AL XLPE PVC SCREENED | NO | N/A | PLP-L250 | SubTransmission | L269_PleasantPoint |  | 33 | NO | NO
CB1 | WAITAWA | 11 | 148 | 252 | 115 | 2.2349 | 130 | 2.5264 | OH LINE-FERRET | YES | YES | PLP-CB1 | DistributionFeeder | CB1_Waitawa |  | 11.22 | NO | NO
CB2 | SUTHERLAND | 11 | 200.0091 | 252 | 160 | 3.1094 | 180 | 3.498 | CABLE-3C 150MM² AL PILC STA | YES | YES | PLP-CB2 | DistributionFeeder | CB2_Sutherlands |  | 11.22 | NO | NO
CB3 | 11 KV INCOMER | 11 | 321.6078 | 348 | 255 | 4.9556 | 285 | 5.5386 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | PLP-CB3 | ZoneSubstation | PLP |  | 11.22 | NO | YES
CB4 | TOTARA VALLEY | 11 | 189 | 252 | 150 | 2.915 | 170 | 3.3037 | OH LINE-MINK | YES | YES | PLP-CB4 | DistributionFeeder | CB4_Totara Valley |  | 11.22 | NO | NO
CB5 | PLEASANT POINT TOWNSHIP | 11 | 131 | 252 | 100 | 1.9434 | 115 | 2.2349 | OH LINE-7/14 CU | YES | NO | PLP-CB5 | DistributionFeeder | CB5_Pleasant Point Township |  | 11.22 | NO | NO
TEKAPO SUBSTATION (E197) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB1042 | TRANSPOWER INCOMER | 33 | 242 | N/A | 190 | 10.86 | 215 | 12.2889 | OH LINE-19/14 CU | NO | N/A | TKA-CB1042 | SubTransmission | SBT_33kV |  | 33 | NO | NO
M346 | 33 KV MT COOK | 33 | 247 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE - 3-70MM2 CU | YES | YES | TKA_M11-M346 | SubTransmission | TKA_M11 |  | 33 | NO | NO
M167 | 33 KV TEKAPO INCOMER | 33 | 183 | 150 | 120 | 6.8589 | 135 | 7.7163 | CIRCUIT BREAKER-TKA-CB1042-PROTECTION | NO | N/A | TEK-M167 | SubTransmission | SBT_33kV |  | 33 | NO | YES
M202 | 11 KV TEKAPO INCOMER | 11 | 328.0399 | 400 | 260 | 4.9537 | 295 | 5.6205 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | TEK-M202 | ZoneSubstation | TEK |  | 11 | NO | YES
M200 | HALDON-LILYBANK | 11 | 186.6183 | 276 | 145 | 2.7626 | 165 | 3.1437 | CABLE-1-3C 150 MM² AL PILC | YES | NO | TEK-M200 | DistributionFeeder | M200_Haldon_Lilybank |  | 11 | NO | NO
M201 | SIMONS | 11 | 73.7094 | 250 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | YES | YES | TEK-M201 | DistributionFeeder | M201_Simons |  | 11 | NO | NO
M205 | GODLEY | 11 | 73.7094 | 200 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | YES | YES | TEK-M205 | DistributionFeeder | M205_Godley |  | 11 | NO | NO
M206 | TEKAPO TOWNSHIP | 11 | 186.6183 | 276 | 145 | 2.7626 | 165 | 3.1437 | CABLE-1-3C 150 MM² AL PILC | YES | NO | TEK-M206 | DistributionFeeder | M206_Tekapo Township |  | 11 | NO | NO
UNWIN HUT SUBSTATION (E152) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
M302 | 33KV INCOMER | 33 | 26.2432 | 50 | 20 | 1.1432 | 20 | 1.1432 | POWER TRANSFORMER RATING AT 1.5 MVA | YES | YES | UHT-M302 | ZoneSubstation | UHT |  | 33 | NO | YES
M158 | VILLAGE 1 | 11 | 259.7 | 100 | 80 | 1.5242 | 90 | 1.7147 | CABLE-1-3C 150 MM² AL PILC | NO | N/A | UHT-M158 | DistributionFeeder | M158_Village |  | 11 | NO | NO
M159 | VILLAGE 2 | 11 | 259.7 | 100 | 80 | 1.5242 | 90 | 1.7147 | CABLE-1-3C 150 MM² AL PILC | NO | N/A | UHT-M159 | DistributionFeeder | M159_Village |  | 11 | NO | NO
OLD MAN RANGE SUBSTATION (E352) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
M331 | 11KV RECLOSER | 11 | 73.7094 | 120 | 55 | 1.0479 | 65 | 1.2384 | OH LINE-HERRING | YES | NO | OMR-M331 | SecondarySubstation | OMR |  | 11 | NO | YES
M338 | 22KV RECLOSER | 22 | 39.3648 | 60 | 30 | 1.1432 | 35 | 1.3337 | POWER TRANSFORMER RATING AT 1.5 MVA | YES | YES | OMR-M338 | DistributionFeeder | M338_Old Man Range |  | 22 | NO | YES
HALDON/LILYBANK SUBSTATION (E117) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
M82 | 11 KV RECLOSER | 11 | 52.4864 | 60 | 40 | 0.7621 | 45 | 0.85737 | POWER TRANSFORMER RATING AT 1 MVA | YES | NO | HLB-M82 | SecondarySubstation | HLB |  | 11 | NO | YES
M86 | 22 KV RECLOSER | 22 | 26.2432 | 30 | 20 | 0.7621 | 20 | 0.7621 | POWER TRANSFORMER RATING AT 1 MVA | YES | NO | HLB-M86 | SecondarySubstation | HLB |  | 22 | NO | YES
M32 | LILYBANK | 22 | 73.7094 | N/A | N/A | N/A | N/A | N/A | OH LINE-HERRING | NO | N/A | HLB-M32 | DistributionFeeder | M32_Lilybank |  | 22 | NO | NO | Not a CB hence no SCADA alarms or protection
M33 | HALDON | 22 | 73.7094 | N/A | N/A | N/A | N/A | N/A | OH LINE-HERRING | NO | N/A | HLB-M33 | DistributionFeeder | M33_Haldon |  | 22 | NO | NO | Not a CB hence no SCADA alarms or protection
TEMUKA GXP (TP-TMK) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
132 | 110 KV TRANSPOWER T1 INCOMER | 110 | 283.4265 | N/A | 225 | 42.8683 | 255 | 48.584 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB132 | GXP | TMK_GXP | T1 | 110 | NO | YES
112 | 110 KV TRANSPOWER T2 INCOMER | 110 | 283.4265 | N/A | 225 | 42.8683 | 255 | 48.584 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB112 | GXP | TMK_GXP | T2 | 110 | NO | YES
1252 | 33 KV TRANSPOWER T1 INCOMER | 33 | 928.0501 | N/A | 740 | 43.058 | 835 | 48.5857 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB1252 | GXP | TMK_GXP | T1 | 33.594 | NO | YES
1232 | 33 KV TRANSPOWER T2 INCOMER | 33 | 928.0501 | N/A | 740 | 43.058 | 835 | 48.5857 | POWER TRANSFORMER RATING AT 54 MVA | NO | N/A | TMK-CB1232 | GXP | TMK_GXP | T2 | 33.594 | NO | YES
1192 | CLANDEBOYE NO. 1 | 33 | 407.1941 | 510 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1192 | SubTransmission | CB1192_Clandeboye No.1 |  | 33.594 | NO | NO
1202 | RANGITATA NO. 2 | 33 | 207.2308 | 462 | 165 | 9.6008 | 185 | 10.7645 | CABLE-1-3C 95 MM² AL XLPE | YES | NO | TMK-CB1202 | SubTransmission | CB1202_Rangitata |  | 33.594 | NO | NO
1212 | TEMUKA NO. 1 | 33 | 426.3301 | 582 | 340 | 19.7834 | 380 | 22.1109 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1212 | SubTransmission | CB1212_Temuka No.1 |  | 33.594 | NO | NO
1222 | CLANDEBOYE NO. 3 | 33 | 407.1941 | 540 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1222 | SubTransmission | CB1222_Clandeboye No.3 |  | 33.594 | NO | NO
1262 | TEMUKA NO. 2 | 33 | 426.3301 | 582 | 340 | 19.7834 | 380 | 22.1109 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1262 | SubTransmission | CB1262_Temuka No.2 |  | 33.594 | NO | NO
1272 | CLANDEBOYE NO. 2 & RANGITATA NO. 1 | 33 | 496.0602 | 510 | 395 | 22.9837 | 445 | 25.893 | OH LINE-WOLF | NO | N/A | TMK-CB1272 | SubTransmission | CB1272_Clandeboye No.2 |  | 33.594 | NO | NO
1282 | CLANDEBOYE NO. 4 | 33 | 407.1941 | 660 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | TMK-CB1282 | SubTransmission | CB1282_Clandeboye No.4 |  | 33.594 | NO | NO
1292 | GERALDINE | 33 | 256.8585 | 462 | 205 | 11.9282 | 230 | 13.3829 | OH LINE-DOG | YES | NO | TMK-CB1292 | SubTransmission | CB1292_Geraldine |  | 33.594 | NO | NO
TEMUKA (D816) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB1 | TEMUKA WEST | 11 | 259.3186 | 402 | 205 | 3.9058 | 230 | 4.3821 | CABLE-1-3C 300 MM² AL XLPE HD | YES | NO | TMK-CB1 | DistributionFeeder | CB1_Temuka West |  | 11 | NO | NO
CB2 | MILFORD | 11 | 159.408 | 402 | 125 | 2.3816 | 140 | 2.6674 | CABLE-1-3C 150 MM² AL PILC | YES | YES | TMK-CB2 | DistributionFeeder | CB2_Milford |  | 11 | NO | NO
CB3 | WINCHESTER | 11 | 300 | 402 | 240 | 4.5726 | 270 | 5.1442 | LINK-T546 | YES | YES | TMK-CB3 | DistributionFeeder | CB3_Winchester |  | 11 | NO | NO
CB4 | INCOMER NO. 1 | 11 | 1041.987 | 1080 | 830 | 15.8136 | 935 | 17.8141 | CABLE-6-1C 500 MM² CU XLPE | NO | N/A | TMK-CB4 | ZoneSubstation | TMK |  | 11 | NO | YES
CB5 | BUS COUPLER | 11 | 984 | 984 | 785 | 14.9563 | 885 | 16.8615 | CIRCUIT BREAKER-TMK-CB5-PROTECTION | NO | N/A | TMK-CB5 | ZoneSubstation | TMK |  | 11 | YES | NO | Load Capability equal protection OC due to lack of information
CB6 | INCOMER NO. 2 | 11 | 1041.987 | 1080 | 830 | 15.8136 | 935 | 17.8141 | CABLE-6-1C 500 MM² CU XLPE | NO | N/A | TMK-CB6 | ZoneSubstation | TMK |  | 11 | NO | YES
CB7 | RANGITATA | 11 | 300 | 402 | 240 | 4.5726 | 270 | 5.1442 | LINK-T547 | YES | YES | TMK-CB7 | DistributionFeeder | CB7_Rangitata |  | 11 | NO | NO
CB8 | TEMUKA EAST | 11 | 241 | 402 | 190 | 3.62 | 215 | 4.0963 | OH LINE-7/0.136 CU | YES | NO | TMK-CB8 | DistributionFeeder | CB8_Temuka East |  | 11 | NO | NO
CB9 | WAITOHI | 11 | 176 | 402 | 140 | 2.6674 | 155 | 2.9531 | OH LINE-19/16 CU | YES | YES | TMK-CB9 | DistributionFeeder | CB9_Waitohi |  | 11 | NO | NO
GERALDINE (D823) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
G259 | 33 KV INCOMER | 33 | 256.8585 | 350 | 205 | 11.9282 | 230 | 13.3829 | OH LINE-DOG | NO | N/A | GLD-G259 | SubTransmission | GLD |  | 33.594 | NO | YES
G260 | 11 KV INCOMER | 11 | 783.3789 | 948 | 625 | 11.9674 | 705 | 13.4992 | POWER TRANSFORMER RATING AT 15 MVA | YES | NO | GLD-G260 | ZoneSubstation | GLD |  | 11.055 | NO | YES
G156 | WOODBURY | 11 | 241 | 350 | 190 | 3.6381 | 215 | 4.1168 | OH LINE-7/0.136 CU | YES | YES | GLD-G156 | DistributionFeeder | G156_Woodbury |  | 11.055 | NO | NO
G191 | GERALDINE TOWNSHIP | 11 | 241 | 350 | 190 | 3.6381 | 215 | 4.1168 | OH LINE-7/0.136 CU | YES | NO | GLD-G191 | DistributionFeeder | G191_Geraldine Township |  | 11.055 | NO | NO
G194 | SPEECHLEY | 11 | 188.6266 | 350 | 150 | 2.8722 | 165 | 3.1594 | OH LINE-MINK | YES | YES | GLD-G194 | DistributionFeeder | G194_Speechly |  | 11.055 | NO | NO
RANGITATA (D1479) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
1522 | 33 KV INCOMER NO. 1 | 33 | 171.8611 | 402 | 135 | 7.8552 | 150 | 8.728 | AEL-FONTERRA CONTRACTUAL-10 MW LIMIT | YES | NO | RGA_T1-CB1522 | SubTransmission | RGA_T1 |  | 33.594 | YES | YES
1562 | 33 KV INCOMER NO. 2 | 33 | 207.2308 | 402 | 165 | 9.6008 | 185 | 10.7645 | CABLE-1-3C 95 MM² AL XLPE | YES | YES | RGA_T2-CB1562 | SubTransmission | RGA_T2 |  | 33.594 | NO | YES
CB35 | 11 KV INCOMER NO. 1 | 11 | 793.8 | 1048 | 635 | 12.3403 | 710 | 13.7979 | CABLE-3-1C 630 MM² CU XLPE | YES | YES | RGA_T1-CB35 | ZoneSubstation | RGA_T1 |  | 11.22 | NO | NO
CB36 | 11 KV INCOMER NO. 2 | 11 | 873.4262 | 1048 | 695 | 13.5064 | 785 | 15.2554 | CABLE-6-1C 400 MM² AL XLPE | NO | N/A | RGA_T2-CB36 | ZoneSubstation | RGA_T2 |  | 11.22 | NO | NO
CB31 | BUS COUPLER NO. 1 (N/O) | 11 | 800 | N/A | 640 | 12.4375 | 720 | 13.9922 | CABLE-3-1C 630MM2 AL XLPE HDPE | NO | N/A | RGA_T1-CB31 | ZoneSubstation | RGA_T1 |  | 11.22 | NO | NO | Manual entry based on tie cable rating
CB32 | BUS COUPLER NO. 2 | 11 | 800 | 600 | 480 | 9.3281 | 540 | 10.4941 | CABLE-3-1C 630MM2 AL XLPE HDPE | NO | N/A | RGA_T2-CB32 | ZoneSubstation | RGA_T2 |  | 11.22 | NO | NO | Manual entry based on tie cable rating
CB2 | ARUNDEL | 11 | 256.8585 | 300 | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | NO | N/A | RGA_T1-CB2 | DistributionFeeder | CB2_Arundel |  | 11.22 | NO | NO
CB3 | MAHAN ROAD | 11 | 208.1814 | 300 | 165 | 3.2065 | 185 | 3.5952 | CABLE-1-3C 95 MM² XLPE | NO | N/A | RGA_T1-CB3 | DistributionFeeder | CB3_Mahan Road |  | 11.22 | NO | NO
CB4 | OLD MAIN SOUTH ROAD | 11 | 256.8585 | N/A | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | NO | N/A | RGA_T1-CB4 | DistributionFeeder | CB4_Main South Road |  | 11.22 | NO | NO
CB11 | BELFIELD | 11 | 275.3865 | 300 | 220 | 4.2754 | 245 | 4.7612 | OH LINE-IODINE | YES | YES | RGA_T2-CB11 | DistributionFeeder | CB11_Belfield |  | 11.22 | NO | NO
CB12 | ORTON | 11 | 275.3865 | 300 | 220 | 4.2754 | 245 | 4.7612 | OH LINE-IODINE | YES | NO | RGA_T2-CB12 | DistributionFeeder | CB12_Orton |  | 11.22 | NO | NO
CB13 | RANGITATA ISLAND | 11 | 256.8585 | 300 | 205 | 3.9839 | 230 | 4.4697 | OH LINE-DOG | YES | YES | RGA_T2-CB13 | DistributionFeeder | CB13_Rangitata Island |  | 11.22 | NO | NO
CANAL ROAD (CB1412) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB1412 | 33 KV CIRCUIT BREAKER | 33 | 171.8611 | 423 | 135 | 7.8552 | 150 | 8.728 | AEL-FONTERRA CONTRACTUAL-10 MW LIMIT | YES | NO | CNL-RGA-CB1412 | SwitchingStation | CNL-RGA |  | 33.594 | YES | NO
CLANDEBOYE NO. 1 (D1246) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
T615 | 33 KV INCOMER NO. 1 | 33 | 407.1941 | 512 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD1-T615 | SubTransmission | CD_1 | T1 | 33.594 | NO | NO
T616 | 33 KV INCOMER NO. 2 | 33 | 347.7083 | 512 | 275 | 16.0013 | 310 | 18.0378 | CABLE-3-1C 300 MM² AL XLPE | NO | N/A | CD1-T616 | SubTransmission | CD_1 | T2 | 33.594 | NO | NO
T600 | MILK POWDER NO. 2 | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T600 | DistributionFeeder | T600_Tie to Milk Powder 2 |  | 11 | NO | NO
T601 | FIRE SERVICES | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T601 | DistributionFeeder | T601_Fire Services |  | 11 | NO | NO
T602 | WHEY PROCESSING | 11 | 239.5512 | 480 | 190 | 3.62 | 215 | 4.0963 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T602 | DistributionFeeder | T602_Whey Processing |  | 11 | NO | NO
T603 | LACTOSE PLANT | 11 | 342.0164 | 480 | 270 | 5.1442 | 305 | 5.811 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD1-T603 | DistributionFeeder | T603_Lactose Plant |  | 11 | NO | NO
T604 | SPARE | 11 | 239.5512 | 480 | 190 | 3.62 | 215 | 4.0963 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T604 | DistributionFeeder | T603_Lactose Plant |  | 11 | NO | NO | Manual entry from previous Switching Digrams
T605 | TIE TO MILFORD CLANDEBOYE ROAD | 11 | 122.77 | 252 | 95 | 1.81 | 110 | 2.0958 | CABLE-1-3C 95 MM² AL PILC | YES | NO | CD1-T605 | DistributionFeeder | T605_Tie to Milford |  | 11 | NO | NO
T606 | 11 KV INCOMER NO. 1 | 11 | 1049.7278 | 1440 | 835 | 15.9089 | 940 | 17.9094 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | CD1-T606 | ZoneSubstation | CD_1 | T1 | 11 | NO | YES
T607 | BUS COUPLER | 11 | 1250 | 1440 | 1000 | 19.0526 | 1125 | 21.4341 | CIRCUIT BREAKER-CD1-T607-RATING | NO | N/A | CD1-T607 | ZoneSubstation | CD_1 |  | 11 | NO | NO | Manual entry from previous Switching Digrams
T608 | 11 KV INCOMER NO. 2 | 11 | 1049.7278 | 1440 | 835 | 15.9089 | 940 | 17.9094 | POWER TRANSFORMER RATING AT 20 MVA | NO | N/A | CD1-T608 | ZoneSubstation | CD_1 | T2 | 11 | NO | YES
T609 | MILD RECEPTION | 11 | 303.1654 | 480 | 240 | 4.5726 | 270 | 5.1442 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T609 | DistributionFeeder | T609_Milk Reception |  | 11 | NO | NO
T610 | CHILLED WATER NO. 1 | 11 | 179.6634 | 480 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T610 | DistributionFeeder | T610_Chilled Water 1 |  | 11 | NO | NO
T611 | EFFLUENT PLANT | 11 | 179.6634 | 480 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | NO | N/A | CD1-T611 | DistributionFeeder | T611_Effluent Plant |  | 11 | NO | NO
T612 | MILK TREATMENT | 11 | 122.77 | 480 | 95 | 1.81 | 110 | 2.0958 | CABLE-1-3C 95 MM² AL PILC | NO | N/A | CD1-T612 | DistributionFeeder | T612_Milk Treatment |  | 11 | NO | NO
T613 | ROLLESTON ROAD | 11 | 179.6634 | 360 | 140 | 2.6674 | 160 | 3.0484 | CABLE-1-3C 185 MM² AL PILC | YES | NO | CD1-T613 | DistributionFeeder | T613_Rolleston Rd |  | 11 | NO | NO
T614 | POWDER HANDELING | 11 | 321.2648 | 480 | 255 | 4.8584 | 285 | 5.43 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD1-T614 | DistributionFeeder | T614_Tie to Powder Handling |  | 11 | NO | NO
CLANDEBOYE NO. 2 (D1462) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
T662 | 33 KV INCOMER NO. 3 | 33 | 407.1941 | 540 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD2-T662 | SubTransmission | CD_2 | T3 | 33.594 | NO | NO
T663 | 33 KV INCOMER NO. 4 | 33 | 407.1941 | 660 | 325 | 18.9106 | 365 | 21.2381 | CABLE-3-1C 400 MM² AL XLPE | NO | N/A | CD2-T663 | SubTransmission | CD_2 | T4 | 33.594 | NO | NO
T650 | MILK POWDER NO. 1 | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T650 | DistributionFeeder | T650_Tie to Milk Powder 1 |  | 11 | NO | NO
T651 | MILK POWDER NO. 3 | 11 | 330.3145 | 480 | 260 | 4.9537 | 295 | 5.6205 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T651 | DistributionFeeder | T651_Milk Powder 3 |  | 11 | NO | NO
T652 | WPC | 11 | 219.7882 | 1200 | 175 | 3.3342 | 195 | 3.7152 | CABLE-1-3C 185 MM² XLPE | NO | N/A | CD2-T652 | DistributionFeeder | T652_Tie to WPC |  | 11 | NO | NO
T653 | CHILLED WATER NO. 3 | 11 | 316.7399 | 480 | 250 | 4.7631 | 285 | 5.43 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T653 | DistributionFeeder | T653_Chilled Water 3 |  | 11 | NO | NO
T654 | R22 REPLACEMENT | 11 | 309.1922 | 480 | 245 | 4.6679 | 275 | 5.2395 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T654 | DistributionFeeder | T654_Tie to Boiler House |  | 11 | NO | NO
T655 | 11 KV INCOMER NO. 4 | 11 | 1312.1597 | 1600 | 1045 | 19.9099 | 1180 | 22.482 | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | CD2-T655 | ZoneSubstation | CD_2 | T4 | 11 | NO | YES
T656 | BUS COUPLER | 11 | 1250 | 1400 | 1000 | 19.0526 | 1125 | 21.4341 | CIRCUIT BREAKER-CD2-T656-RATING | NO | N/A | CD2-T656 | ZoneSubstation | CD_2 |  | 11 | NO | NO | Manual entry from previous Switching Digrams
T657 | 11 KV INCOMER NO. 3 | 11 | 1312.1597 | 1400 | 1045 | 19.9099 | 1180 | 22.482 | POWER TRANSFORMER RATING AT 25 MVA | NO | N/A | CD2-T657 | ZoneSubstation | CD_2 | T3 | 11 | NO | YES
T658 | MILK POWDER NO. 2 | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T658 | DistributionFeeder | T658_Milk Powder 2 |  | 11 | NO | YES
T659 | MOZZ REFRIG/MOZZ NO. 1 | 11 | 306.0371 | 480 | 240 | 4.5726 | 275 | 5.2395 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T659 | DistributionFeeder | T659_Tie to Energy Centre 1 |  | 11 | NO | NO
T660 | REFIGERATION | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T660 | DistributionFeeder | T660_Refrigeration |  | 11 | NO | NO
T661 | LABORATORY | 11 | 285.0659 | 480 | 225 | 4.2868 | 255 | 4.8584 | CABLE-1-3C 300 MM² AL XLPE | NO | N/A | CD2-T661 | DistributionFeeder | T661_Laboratory |  | 11 | NO | NO
CB2 | MOZZ NO. 3 PACKING | 11 | 630 | 600 | 480 | 9.1452 | 540 | 10.2884 | RMU SWITCH-T708 | NO | N/A | CD2-CB2 | DistributionFeeder | CB2_Mozz3_1 |  | 11 | NO | NO
CB15 | MOZZ NO. 3 MAIN PROCESS | 11 | 630 | 600 | 480 | 9.1452 | 540 | 10.2884 | RMU SWITCH-T737 | NO | N/A | CD2-CB15 | DistributionFeeder | CB15_Mozz3_2 |  | 11 | NO | NO
TWIZEL (E120) | [11 empty] | Supporting info
CB ID | DESIGNATION | Rated | LOAD CAPABILITY | OC PICKUP | SCADA ALARM |  |  |  | LIMITING EQUIPMENT | RECLOSING |  | OC Pick up Reference ID | Supply Level | Station/Feeder | Refered to PTX | Voltage | Include CB | Include PTX | Notes
|  | Voltage |  |  | Pre-Emergency |  | Emergency |  |  | AVAILABLE | UTILISED
|  | (kV) | (A) | (A) | (A) | (MVA) | (A) | (MVA)
CB6312 | 33 KV TP INCOMER | 33 | 350 | 252 | 200 | 11.4315 | 225 | 12.8605 | TRANSFORMER-T18-TRANSFORMER | NO | N/A | TWZ-CB6312 | GXP | TWZ_GXP |  | 33 | NO | NO
Z68 | 33 KV AEL INCOMER | 33 | 296 | 150 | 120 | 6.8589 | 135 | 7.7163 | OH LINE-WAXWING | NO | N/A | TVS-Z68 | SubTransmission | TWZ_GXP |  | 33 | NO | NO
Z1 | URBAN NO. 1 | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE - MINK | NO | N/A | TVS-Z1 | DistributionFeeder | Z1_Urban No. 1 |  | 11 | NO | NO
Z2 | URBAN NO. 2 | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE-MINK | NO | N/A | TVS-Z2 | DistributionFeeder | Z2_Urban No. 2 |  | 11 | NO | NO
Z3 | INDUSTRIAL | 11 | 85.3875 | 150 | 65 | 1.2384 | 75 | 1.4289 | CABLE-1-3C 35 MM² AL PILC | NO | N/A | TVS-Z3 | DistributionFeeder | Z3_Industrial |  | 11 | NO | NO
Z4 | TWIZEL RURAL | 11 | 189 | 152 | 120 | 2.2863 | 135 | 2.5721 | OH LINE - MINK | NO | N/A | TVS-Z4 | DistributionFeeder | Z4_Twizel Rural |  | 11 | NO | NO
Z5 | SPARE | 11 | N/A | N/A | 0 | 0 | N/A | N/A | N/A | NO | N/A | TVS-Z5 | DistributionFeeder | Z5_Spare |  | 11 | NO | NO | Spare i.e. not utilised
Z6 | 11 KV INCOMER NO. 1 | 11 | 328.0399 | N/A | 260 | 4.9537 | 295 | 5.6205 | POWER TRANSFORMER RATING AT 6.25 MVA | NO | N/A | TVS-Z6 | ZoneSubstation | TVS |  | 11 | NO | YES
Z7 | 11 KV INCOMER NO. 2 | 11 | N/A | N/A | 0 | 0 | N/A | N/A | N/A | NO | N/A | TVS-Z7 | ZoneSubstation | TVS |  | 11 | NO | NO | Spare i.e. not utilised
Z9 | LOCAL SERVICE | 11 | 251.6 | 30 | 20 | 0.38105 | 25 | 0.47631 | CABLE - 1-3C 95 MM² CU XLPE | NO | N/A | TVS-Z9 | DistributionFeeder | Z9_Local Supply |  | 11 | NO | NO
Note on D2: Author: As agreed upon by Network Departments on the 01/03/2021 During SCADA Alarams proposal session
Note on D3: Author: As agreed upon by Network Departments on the 01/03/2021 During SCADA Alarams proposal session
Note on R6: Author: Leave blank if not used
Note on E34: Author: Manual entry from previous Switching Digrams
Note on F34: Author: Manual entry from previous Switching Digrams
Note on K34: Author: Manual entry
Note on E44: Author: Manual entry from previous Switching Diagrams
Note on K44: Author: Manual entry
Note on E45: Author: Manual entry from previous Switching Diagrams
Note on K45: Author: Manual entry
Note on E56: Author: Manual entry from previous Switching Diagrams
Note on I56: Author: Manual entry from previous Switching Diagrams
Note on K56: Author: Manual entry from previous Switching Diagrams
Note on E57: Author: Manual entry from previous Switching Diagrams
Note on F57: Author: Equal value above
Note on I57: Author: Manual entry from previous Switching Diagrams
Note on K57: Author: Manual entry from previous Switching Diagrams
Note on E58: Author: Manual entry from previous Switching Diagrams
Note on F58: Author: Equal value above
Note on I58: Author: Manual entry from previous Switching Diagrams
Note on K58: Author: Manual entry from previous Switching Diagrams
Note on E90: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K90: Author: Manual entry
Note on E96: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K96: Author: Manual entry
Note on E103: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K103: Author: Manual entry
Note on E109: Author: Manual entry based on substation drawing 12528 rating of the CB
Note on K109: Author: Manual entry
Note on E138: Author: Manual entry based on substation drawing T269-01 rating of the CB
Note on K138: Author: Manual entry
Note on E139: Author: Manual entry based on substation drawing T269-01 rating of the CB
Note on K139: Author: Manual entry
Note on E153: Author: Manual entry based on substation drawing T269-02 rating of the CB
Note on K153: Author: Manual entry
Note on E183: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on F183: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on K183: Author: Manual entry
Note on E184: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on F184: Author: Manual entry based on substation drawing T269-03 rating of the CB
Note on K184: Author: Manual entry
Note on F194: Author: Not a CB so no protection or SCADA alarms
Note on G194: Author: Not a CB so no protection or SCADA alarms
Note on H194: Author: Not a CB so no protection or SCADA alarms
Note on I194: Author: Not a CB so no protection or SCADA alarms
Note on J194: Author: Not a CB so no protection or SCADA alarms
Note on F195: Author: Not a CB so no protection or SCADA alarms
Note on G195: Author: Not a CB so no protection or SCADA alarms
Note on H195: Author: Not a CB so no protection or SCADA alarms
Note on I195: Author: Not a CB so no protection or SCADA alarms
Note on J195: Author: Not a CB so no protection or SCADA alarms
Note on F196: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on F197: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on F198: Author: Manual entry from AEL protection database under TIM GXP sheet
Note on E206: Author: Manual entry from previous switching digram
Note on K206: Author: Manual entry
Note on E207: Author: Manual entry from previous switching digram
Note on K207: Author: Manual entry
Note on E210: Author: Manual entry from previous switching digram
Note on K210: Author: Manual entry
Note on F264: Author: Not a CB so no protection or SCADA alarms
Note on G264: Author: Not a CB so no protection or SCADA alarms
Note on H264: Author: Not a CB so no protection or SCADA alarms
Note on I264: Author: Not a CB so no protection or SCADA alarms
Note on J264: Author: Not a CB so no protection or SCADA alarms
Note on F265: Author: Not a CB so no protection or SCADA alarms
Note on G265: Author: Not a CB so no protection or SCADA alarms
Note on H265: Author: Not a CB so no protection or SCADA alarms
Note on I265: Author: Not a CB so no protection or SCADA alarms
Note on J265: Author: Not a CB so no protection or SCADA alarms
Note on E292: Author: Manual entry. =OC limit
Note on K292: Author: Manual entry
Note on E316: Author: Manual entry
Note on K316: Author: Manual entry
Note on E317: Author: Manual entry
Note on K317: Author: Manual entry
Note on E341: Author: Set to equal T602 for now
Note on K341: Author: Set to equal T602 for now
Note on E344: Author: Manual entry based on previous switching diagram
Note on K344: Author: Manual entry
Note on E365: Author: Manual entry based on previous switching diagram
Note on K365: Author: Manual entry
Note on E384: Author: Not Utilised at the moment
Note on F384: Author: Not Utilised at the moment
Note on I384: Author: Not Utilised at the moment
Note on J384: Author: Not Utilised at the moment
Note on K384: Author: Not Utilised at the moment
Note on F385: Author: No protection information in AEL protection database
Note on E386: Author: Not Utilised at the moment
Note on F386: Author: Not Utilised at the moment
Note on I386: Author: Not Utilised at the moment
Note on J386: Author: Not Utilised at the moment
Note on K386: Author: Not Utilised at the moment

## ABY_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of | ID | Type | ID | Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal R. |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [5 empty] | Data |  |  |  |  | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | - | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPABY_GXP110 | GXPABY_GXPDS64110Disconnector | GXP | ABY_GXP | 110 kv Bus | 11 kV Bus | 1 | TP Branch Report ABY.TF.T2 | DS64 | Disconnector | ABY-DS-64 | Disconnector | 110 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 152.4205 | 152.4205 | 152.4205 | 152.4205 | 152.4205 | - | - | - | - | ABY_GXP152.420471066061 | GXPABY_GXP110800 | GXPABY_GXP110800 | 152.4205 | 800 | 800 | 110 kv Bus | 11 kV Bus | Disconnector-DS64-Disconnector | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Circuit Breaker | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 2 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | ABY-CB62 | Circuit Breaker | 110 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 476.314 | 476.314 | 476.314 | 476.314 | 476.314 | - | - | - | - | ABY_GXP476.313972081441 | GXPABY_GXP1102500 | GXPABY_GXP1102500 | 476.314 | 2500 | 2500 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Circuit Breaker | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Current Transformer | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 3 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | ABY-CT-CT62 | Current Transformer | 110 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | 238.157 | 238.157 | 238.157 | 238.157 | - | - | - | - | ABY_GXP238.156986040721 | GXPABY_GXP1101250 | GXPABY_GXP1101250 | 238.157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Current Transformer | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Current Transformer | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 4 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | ABY-CT-CT62 | Current Transformer | 110 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | 238.157 | 238.157 | 238.157 | 238.157 | - | - | - | - | ABY_GXP238.156986040721 | GXPABY_GXP1101250 | GXPABY_GXP1101250 | 238.157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Current Transformer | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Current Transformer | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 5 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | ABY-CT-CT62 | Current Transformer | 110 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | 238.157 | 238.157 | 238.157 | 238.157 | - | - | - | - | ABY_GXP238.156986040721 | GXPABY_GXP1101250 | GXPABY_GXP1101250 | 238.157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Current Transformer | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Protection | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 6 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | Relay SEL 451 | Protection | 110 | 199 | 37.9146 | 199 | 37.9146 | 199 | 37.9146 | - | - | - | - | 199 | 37.9146 | 199 | 37.9146 | 600 | 114.3154 | 400 | 76.2102 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 37.9146 | 37.9146 | 37.9146 | - | - | 37.9146 | 114.3154 | 76.2102 | - | ABY_GXP37.9145921776827 | GXPABY_GXP110199 | GXPABY_GXP110199 | 37.9146 | 199 | 199 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Protection | 110
GXPABY_GXP110 | GXPABY_GXPABY-CB62110Protection | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 7 | TP Branch Report ABY.TF.T2 | ABY-CB62 | Circuit Breaker | Relay 7UT613 | Protection | 110 | 199 | 37.9146 | 199 | 37.9146 | 199 | 37.9146 | - | - | - | - | 199 | 37.9146 | 199 | 37.9146 | 800 | 152.4205 | 400 | 76.2102 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 37.9146 | 37.9146 | 37.9146 | - | - | 37.9146 | 152.4205 | 76.2102 | - | ABY_GXP37.9145921776827 | GXPABY_GXP110199 | GXPABY_GXP110199 | 37.9146 | 199 | 199 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB62-Protection | 110
GXPABY_GXP110 | GXPABY_GXPT2110HV Winding | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 8 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | HV Winding | 110 | 105 | 20.0052 | 105 | 20.0052 | 105 | 20.0052 | 155 | 29.5315 | 148 | 28.1978 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ABY_GXP | GXPABY_GXP110 | GXPABY_GXP110105 |  |  | 105 | 110 kv Bus | 11 kV CBs | Transformer-T2-HV Winding | 110
GXPABY_GXP110 | GXPABY_GXPT2110Tap Changer | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 9 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Tap Changer | 110 | 250 | 47.6314 | 250 | 47.6314 | 250 | 47.6314 | 300 | 57.1577 | 300 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | 57.1577 | 57.1577 | - | - | - | - | ABY_GXP47.6313972081441 | GXPABY_GXP110250 | GXPABY_GXP110250 | 47.6314 | 250 | 250 | 110 kv Bus | 11 kV CBs | Transformer-T2-Tap Changer | 110
GXPABY_GXP110 | GXPABY_GXPT2110Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 10 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 110 | 2000 | 381.0512 | 2000 | 381.0512 | 2000 | 381.0512 | 2400 | 457.2614 | 2400 | 457.2614 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 381.0512 | 381.0512 | 381.0512 | 457.2614 | 457.2614 | - | - | - | - | ABY_GXP381.051177665153 | GXPABY_GXP1102000 | GXPABY_GXP1102000 | 381.0512 | 2000 | 2000 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 110
GXPABY_GXP110 | GXPABY_GXPT2110Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 11 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 110 | 2000 | 381.0512 | 2000 | 381.0512 | 2000 | 381.0512 | 2400 | 457.2614 | 2400 | 457.2614 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 381.0512 | 381.0512 | 381.0512 | 457.2614 | 457.2614 | - | - | - | - | ABY_GXP381.051177665153 | GXPABY_GXP1102000 | GXPABY_GXP1102000 | 381.0512 | 2000 | 2000 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 110
GXPABY_GXP110 | GXPABY_GXPT2110Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 12 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 110 | 2000 | 381.0512 | 2000 | 381.0512 | 2000 | 381.0512 | 2400 | 457.2614 | 2400 | 457.2614 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 381.0512 | 381.0512 | 381.0512 | 457.2614 | 457.2614 | - | - | - | - | ABY_GXP381.051177665153 | GXPABY_GXP1102000 | GXPABY_GXP1102000 | 381.0512 | 2000 | 2000 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 110
GXPABY_GXP11 | GXPABY_GXPT211LV Winding | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 13 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | LV Winding | 11 | 1050 | 20.0052 | 1050 | 20.0052 | 1050 | 20.0052 | 1548 | 29.4934 | 1480 | 28.1978 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ABY_GXP | GXPABY_GXP11 | GXPABY_GXP111050 |  |  | 1050 | 110 kv Bus | 11 kV CBs | Transformer-T2-LV Winding | 11
GXPABY_GXP11 | GXPABY_GXPT211Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 14 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | 1500 | 28.5788 | 1500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | 28.5788 | 28.5788 | - | - | - | - | ABY_GXP23.8156986040721 | GXPABY_GXP111250 | GXPABY_GXP111250 | 23.8157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 11
GXPABY_GXP11 | GXPABY_GXPT211Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 15 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | 1500 | 28.5788 | 1500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | 28.5788 | 28.5788 | - | - | - | - | ABY_GXP23.8156986040721 | GXPABY_GXP111250 | GXPABY_GXP111250 | 23.8157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 11
GXPABY_GXP11 | GXPABY_GXPT211Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 16 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | 1500 | 28.5788 | 1500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | 28.5788 | 28.5788 | - | - | - | - | ABY_GXP23.8156986040721 | GXPABY_GXP111250 | GXPABY_GXP111250 | 23.8157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 11
GXPABY_GXP11 | GXPABY_GXPT211Bushings | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 17 | TP Branch Report ABY.TF.T2 | T2 | Transformer | ABY-TF-T2 | Bushings | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | 1500 | 28.5788 | 1500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | 28.5788 | 28.5788 | - | - | - | - | ABY_GXP23.8156986040721 | GXPABY_GXP111250 | GXPABY_GXP111250 | 23.8157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Transformer-T2-Bushings | 11
GXPABY_GXP11 | GXPABY_GXPABY-CB271211Protection | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 18 | TP Branch Report ABY.TF.T2 | ABY-CB2712 | Circuit Breaker | Relay SEL 451 | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1635 | 31.1509 | 1635 | 31.1509 | 3600 | 68.5892 | 2400 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 31.1509 | 68.5892 | 45.7261 | - | ABY_GXP23.8156986040721 | GXPABY_GXP111250 | GXPABY_GXP111250 | 23.8157 | 1250 | 1250 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB2712-Protection | 11
GXPABY_GXP11 | GXPABY_GXPABY-CB271211Other Equipment | GXP | ABY_GXP | 110 kv Bus | 11 kV CBs | 19 | TP Branch Report ABY.TF.T2 | ABY-CB2712 | Circuit Breaker | ABY-CB2712-OEL | Other Equipment | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | ABY_GXP11.4315353299546 | GXPABY_GXP11600 | GXPABY_GXP11600 | 11.4315 | 600 | 600 | 110 kv Bus | 11 kV CBs | Circuit Breaker-ABY-CB2712-Other Equipment | 11
SubTransmissionCB2722_Fairlie11 | SubTransmissionCB2722_FairlieABY-CB272211Protection | SubTransmission | CB2722_Fairlie | CB2722 | F388 | 20 | TP Branch Report ABY.FDR.2722 | ABY-CB2722 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 450 | 8.5737 | 450 | 8.5737 | 900 | 17.1473 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 8.5737 | 17.1473 | 11.4315 | - | CB2722_Fairlie8.57365149746594 | SubTransmissionCB2722_Fairlie11450 | SubTransmissionCB2722_Fairlie11450 | 8.5737 | 450 | 450 | CB2722 | F388 | Circuit Breaker-ABY-CB2722-Protection | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_RaincliffABY-CB273211Protection | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 21 | TP Branch Report ABY.FDR.2732 | ABY-CB2732 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 225 | 4.2868 | 206 | 3.9248 | 900 | 17.1473 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 4.2868 | 17.1473 | 11.4315 | - | CB2732_Raincliff4.28682574873297 | DistributionFeederCB2732_Raincliff11225 | DistributionFeederCB2732_Raincliff11206 | 4.2868 | 225 | 206 | CB2732 | F234 SW.ST | Circuit Breaker-ABY-CB2732-Protection | 11
DistributionFeederCB2742_Cave11 | DistributionFeederCB2742_CaveABY-CB274211Protection | DistributionFeeder | CB2742_Cave | CB2742 | Pole 53272 | 22 | TP Branch Report ABY.FDR.2742 | ABY-CB2742 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 225 | 4.2868 | 206 | 3.9248 | 900 | 17.1473 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 4.2868 | 17.1473 | 11.4315 | - | CB2742_Cave4.28682574873297 | DistributionFeederCB2742_Cave11225 | DistributionFeederCB2742_Cave11206 | 4.2868 | 225 | 206 | CB2742 | Pole 53272 | Circuit Breaker-ABY-CB2742-Protection | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_Raincliff3-1c 400 mm² Al XLPE11- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 1 | GEMA/Drawing 12297 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 73.2 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 3 | 0.8 | 0.85 | 442.7565 | 8.4356 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.4356 | CB2732_Raincliff8.43564428719507 | DistributionFeederCB2732_Raincliff11442.7565 | DistributionFeederCB2732_Raincliff11442.7565 | 8.4356 | 442.7565 | 442.7565 | CB2732 | F234 SW.ST | Cable-3-1c 400 mm² Al XLPE | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_RaincliffF26711- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 2 | GEMA | F267 | ABS | - | - | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | - | - | - | - | CB2732_Raincliff15.2420471066061 | DistributionFeederCB2732_Raincliff11800 | DistributionFeederCB2732_Raincliff11800 | 15.242 | 800 | 800 | CB2732 | F234 SW.ST | ABS-F267 | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_Raincliff70 mm² Cu11- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 3 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 11 | 328 | 6.2492 | - | - | 247 | 4.706 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.11 | - | - | - | - | - | - | - | - | - | - | - | 6.2492 | - | 4.706 | - | - | - | - | - | - | CB2732_Raincliff4.70598204416464 | DistributionFeederCB2732_Raincliff11247 | DistributionFeederCB2732_Raincliff11247 | 4.706 | 247 | 247 | CB2732 | F234 SW.ST | OH Line-70 mm² Cu | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_RaincliffDOG11- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 344 | 6.5541 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6443.9 | - | - | - | - | - | - | - | - | - | - | - | 6.5541 | - | 4.8938 | - | - | - | - | - | - | CB2732_Raincliff4.89381213609487 | DistributionFeederCB2732_Raincliff11256.858523103439 | DistributionFeederCB2732_Raincliff11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | CB2732 | F234 SW.ST | OH Line-DOG | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_RaincliffF41311- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 5 | GEMA | F413 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB2732_Raincliff7.62102355330306 | DistributionFeederCB2732_Raincliff11400 | DistributionFeederCB2732_Raincliff11400 | 7.621 | 400 | 400 | CB2732 | F234 SW.ST | ABS-F413 | 11
DistributionFeederCB2732_Raincliff11 | DistributionFeederCB2732_Raincliff19/14 Cu11- | DistributionFeeder | CB2732_Raincliff | CB2732 | F234 SW.ST | 6 | GEMA/AEL OH Amp Calc. | 19/14 Cu | OH Line | - | - | 11 | 321 | 6.1159 | - | - | 241.6125 | 4.6033 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 48.3 | - | - | - | - | - | - | - | - | - | - | - | 6.1159 | - | 4.6033 | - | - | - | - | - | - | CB2732_Raincliff4.60333561089353 | DistributionFeederCB2732_Raincliff11241.612459465415 | DistributionFeederCB2732_Raincliff11241.612459465415 | 4.6033 | 241.6125 | 241.6125 | CB2732 | F234 SW.ST | OH Line-19/14 Cu | 11
DistributionFeederCB2742_Cave11 | DistributionFeederCB2742_Cave3-1c 400 mm² Al XLPE11- | DistributionFeeder | CB2742_Cave | CB2742 | Pole 53272 | 1 | GEMA/Drawing 12297 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 34.8 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 3 | 0.8 | 0.85 | 442.7565 | 8.4356 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.4356 | CB2742_Cave8.43564428719507 | DistributionFeederCB2742_Cave11442.7565 | DistributionFeederCB2742_Cave11442.7565 | 8.4356 | 442.7565 | 442.7565 | CB2742 | Pole 53272 | Cable-3-1c 400 mm² Al XLPE | 11
DistributionFeederCB2742_Cave11 | DistributionFeederCB2742_CaveF24911- | DistributionFeeder | CB2742_Cave | CB2742 | Pole 53272 | 2 | GEMA | F249 | ABS | - | - | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | - | - | - | - | CB2742_Cave15.2420471066061 | DistributionFeederCB2742_Cave11800 | DistributionFeederCB2742_Cave11800 | 15.242 | 800 | 800 | CB2742 | Pole 53272 | ABS-F249 | 11
DistributionFeederCB2742_Cave11 | DistributionFeederCB2742_CaveDOG11- | DistributionFeeder | CB2742_Cave | CB2742 | Pole 53272 | 3 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 344 | 6.5541 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.1 | - | - | - | - | - | - | - | - | - | - | - | 6.5541 | - | 4.8938 | - | - | - | - | - | - | CB2742_Cave4.89381213609487 | DistributionFeederCB2742_Cave11256.858523103439 | DistributionFeederCB2742_Cave11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | CB2742 | Pole 53272 | OH Line-DOG | 11
ZoneSubstationABY11 | ZoneSubstationABY3-1c 400 mm² Al XLPE11- | ZoneSubstation | ABY | CB2722 | F268 | 1 | GEMA/Drawing 12297 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 61.9 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 3 | 0.8 | 0.85 | 442.7565 | 8.4356 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.4356 | ABY8.43564428719507 | ZoneSubstationABY11442.7565 | ZoneSubstationABY11442.7565 | 8.4356 | 442.7565 | 442.7565 | CB2722 | F268 | Cable-3-1c 400 mm² Al XLPE | 11
ZoneSubstationABY11 | ZoneSubstationABYF26811- | ZoneSubstation | ABY | CB2722 | F268 | 2 | GEMA | F268 | ABS | - | - | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | - | - | - | - | ABY15.2420471066061 | ZoneSubstationABY11800 | ZoneSubstationABY11800 | 15.242 | 800 | 800 | CB2722 | F268 | ABS-F268 | 11
ZoneSubstationABY11 | ZoneSubstationABY120 mm² Cu11- | ZoneSubstation | ABY | F268 | C251 | 3 | GEMA/AEL OH Amp Calc. | 120 mm² Cu | OH Line | - | - | 11 | 486.3222 | 9.2657 | - | - | 363 | 6.9161 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.1 | - | - | - | - | - | - | - | - | - | - | - | 9.2657 | - | 6.9161 | - | - | - | - | - | - | ABY6.91607887462253 | ZoneSubstationABY11363 | ZoneSubstationABY11363 | 6.9161 | 363 | 363 | F268 | C251 | OH Line-120 mm² Cu | 11
ZoneSubstationABY11 | ZoneSubstationABYC25111LV Winding | ZoneSubstation | ABY | F268 | C251 | 4 | AEL Transformers Database | C251 | Transformer | - | LV Winding | 11 | 393.6 | 7.4991 | 393.6 | 7.4991 | 393.6 | 7.4991 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ABY | ZoneSubstationABY11 | ZoneSubstationABY11393.6 |  |  | 393.6 | F268 | C251 | Transformer-C251-LV Winding | 11
ZoneSubstationABY33 | ZoneSubstationABYC25133HV Winding | ZoneSubstation | ABY | F268 | C251 | 5 | AEL Transformers Database | C251 | Transformer | - | HV Winding | 33 | 131.2 | 7.4991 | 131.2 | 7.4991 | 131.2 | 7.4991 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ABY | ZoneSubstationABY33 | ZoneSubstationABY33131.2 |  |  | 131.2 | F268 | C251 | Transformer-C251-HV Winding | 33
ZoneSubstationABY33 | ZoneSubstationABYIODINE33- | ZoneSubstation | ABY | C251 | CB4242 | 6 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.1 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | ABY15.7404518297676 | ZoneSubstationABY33275.386487911596 | ZoneSubstationABY33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | C251 | CB4242 | OH Line-IODINE | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieABY-CB424233Protection | SubTransmission | CB2722_Fairlie | C251 | CB4242 | 7 | AEL Protection Database | ABY-CB4242 | Circuit Breaker | Relay SEL 311C | Protection | 33 | 368.604 | 21.0685 | 2000 | 114.3154 | 275.3865 | 15.7405 | - | - | - | - | 150 | 8.5737 | - | - | - | - | 500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | 114.3154 | 15.7405 | - | - | 8.5737 | - | 28.5788 | - | CB2722_Fairlie8.57365149746594 | SubTransmissionCB2722_Fairlie33150 | SubTransmissionCB2722_Fairlie33150 | 8.5737 | 150 | 150 | C251 | CB4242 | Circuit Breaker-ABY-CB4242-Protection | 33
ZoneSubstationABY33 | ZoneSubstationABYIODINE33- | ZoneSubstation | ABY | CB4242 | F388 | 8 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.6 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | ABY15.7404518297676 | ZoneSubstationABY33275.386487911596 | ZoneSubstationABY33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | CB4242 | F388 | OH Line-IODINE | 33
ZoneSubstationABY33 | ZoneSubstationABYCB424633- | ZoneSubstation | ABY | CB4242 | F388 | 9 | GEMA | CB4246 | ABS | - | - | 33 | 368.604 | 21.0685 | 800 | 45.7261 | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | 45.7261 | 15.7405 | - | - | - | - | - | - | ABY15.7404518297676 | ZoneSubstationABY33275.386487911596 | ZoneSubstationABY33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | CB4242 | F388 | ABS-CB4246 | 33
ZoneSubstationABY33 | ZoneSubstationABYIODINE33- | ZoneSubstation | ABY | CB4242 | F388 | 10 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 14 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | ABY15.7404518297676 | ZoneSubstationABY33275.386487911596 | ZoneSubstationABY33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | CB4242 | F388 | OH Line-IODINE | 33
ZoneSubstationABY33 | ZoneSubstationABY70 mm² Cu33- | ZoneSubstation | ABY | CB4242 | F388 | 11 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.5 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | ABY14.1179461324939 | ZoneSubstationABY33247 | ZoneSubstationABY33247 | 14.1179 | 247 | 247 | CB4242 | F388 | OH Line-70 mm² Cu | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieF38833- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 1 | - | F388 | ABS | - | - | 33 | - | - | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 14.1179 | - | - | - | - | - | - | CB2722_Fairlie14.1179461324939 | SubTransmissionCB2722_Fairlie33247 | SubTransmissionCB2722_Fairlie33247 | 14.1179 | 247 | 247 | F388 | OPU T-off | ABS-F388 | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_Fairlie70 mm² Cu33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 2 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 27.7 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | CB2722_Fairlie14.1179461324939 | SubTransmissionCB2722_Fairlie33247 | SubTransmissionCB2722_Fairlie33247 | 14.1179 | 247 | 247 | F388 | OPU T-off | OH Line-70 mm² Cu | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieDOG33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 3 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7241 | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | OH Line-DOG | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairliePETREL33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 4 | GEMA/AEL OH Amp Calc. | PETREL | OH Line | - | - | 33 | 230 | 13.1463 | - | - | 172.8371 | 9.879 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 520.9 | - | - | - | - | - | - | - | - | - | - | - | 13.1463 | - | 9.879 | - | - | - | - | - | - | CB2722_Fairlie9.87896668162793 | SubTransmissionCB2722_Fairlie33172.837093119795 | SubTransmissionCB2722_Fairlie33172.837093119795 | 9.879 | 172.8371 | 172.8371 | F388 | OPU T-off | OH Line-PETREL | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieDOG33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2714.4 | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | OH Line-DOG | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieF30533- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 6 | GEMA | F305 | ABS | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | ABS-F305 | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieDOG33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 7 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7585 | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | OH Line-DOG | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieF31733- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 8 | GEMA | F317 | ABS | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | ABS-F317 | 33
SubTransmissionCB2722_Fairlie33 | SubTransmissionCB2722_FairlieDOG33- | SubTransmission | CB2722_Fairlie | F388 | OPU T-off | 9 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 344 | 19.6622 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 174.1 | - | - | - | - | - | - | - | - | - | - | - | 19.6622 | - | 14.6814 | - | - | - | - | - | - | CB2722_Fairlie14.6814364082846 | SubTransmissionCB2722_Fairlie33256.858523103439 | SubTransmissionCB2722_Fairlie33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | F388 | OPU T-off | OH Line-DOG | 33
SubTransmissionOPU33 | SubTransmissionOPU70 mm² Cu33- | SubTransmission | OPU | OPU T-off | F328 | 1 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.2 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | OPU14.1179461324939 | SubTransmissionOPU33247 | SubTransmissionOPU33247 | 14.1179 | 247 | 247 | OPU T-off | F328 | OH Line-70 mm² Cu | 33
SubTransmissionOPU33 | SubTransmissionOPUF39933- | SubTransmission | OPU | OPU T-off | F328 | 2 | GEMA | F399 | Link | - | - | 33 | 328 | 18.7477 | 630 | 36.0093 | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | 36.0093 | 14.1179 | - | - | - | - | - | - | OPU14.1179461324939 | SubTransmissionOPU33247 | SubTransmissionOPU33247 | 14.1179 | 247 | 247 | OPU T-off | F328 | Link-F399 | 33
SubTransmissionOPU33 | SubTransmissionOPUOPU-F40033Protection | SubTransmission | OPU | OPU T-off | F328 | 3 | GEMA/AEL Protection Database | OPU-F400 | Recloser | Relay SEL 351R | Protection | 33 | 328 | 18.7477 | 630 | 36.0093 | 247 | 14.1179 | - | - | - | - | 150 | 8.5737 | - | - | - | - | 1000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | 36.0093 | 14.1179 | - | - | 8.5737 | - | 57.1577 | - | OPU8.57365149746594 | SubTransmissionOPU33150 | SubTransmissionOPU33150 | 8.5737 | 150 | 150 | OPU T-off | F328 | Recloser -OPU-F400-Protection | 33
SubTransmissionOPU33 | SubTransmissionOPUF39833- | SubTransmission | OPU | OPU T-off | F328 | 4 | GEMA | F398 | ABS | - | - | 33 | 328 | 18.7477 | 800 | 45.7261 | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | 45.7261 | 14.1179 | - | - | - | - | - | - | OPU14.1179461324939 | SubTransmissionOPU33247 | SubTransmissionOPU33247 | 14.1179 | 247 | 247 | OPU T-off | F328 | ABS-F398 | 33
SubTransmissionOPU33 | SubTransmissionOPUF40133- | SubTransmission | OPU | OPU T-off | F328 | 5 | GEMA | F401 | Link | - | - | 33 | 328 | 18.7477 | 630 | 36.0093 | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | 36.0093 | 14.1179 | - | - | - | - | - | - | OPU14.1179461324939 | SubTransmissionOPU33247 | SubTransmissionOPU33247 | 14.1179 | 247 | 247 | OPU T-off | F328 | Link-F401 | 33
SubTransmissionOPU33 | SubTransmissionOPU70 mm² Cu33- | SubTransmission | OPU | OPU T-off | F328 | 6 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.3 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | OPU14.1179461324939 | SubTransmissionOPU33247 | SubTransmissionOPU33247 | 14.1179 | 247 | 247 | OPU T-off | F328 | OH Line-70 mm² Cu | 33
SubTransmissionOPU33 | SubTransmissionOPU3-1c 300 mm² AL XLPE33- | SubTransmission | OPU | OPU T-off | F328 | 7 | GEMA/General Cables | 3-1c 300 mm² AL XLPE | Cable | - | - | 33 | 414 | 23.6633 | 414 | 23.6633 | 414 | 23.6633 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 96.7 | 1.1 | 0.965 | 15 | 1 | 2 | 0.86 | 1 | 0 | 1 | 343.5786 | 19.6382 | 23.6633 | 23.6633 | 23.6633 | - | - | - | - | - | 19.6382 | OPU19.6381545225817 | SubTransmissionOPU33343.5786 | SubTransmissionOPU33343.5786 | 19.6382 | 343.5786 | 343.5786 | OPU T-off | F328 | Cable-3-1c 300 mm² AL XLPE | 33
SubTransmissionOPU33 | SubTransmissionOPUJAGUAR33- | SubTransmission | OPU | OPU T-off | F328 | 8 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33 | 523 | 29.8935 | - | - | 386.9283 | 22.1159 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 29.8935 | - | 22.1159 | - | - | - | - | - | - | OPU22.1159210331553 | SubTransmissionOPU33386.92827157178 | SubTransmissionOPU33386.92827157178 | 22.1159 | 386.9283 | 386.9283 | OPU T-off | F328 | OH Line-JAGUAR | 33
SubTransmissionOPU33 | SubTransmissionOPUF32833- | SubTransmission | OPU | OPU T-off | F328 | 9 | GEMA/AEL OH Amp Calc. | F328 | ABS | - | - | 33 | - | - | - | - | 386.9283 | 22.1159 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.1159 | - | - | - | - | - | - | OPU22.1159210331553 | SubTransmissionOPU33386.92827157178 | SubTransmissionOPU33386.92827157178 | 22.1159 | 386.9283 | 386.9283 | OPU T-off | F328 | ABS-F328 | 33
ZoneSubstationOPU33 | ZoneSubstationOPUJAGUAR33- | ZoneSubstation | OPU | F328 | OPU Gen | 1 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33 | 523 | 29.8935 | - | - | 386.9283 | 22.1159 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18 | - | - | - | - | - | - | - | - | - | - | - | 29.8935 | - | 22.1159 | - | - | - | - | - | - | OPU22.1159210331553 | ZoneSubstationOPU33386.92827157178 | ZoneSubstationOPU33386.92827157178 | 22.1159 | 386.9283 | 386.9283 | F328 | OPU Gen | OH Line-JAGUAR | 33
ZoneSubstationOPU33 | ZoneSubstationOPUF32933- | ZoneSubstation | OPU | F328 | OPU Gen | 2 | - | F329 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OPU | ZoneSubstationOPU33 | ZoneSubstationOPU33 |  |  |  | F328 | OPU Gen | ABS-F329 | 33
ZoneSubstationOPU33 | ZoneSubstationOPUC40733HV Winding | ZoneSubstation | OPU | F328 | OPU Gen | 3 | AEL Transformers Database | C407 | Transformer | - | HV Winding | 33 | 160.9583 | 9.2 | 160.9583 | 9.2 | 160.9583 | 9.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OPU | ZoneSubstationOPU33 | ZoneSubstationOPU33160.958256864987 |  |  | 160.9583 | F328 | OPU Gen | Transformer-C407-HV Winding | 33
ZoneSubstationOPU6.6 | ZoneSubstationOPUC4076.6LV Winding | ZoneSubstation | OPU | F328 | OPU Gen | 4 | AEL Transformers Database | C407 | Transformer | - | LV Winding | 6.6 | 804.7913 | 9.2 | 804.7913 | 9.2 | 804.7913 | 9.2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OPU | ZoneSubstationOPU6.6 | ZoneSubstationOPU6.6804.791284324933 |  |  | 804.7913 | F328 | OPU Gen | Transformer-C407-LV Winding | 6.6
ZoneSubstationFLE33 | ZoneSubstationFLE70 mm² Cu33- | ZoneSubstation | FLE | OPU T-off | F377 | 1 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.3 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | FLE14.1179461324939 | ZoneSubstationFLE33247 | ZoneSubstationFLE33247 | 14.1179 | 247 | 247 | OPU T-off | F377 | OH Line-70 mm² Cu | 33
ZoneSubstationFLE33 | ZoneSubstationFLEF38533- | ZoneSubstation | FLE | OPU T-off | F377 | 2 | - | F385 | ABS | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | FLE14.1179461324939 | ZoneSubstationFLE33247 | ZoneSubstationFLE33247 | 14.1179 | 247 | 247 | OPU T-off | F377 | ABS-F385 | 33
ZoneSubstationFLE33 | ZoneSubstationFLE70 mm² Cu33- | ZoneSubstation | FLE | OPU T-off | F377 | 3 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 33 | 328 | 18.7477 | - | - | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1 | - | - | - | - | - | - | - | - | - | - | - | 18.7477 | - | 14.1179 | - | - | - | - | - | - | FLE14.1179461324939 | ZoneSubstationFLE33247 | ZoneSubstationFLE33247 | 14.1179 | 247 | 247 | OPU T-off | F377 | OH Line-70 mm² Cu | 33
ZoneSubstationFLE33 | ZoneSubstationFLEF30733- | ZoneSubstation | FLE | OPU T-off | F377 | 4 | - | F307 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | FLE | ZoneSubstationFLE33 | ZoneSubstationFLE33 |  |  |  | OPU T-off | F377 | ABS-F307 | 33
ZoneSubstationFLE33 | ZoneSubstationFLEFLE-F32333Protection | ZoneSubstation | FLE | OPU T-off | F377 | 5 | AEL Protection Database | FLE-F323 | Circuit Breaker | Relay SEL 351S | Protection | 33 | 560 | 32.0083 | 560 | 32.0083 | 560 | 32.0083 | - | - | - | - | 100 | 5.7158 | - | - | - | - | 500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.0083 | 32.0083 | 32.0083 | - | - | 5.7158 | - | 28.5788 | - | FLE5.7157676649773 | ZoneSubstationFLE33100 | ZoneSubstationFLE33100 | 5.7158 | 100 | 100 | OPU T-off | F377 | Circuit Breaker-FLE-F323-Protection | 33
ZoneSubstationFLE33 | ZoneSubstationFLEC133HV Winding | ZoneSubstation | FLE | OPU T-off | F377 | 6 | AEL Transformers Database | C1 | Transformer | - | HV Winding | 33 | 109.3466 | 6.25 | 109.3466 | 6.25 | 109.3466 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | FLE | ZoneSubstationFLE33 | ZoneSubstationFLE33109.346641891975 |  |  | 109.3466 | OPU T-off | F377 | Transformer-C1-HV Winding | 33
ZoneSubstationFLE11.1001 | ZoneSubstationFLEC111.1001LV Winding | ZoneSubstation | FLE | OPU T-off | F377 | 7 | AEL Transformers Database | C1 | Transformer | - | LV Winding | 11.1001 | 325.0817 | 6.25 | 325.0817 | 6.25 | 325.0817 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | FLE | ZoneSubstationFLE11.1001 | ZoneSubstationFLE11.1001325.08168236639 |  |  | 325.0817 | OPU T-off | F377 | Transformer-C1-LV Winding | 11.1001
ZoneSubstationFLE11.1001 | ZoneSubstationFLEIODINE11.1001- | ZoneSubstation | FLE | OPU T-off | F377 | 8 | Drawing 13250/AEL OH Amp Calc. | IODINE | OH Line | - | - | 11.1001 | 368.604 | 7.0868 | - | - | 390 | 7.4981 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5 | - | - | - | - | - | - | - | - | - | - | - | 7.0868 | - | 7.4981 | - | - | - | - | - | - | FLE7.08675688902055 | ZoneSubstationFLE11.1001368.603976320704 | ZoneSubstationFLE11.1001368.603976320704 | 7.0868 | 368.604 | 368.604 | OPU T-off | F377 | OH Line-IODINE | 11.1001
ZoneSubstationFLE11.1001 | ZoneSubstationFLEFX3811.1001- | ZoneSubstation | FLE | OPU T-off | F377 | 9 | GEMA | FX38 | ABS | - | - | 11.1001 | 600 | 11.5356 | 600 | 11.5356 | 600 | 11.5356 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.5356 | 11.5356 | 11.5356 | - | - | - | - | - | - | FLE11.5355623014572 | ZoneSubstationFLE11.1001600 | ZoneSubstationFLE11.1001600 | 11.5356 | 600 | 600 | OPU T-off | F377 | ABS-FX38 | 11.1001
ZoneSubstationFLE11.1001 | ZoneSubstationFLE3-1c 300 mm² AL XLPE11.1001- | ZoneSubstation | FLE | OPU T-off | F377 | 10 | GEMA/General Cables | 3-1c 300 mm² AL XLPE | Cable | - | - | 11.1001 | 414 | 7.9595 | 414 | 7.9595 | 414 | 7.9595 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 18.4 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 405.72 | 7.8003 | 7.9595 | 7.9595 | 7.9595 | - | - | - | - | - | 7.8003 | FLE7.80034722824534 | ZoneSubstationFLE11.1001405.72 | ZoneSubstationFLE11.1001405.72 | 7.8003 | 405.72 | 405.72 | OPU T-off | F377 | Cable-3-1c 300 mm² AL XLPE | 11.1001
ZoneSubstationFLE11.1001 | ZoneSubstationFLEFLE-F37711.1001Protection | ZoneSubstation | FLE | OPU T-off | F377 | 11 | AEL Protection Database | FLE-F377 | Circuit Breaker | Relay SEL 751A | Protection | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | 280 | 5.3833 | - | - | - | - | 400 | 7.6904 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | 5.3833 | - | 7.6904 | - | FLE5.38326240734668 | ZoneSubstationFLE11.1001280 | ZoneSubstationFLE11.1001280 | 5.3833 | 280 | 280 | OPU T-off | F377 | Circuit Breaker-FLE-F377-Protection | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_CricklewoodFLE-F37611.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 1 | AEL Protection Database | FLE-F376 | Circuit Breaker | - | - | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | - | - | - | - | F374_Cricklewood12.11234041653 | DistributionFeederF374_Cricklewood11.1001630 | DistributionFeederF374_Cricklewood11.1001630 | 12.1123 | 630 | 630 | F377 | Pole 11915 | Circuit Breaker-FLE-F376 | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_Cricklewood3-1c 300 mm² AL XLPE11.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 2 | GEMA/General Cables | 3-1c 300 mm² AL XLPE | Cable | - | - | 11.1001 | 466 | 8.9593 | 466 | 8.9593 | 466 | 8.9593 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 2 | 0 | 1 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 466 | 8.9593 | 8.9593 | 8.9593 | 8.9593 | - | - | - | - | - | 8.9593 | F374_Cricklewood8.95928672079841 | DistributionFeederF374_Cricklewood11.1001466 | DistributionFeederF374_Cricklewood11.1001466 | 8.9593 | 466 | 466 | F377 | Pole 11915 | Cable-3-1c 300 mm² AL XLPE | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_CricklewoodFLE-F37511.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 3 | AEL Protection Database | FLE-F375 | Circuit Breaker | - | - | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | - | - | - | - | F374_Cricklewood12.11234041653 | DistributionFeederF374_Cricklewood11.1001630 | DistributionFeederF374_Cricklewood11.1001630 | 12.1123 | 630 | 630 | F377 | Pole 11915 | Circuit Breaker-FLE-F375 | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_CricklewoodFLE-F37411.1001Protection | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 4 | AEL Protection Database | FLE-F374 | Circuit Breaker | Relay SEL 751A | Protection | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | 192 | 3.6914 | - | - | - | - | 400 | 7.6904 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | 3.6914 | - | 7.6904 | - | F374_Cricklewood3.6913799364663 | DistributionFeederF374_Cricklewood11.1001192 | DistributionFeederF374_Cricklewood11.1001192 | 3.6914 | 192 | 192 | F377 | Pole 11915 | Circuit Breaker-FLE-F374-Protection | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_Cricklewood3-1c 185 mm² AL XLPE11.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 5 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11.1001 | 362 | 6.9598 | 362 | 6.9598 | 362 | 6.9598 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 41.7 | 0.9 | 0.99 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 358.38 | 6.8902 | 6.9598 | 6.9598 | 6.9598 | - | - | - | - | - | 6.8902 | F374_Cricklewood6.89019136266037 | DistributionFeederF374_Cricklewood11.1001358.38 | DistributionFeederF374_Cricklewood11.1001358.38 | 6.8902 | 358.38 | 358.38 | F377 | Pole 11915 | Cable-3-1c 185 mm² AL XLPE | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_CricklewoodF31111.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 6 | - | F311 | Link | - | - | 11.1001 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | F374_Cricklewood | DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_Cricklewood11.1001 |  |  |  | F377 | Pole 11915 | Link-F311 | 11.1001
DistributionFeederF374_Cricklewood11.1001 | DistributionFeederF374_CricklewoodMINK11.1001- | DistributionFeeder | F374_Cricklewood | F377 | Pole 11915 | 7 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11.1001 | 251 | 4.8257 | - | - | 188.6266 | 3.6265 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 174.1 | - | - | - | - | - | - | - | - | - | - | - | 4.8257 | - | 3.6265 | - | - | - | - | - | - | F374_Cricklewood3.62652329883412 | DistributionFeederF374_Cricklewood11.1001188.626607220145 | DistributionFeederF374_Cricklewood11.1001188.626607220145 | 3.6265 | 188.6266 | 188.6266 | F377 | Pole 11915 | OH Line-MINK | 11.1001
DistributionFeederF380_Fairlie Rural11.1001 | DistributionFeederF380_Fairlie RuralFLE-F38011.1001Protection | DistributionFeeder | F380_Fairlie Rural | F380 | Pole 15164 | 1 | AEL Protection Database | FLE-F380 | Circuit Breaker | Relay SEL 751A | Protection | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | 192 | 3.6914 | - | - | - | - | 400 | 7.6904 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | 3.6914 | - | 7.6904 | - | F380_Fairlie Rural3.6913799364663 | DistributionFeederF380_Fairlie Rural11.1001192 | DistributionFeederF380_Fairlie Rural11.1001192 | 3.6914 | 192 | 192 | F380 | Pole 15164 | Circuit Breaker-FLE-F380-Protection | 11.1001
DistributionFeederF380_Fairlie Rural11.1001 | DistributionFeederF380_Fairlie Rural3-1c 185 mm² AL XLPE11.1001- | DistributionFeeder | F380_Fairlie Rural | F380 | Pole 15164 | 2 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11.1001 | 362 | 6.9598 | 362 | 6.9598 | 362 | 6.9598 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 15.8 | 1.25 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.45 | 0.8 | 278.016 | 5.3451 | 6.9598 | 6.9598 | 6.9598 | - | - | - | - | - | 5.3451 | F380_Fairlie Rural5.3451181480032 | DistributionFeederF380_Fairlie Rural11.1001278.016 | DistributionFeederF380_Fairlie Rural11.1001278.016 | 5.3451 | 278.016 | 278.016 | F380 | Pole 15164 | Cable-3-1c 185 mm² AL XLPE | 11.1001
DistributionFeederF380_Fairlie Rural11.1001 | DistributionFeederF380_Fairlie RuralF32211.1001- | DistributionFeeder | F380_Fairlie Rural | F380 | Pole 15164 | 3 | - | F322 | ABS | - | - | 11.1001 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | F380_Fairlie Rural | DistributionFeederF380_Fairlie Rural11.1001 | DistributionFeederF380_Fairlie Rural11.1001 |  |  |  | F380 | Pole 15164 | ABS-F322 | 11.1001
DistributionFeederF380_Fairlie Rural11.1001 | DistributionFeederF380_Fairlie Rural70 mm² Cu11.1001- | DistributionFeeder | F380_Fairlie Rural | F380 | Pole 15164 | 4 | GEMA/AEL OH Amp Calc. | 70 mm² Cu | OH Line | - | - | 11.1001 | 328 | 6.3061 | - | - | 247 | 4.7488 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 27.2 | - | - | - | - | - | - | - | - | - | - | - | 6.3061 | - | 4.7488 | - | - | - | - | - | - | F380_Fairlie Rural4.74880648076654 | DistributionFeederF380_Fairlie Rural11.1001247 | DistributionFeederF380_Fairlie Rural11.1001247 | 4.7488 | 247 | 247 | F380 | Pole 15164 | OH Line-70 mm² Cu | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie TownshipFLE-F38311.1001Protection | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 1 | AEL Protection Database | FLE-F383 | Circuit Breaker | Relay SEL 751A | Protection | 11.1001 | 630 | 12.1123 | 630 | 12.1123 | 630 | 12.1123 | - | - | - | - | 192 | 3.6914 | - | - | - | - | 400 | 7.6904 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.1123 | 12.1123 | 12.1123 | - | - | 3.6914 | - | 7.6904 | - | F383_Fairlie Township3.6913799364663 | DistributionFeederF383_Fairlie Township11.1001192 | DistributionFeederF383_Fairlie Township11.1001192 | 3.6914 | 192 | 192 | F383 | Pole 15305 | Circuit Breaker-FLE-F383-Protection | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie Township3-1c 185 mm² AL XLPE11.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 2 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11.1001 | 362 | 6.9598 | 362 | 6.9598 | 362 | 6.9598 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 67.5 | 1.25 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.45 | 0.8 | 278.016 | 5.3451 | 6.9598 | 6.9598 | 6.9598 | - | - | - | - | - | 5.3451 | F383_Fairlie Township5.3451181480032 | DistributionFeederF383_Fairlie Township11.1001278.016 | DistributionFeederF383_Fairlie Township11.1001278.016 | 5.3451 | 278.016 | 278.016 | F383 | Pole 15305 | Cable-3-1c 185 mm² AL XLPE | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie TownshipF37011.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 3 | GEMA | F370 | ABS | - | - | 11.1001 | 300 | 5.7678 | 300 | 5.7678 | 300 | 5.7678 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7678 | 5.7678 | 5.7678 | - | - | - | - | - | - | F383_Fairlie Township5.76778115072859 | DistributionFeederF383_Fairlie Township11.1001300 | DistributionFeederF383_Fairlie Township11.1001300 | 5.7678 | 300 | 300 | F383 | Pole 15305 | ABS-F370 | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie Township19/14 Cu11.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 4 | GEMA/AEL OH Amp Calc. | 19/14 Cu | OH Line | - | - | 11.1001 | 321 | 6.1715 | - | - | 241.6125 | 4.6452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 14.67 | - | - | - | - | - | - | - | - | - | - | - | 6.1715 | - | 4.6452 | - | - | - | - | - | - | F383_Fairlie Township4.64522596495266 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | 4.6452 | 241.6125 | 241.6125 | F383 | Pole 15305 | OH Line-19/14 Cu | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie TownshipF26311.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 5 | - | F263 | ABS | - | - | 11.1001 | 600 | 11.5356 | - | - | 241.6125 | 4.6452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.5356 | - | 4.6452 | - | - | - | - | - | - | F383_Fairlie Township4.64522596495266 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | 4.6452 | 241.6125 | 241.6125 | F383 | Pole 15305 | ABS-F263 | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie Township19/14 Cu11.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 6 | GEMA/AEL OH Amp Calc. | 19/14 Cu | OH Line | - | - | 11.1001 | 321 | 6.1715 | - | - | 241.6125 | 4.6452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 411.7 | - | - | - | - | - | - | - | - | - | - | - | 6.1715 | - | 4.6452 | - | - | - | - | - | - | F383_Fairlie Township4.64522596495266 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | DistributionFeederF383_Fairlie Township11.1001241.612459465415 | 4.6452 | 241.6125 | 241.6125 | F383 | Pole 15305 | OH Line-19/14 Cu | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie Township1-3c 95 mm² AL PILC11.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 7 | GEMA/General Cables | 1-3c 95 mm² AL PILC | Cable | - | - | 11.1001 | 205 | 3.9413 | 205 | 3.9413 | 205 | 3.9413 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 292.4 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.15 | 0.85 | 170.765 | 3.2831 | 3.9413 | 3.9413 | 3.9413 | - | - | - | - | - | 3.2831 | F383_Fairlie Township3.28311716068056 | DistributionFeederF383_Fairlie Township11.1001170.765 | DistributionFeederF383_Fairlie Township11.1001170.765 | 3.2831 | 170.765 | 170.765 | F383 | Pole 15305 | Cable-1-3c 95 mm² AL PILC | 11.1001
DistributionFeederF383_Fairlie Township11.1001 | DistributionFeederF383_Fairlie Township7/10 Cu11.1001- | DistributionFeeder | F383_Fairlie Township | F383 | Pole 15305 | 8 | GEMA/AEL OH Amp Calc. | 7/10 Cu | OH Line | - | - | 11.1001 | 285 | 5.4794 | - | - | 214.9397 | 4.1324 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 146 | - | - | - | - | - | - | - | - | - | - | - | 5.4794 | - | 4.1324 | - | - | - | - | - | - | F383_Fairlie Township4.13241694934207 | DistributionFeederF383_Fairlie Township11.1001214.939688661041 | DistributionFeederF383_Fairlie Township11.1001214.939688661041 | 4.1324 | 214.9397 | 214.9397 | F383 | Pole 15305 | OH Line-7/10 Cu | 11.1001
[13 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 9.879 |  |  | 8.5737 | 17.1473 | 11.4315 |  | - | - |  | 8.5737 | - |  | - | - | - | -
Note on N29: Author: Based on 50°C design
Note on R29: Author: Based on 50°C design
Note on N30: Author: Based on 50°C design
Note on R30: Author: Based on 50°C design
Note on R31: Author: Based on 50°C design
Note on N32: Author: Based on 50°C design
Note on R32: Author: Based on 50°C design
Note on R33: Author: Based on 50°C design
Note on R34: Author: Based on 50°C design
Note on N35: Author: Based on 50°C design
Note on R35: Author: Based on 50°C design
Note on N38: Author: Based on 50°C design
Note on R38: Author: Based on 50°C design
Note on N41: Author: Based on 50°C design
Note on R41: Author: Based on 50°C design
Note on N43: Author: Based on 50°C design
Note on R43: Author: Based on 50°C design
Note on N45: Author: Based on 50°C design
Note on R45: Author: Based on 50°C design
Note on N46: Author: Based on 50°C design
Note on R46: Author: Based on 50°C design
Note on N48: Author: Based on 50°C design
Note on R48: Author: Based on 50°C design
Note on N49: Author: Based on 50°C design
Note on R49: Author: Based on 50°C design
Note on I50: Author: Rating obtained by using rating from drawijng 782 of 200 A and scaling it similar to DOG
Note on N50: Author: Based on 50°C design
Note on R50: Author: Based on 50°C design
Note on N51: Author: Based on 50°C design
Note on R51: Author: Based on 50°C design
Note on N53: Author: Based on 50°C design
Note on R53: Author: Based on 50°C design
Note on N55: Author: Based on 50°C design
Note on R55: Author: Based on 50°C design
Note on N56: Author: Based on 50°C design
Note on R56: Author: Based on 50°C design
Note on N61: Author: Based on 50°C design
Note on R61: Author: Based on 50°C design
Note on AM62: Author: Bedded in river sand or inside 150 mm Duct
Note on N63: Author: Based on 50°C design
Note on R63: Author: Based on 50°C design
Note on N64: Author: Based on 50°C design
Note on R64: Author: Based on 50°C design
Note on N65: Author: Based on 50°C design
Note on R65: Author: Based on 50°C design
Note on N69: Author: Based on 50°C design
Note on R69: Author: Based on 50°C design
Note on N71: Author: Based on 50°C design
Note on R71: Author: Based on 50°C design
Note on N76: Author: Based on 50°C design
Note on R76: Author: Based on 50°C design
Note on AG81: Author: In covered enclosed conduit
Note on AI81: Author: In covered enclosed conduit
Note on N86: Author: Based on 50°C design
Note on R86: Author: Based on 50°C design
Note on N90: Author: Based on 50°C design
Note on R90: Author: Based on 50°C design
Note on N94: Author: Based on 50°C design
Note on R94: Author: Based on 50°C design
Note on N96: Author: Based on 50°C design
Note on R96: Author: Based on 50°C design
Note on N98: Author: Based on 50°C design
Note on R98: Author: Based on 50°C design

## BPD_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of Data | ID | Type | Device ID | Device Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal Resistivity |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | - | - | - | - | - |  | - | - | - | - | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | (A) | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPBPD_GXP110 | GXPBPD_GXPBPD-T2-CB482110Other Equipment | GXP | BPD_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report BDT.BPD.2 | BPD-T2-CB482 | Current Transformer | BPD-CT-CT482 | Other Equipment | 110 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 34.2946 | 34.2946 | 34.2946 | 34.2946 | 34.2946 | 34.2946 | - | - | - | BPD_GXP34.2946059898638 | GXPBPD_GXP110180 | GXPBPD_GXP110180 | 34.2946 | 180 | 180 | 110 kV Bus | 11 kV Bus | Current Transformer-BPD-T2-CB482-Other Equipment | 110
GXPBPD_GXP110 | GXPBPD_GXPDS446110Disconnector | GXP | BPD_GXP | 110 kV Bus | DS446 | 2 | TP Branch Report BPD.DS.446 | DS446 | Disconnector | BPD-DS-446 | Disconnector | 110 | 630 | 120.0311 | 630 | 120.0311 | 630 | 120.0311 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120.0311 | 120.0311 | 120.0311 | - | - | - | - | - | - | BPD_GXP120.031120964523 | GXPBPD_GXP110630 | GXPBPD_GXP110630 | 120.0311 | 630 | 630 | 110 kV Bus | DS446 | Disconnector-DS446-Disconnector | 110
GXPBPD_GXP110 | GXPBPD_GXPDS486110Disconnector | GXP | BPD_GXP | 110 kV Bus | DS486 | 3 | TP Branch Report BPD.DS.486 | DS486 | Disconnector | BPD-DS-486 | Disconnector | 110 | 630 | 120.0311 | 630 | 120.0311 | 630 | 120.0311 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120.0311 | 120.0311 | 120.0311 | - | - | - | - | - | - | BPD_GXP120.031120964523 | GXPBPD_GXP110630 | GXPBPD_GXP110630 | 120.0311 | 630 | 630 | 110 kV Bus | DS486 | Disconnector-DS486-Disconnector | 110
GXPBPD_GXP110 | GXPBPD_GXPWOLF110- | GXP | BPD_GXP | 110 kV Bus | BPD T-off | 4 | TP Branch Report BDT.BPD.2 | WOLF | OH Line | - | - | 110 | 422 | 80.4018 | 386 | 73.5429 | 345 | 65.7313 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 80.4018 | 73.5429 | 65.7313 | - | - | - | - | - | - | BPD_GXP65.7313281472389 | GXPBPD_GXP110345 | GXPBPD_GXP110345 | 65.7313 | 345 | 345 | 110 kV Bus | BPD T-off | OH Line-WOLF | 110
GXPBPD_GXP110 | GXPBPD_GXPBPD-T1-CB442110Other Equipment | GXP | BPD_GXP | 110 kV Bus | DS446 | 5 | TP Branch Report BPD.DS.446 | BPD-T1-CB442 | Current Transformer | BPD-CT-442-OEL | Other Equipment | 110 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | 45.7261 | 45.7261 | - | - | - | - | BPD_GXP45.7261413198184 | GXPBPD_GXP110240 | GXPBPD_GXP110240 | 45.7261 | 240 | 240 | 110 kV Bus | DS446 | Current Transformer-BPD-T1-CB442-Other Equipment | 110
GXPBPD_GXP110 | GXPBPD_GXPBPD-T1-CB442110Protection | GXP | BPD_GXP | 110 kV Bus | DS446 | 1 | TP Branch Report BPD.DS.446\GEMA | BPD-T1-CB442 | Circuit Breaker | Relay SEL 351S | Protection | 110 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | - | - | - | - | 292 | 55.6335 | 219 | 41.7251 | 600 | 114.3154 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | 600.1556 | 600.1556 | - | - | 55.6335 | 114.3154 | 45.7261 | - | BPD_GXP45.7261413198184 | GXPBPD_GXP110240 | GXPBPD_GXP110219 | 45.7261 | 240 | 219 | 110 kV Bus | DS446 | Circuit Breaker-BPD-T1-CB442-Protection | 110
GXPBPD_GXP110 | GXPBPD_GXPBPD-T2-CB482110Protection | GXP | BPD_GXP | 110 kV Bus | DS486 | 3 | TP Branch Report BPD.DS.486\GEMA | BPD-T2-CB482 | Circuit Breaker | Relay SEL 351S | Protection | 110 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | - | - | - | - | 146 | 27.8167 | 110 | 20.9578 | 600 | 114.3154 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | 600.1556 | 600.1556 | - | - | 27.8167 | 114.3154 | 45.7261 | - | BPD_GXP27.8167359695562 | GXPBPD_GXP110146 | GXPBPD_GXP110110 | 27.8167 | 146 | 110 | 110 kV Bus | DS486 | Circuit Breaker-BPD-T2-CB482-Protection | 110
ZoneSubstationBPD110T2 | ZoneSubstationBPDBPD-T2-CB482110Other Equipment | ZoneSubstation | BPD | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report BDT.BPD.2 | BPD-T2-CB482 | Current Transformer | BPD-CT-CT482 | Other Equipment | 110 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | 180 | 34.2946 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 34.2946 | 34.2946 | 34.2946 | 34.2946 | 34.2946 | 34.2946 | - | - | - | BPD34.2946059898638 | ZoneSubstationBPD110180 | ZoneSubstationBPD110180 | 34.2946 | 180 | 180 | 110 kV Bus | 11 kV Bus | Current Transformer-BPD-T2-CB482-Other Equipment | 110
ZoneSubstationBPD110T1 | ZoneSubstationBPDDS446110Disconnector | ZoneSubstation | BPD | 110 kV Bus | DS446 | 2 | TP Branch Report BPD.DS.446 | DS446 | Disconnector | BPD-DS-446 | Disconnector | 110 | 630 | 120.0311 | 630 | 120.0311 | 630 | 120.0311 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120.0311 | 120.0311 | 120.0311 | - | - | - | - | - | - | BPD120.031120964523 | ZoneSubstationBPD110630 | ZoneSubstationBPD110630 | 120.0311 | 630 | 630 | 110 kV Bus | DS446 | Disconnector-DS446-Disconnector | 110
ZoneSubstationBPD110T2 | ZoneSubstationBPDDS486110Disconnector | ZoneSubstation | BPD | 110 kV Bus | DS486 | 3 | TP Branch Report BPD.DS.486 | DS486 | Disconnector | BPD-DS-486 | Disconnector | 110 | 630 | 120.0311 | 630 | 120.0311 | 630 | 120.0311 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120.0311 | 120.0311 | 120.0311 | - | - | - | - | - | - | BPD120.031120964523 | ZoneSubstationBPD110630 | ZoneSubstationBPD110630 | 120.0311 | 630 | 630 | 110 kV Bus | DS486 | Disconnector-DS486-Disconnector | 110
ZoneSubstationBPD110T2 | ZoneSubstationBPDWOLF110- | ZoneSubstation | BPD | 110 kV Bus | BPD T-off | 4 | TP Branch Report BDT.BPD.2 | WOLF | OH Line | - | - | 110 | 422 | 80.4018 | 386 | 73.5429 | 345 | 65.7313 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 80.4018 | 73.5429 | 65.7313 | - | - | - | - | - | - | BPD65.7313281472389 | ZoneSubstationBPD110345 | ZoneSubstationBPD110345 | 65.7313 | 345 | 345 | 110 kV Bus | BPD T-off | OH Line-WOLF | 110
ZoneSubstationBPD110T1 | ZoneSubstationBPDBPD-T1-CB442110Other Equipment | ZoneSubstation | BPD | 110 kV Bus | DS446 | 5 | TP Branch Report BPD.DS.446 | BPD-T1-CB442 | Current Transformer | BPD-CT-442-OEL | Other Equipment | 110 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | 45.7261 | 45.7261 | - | - | - | - | BPD45.7261413198184 | ZoneSubstationBPD110240 | ZoneSubstationBPD110240 | 45.7261 | 240 | 240 | 110 kV Bus | DS446 | Current Transformer-BPD-T1-CB442-Other Equipment | 110
ZoneSubstationBPD110T1 | ZoneSubstationBPDBPD-T1-CB442110Protection | ZoneSubstation | BPD | 110 kV Bus | DS446 | 1 | TP Branch Report BPD.DS.446\GEMA | BPD-T1-CB442 | Circuit Breaker | Relay SEL 351S | Protection | 110 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | - | - | - | - | 292 | 55.6335 | 219 | 41.7251 | 600 | 114.3154 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | 600.1556 | 600.1556 | - | - | 55.6335 | 114.3154 | 45.7261 | - | BPD45.7261413198184 | ZoneSubstationBPD110240 | ZoneSubstationBPD110219 | 45.7261 | 240 | 219 | 110 kV Bus | DS446 | Circuit Breaker-BPD-T1-CB442-Protection | 110
ZoneSubstationBPD110T2 | ZoneSubstationBPDBPD-T2-CB482110Protection | ZoneSubstation | BPD | 110 kV Bus | DS486 | 3 | TP Branch Report BPD.DS.486\GEMA | BPD-T2-CB482 | Circuit Breaker | Relay SEL 351S | Protection | 110 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | - | - | - | - | 146 | 27.8167 | 110 | 20.9578 | 600 | 114.3154 | 240 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | 600.1556 | 600.1556 | - | - | 27.8167 | 114.3154 | 45.7261 | - | BPD27.8167359695562 | ZoneSubstationBPD110146 | ZoneSubstationBPD110110 | 27.8167 | 146 | 110 | 110 kV Bus | DS486 | Circuit Breaker-BPD-T2-CB482-Protection | 110
ZoneSubstationBPD110T2 | ZoneSubstationBPDT2/A1067110HV Winding | ZoneSubstation | BPD | CB482 | 11 kV Bus | 5 | AEL Transformer database | T2/A1067 | Transformer | - | HV Winding | 110 | 104.9728 | 20 | 104.9728 | 20 | 104.9728 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD110 | ZoneSubstationBPD110104.972776216296 |  |  | 104.9728 | CB482 | 11 kV Bus | Transformer-T2/A1067-HV Winding | 110
ZoneSubstationBPD11.22T2 | ZoneSubstationBPDT2/A106711.22Secondary LV Winding | ZoneSubstation | BPD | CB482 | 11 kV Bus | 5 | AEL Transformer database | T2/A1067 | Transformer | - | Secondary LV Winding | 11.22 | 771.8586 | 15 | 771.8586 | 15 | 771.8586 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD11.22 | ZoneSubstationBPD11.22771.858648649232 |  |  | 771.8586 | CB482 | 11 kV Bus | Transformer-T2/A1067-Secondary LV Winding | 11.22
ZoneSubstationBPD33T2 | ZoneSubstationBPDT2/A106733Territary LV Winding | ZoneSubstation | BPD | CB482 | 11 kV Bus | 5 | AEL Transformer database | T2/A1067 | Transformer | - | Territary LV Winding | 33 | 262.4319 | 15 | 262.4319 | 15 | 262.4319 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD33 | ZoneSubstationBPD33262.431940540739 |  |  | 262.4319 | CB482 | 11 kV Bus | Transformer-T2/A1067-Territary LV Winding | 33
ZoneSubstationBPD110T1 | ZoneSubstationBPDT1/A1067110HV Winding | ZoneSubstation | BPD | CB442 | 11 kV Bus | 5 | AEL Transformer database | T1/A1067 | Transformer | - | HV Winding | 110 | 209.9456 | 40 | 209.9456 | 40 | 209.9456 | 40 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD110 | ZoneSubstationBPD110209.945552432591 |  |  | 209.9456 | CB442 | 11 kV Bus | Transformer-T1/A1067-HV Winding | 110
ZoneSubstationBPD11.22T1 | ZoneSubstationBPDT1/A106711.22Secondary LV Winding | ZoneSubstation | BPD | CB442 | 11 kV Bus | 5 | AEL Transformer database | T1/A1067 | Transformer | - | Secondary LV Winding | 11.22 | 1543.7173 | 30 | 1543.7173 | 30 | 1543.7173 | 30 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD11.22 | ZoneSubstationBPD11.221543.71729729846 |  |  | 1543.7173 | CB442 | 11 kV Bus | Transformer-T1/A1067-Secondary LV Winding | 11.22
ZoneSubstationBPD33T1 | ZoneSubstationBPDT1/A106733Territary LV Winding | ZoneSubstation | BPD | CB442 | 11 kV Bus | 5 | AEL Transformer database | T1/A1067 | Transformer | - | Territary LV Winding | 33 | 349.9093 | 20 | 349.9093 | 20 | 349.9093 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BPD | ZoneSubstationBPD33 | ZoneSubstationBPD33349.909254054319 |  |  | 349.9093 | CB442 | 11 kV Bus | Transformer-T1/A1067-Territary LV Winding | 33
ZoneSubstationBPD11.22T1 | ZoneSubstationBPDBPD-T1-CB3511.22Protection | ZoneSubstation | BPD | 110 kV Bus | 11 kV Bus | 6 | 860RP2045 Drawing\AEL Protection database | BPD-T1-CB35 | Circuit Breaker | Relay SEL 751A | Protection | 11.22 | 2500 | 48.584 | 2500 | 48.584 | 2500 | 48.584 | - | - | - | - | 2208 | 42.9094 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 48.584 | 48.584 | 48.584 | - | - | 42.9094 | - | - | - | BPD42.9094110145176 | ZoneSubstationBPD11.222208 | ZoneSubstationBPD11.222208 | 42.9094 | 2208 | 2208 | 110 kV Bus | 11 kV Bus | Circuit Breaker-BPD-T1-CB35-Protection | 11.22
ZoneSubstationBPD11.22T1 | ZoneSubstationBPD3-1c 1000mm2 Al XLPE MDPE11.22- | ZoneSubstation | BPD | 110 kV Bus | 11 kV Bus | 7 | 860RP2045 Drawing\AEL Protection database | 3-1c 1000mm2 Al XLPE MDPE | Cable | - | - | 11.22 | 2186 | 42.4819 | 2186 | 42.4819 | 2186 | 42.4819 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 42.4819 | 42.4819 | 42.4819 | - | - | - | - | - | - | BPD42.4818715931772 | ZoneSubstationBPD11.222186 | ZoneSubstationBPD11.222186 | 42.4819 | 2186 | 2186 | 110 kV Bus | 11 kV Bus | Cable-3-1c 1000mm2 Al XLPE MDPE | 11.22
ZoneSubstationBPD11.22T2 | ZoneSubstationBPDBPD-T2-CB3611.22Protection | ZoneSubstation | BPD | 110 kV Bus | 11 kV Bus | 6 | 860RP2045 Drawing\AEL Protection database | BPD-T2-CB36 | Circuit Breaker | Relay SEL 351S-7 | Protection | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 1100 | 21.377 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 21.377 | - | - | - | BPD21.3769710670151 | ZoneSubstationBPD11.221100 | ZoneSubstationBPD11.221100 | 21.377 | 1100 | 1100 | 110 kV Bus | 11 kV Bus | Circuit Breaker-BPD-T2-CB36-Protection | 11.22
ZoneSubstationBPD11.22T2 | ZoneSubstationBPD6 1c 400mm2 Al XLPE11.22- | ZoneSubstation | BPD | 110 kV Bus | 11 kV Bus | 7 | 860RP2045 Drawing\AEL Protection database | 6 1c 400mm2 Al XLPE | Cable | - | - | 11.22 | 900 | 17.4902 | 900 | 17.4902 | 900 | 17.4902 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 17.4902 | 17.4902 | 17.4902 | - | - | - | - | - | - | BPD17.4902490548305 | ZoneSubstationBPD11.22900 | ZoneSubstationBPD11.22900 | 17.4902 | 900 | 900 | 110 kV Bus | 11 kV Bus | Cable-6 1c 400mm2 Al XLPE | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsBPD-T2-CB1111.22Protection | DistributionFeeder | CB11_Waihao Downs | 11 kV Bus | BPD11 CB | 1 | AEL 15000\RPS 860RP1685\AEL Transformer database | BPD-T2-CB11 | Circuit Breaker | Relay SEL 351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 400 | 7.7734 | - | - | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 7.7734 | - | 7.7734 | - | CB11_Waihao Downs7.77344402436912 | DistributionFeederCB11_Waihao Downs11.22400 | DistributionFeederCB11_Waihao Downs11.22400 | 7.7734 | 400 | 400 | 11 kV Bus | BPD11 CB | Circuit Breaker-BPD-T2-CB11-Protection | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao Downs3-1c 400mm² AL XLPE11.22- | DistributionFeeder | CB11_Waihao Downs | BPD11 CB | Cable Joint | 3 | GEMA\AEL Drawing 12023 | 3-1c 400mm² AL XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 48.5 | 1.5 | 0.94 | 15 | 1 | 1.2 | 1 | 5 | 0.4 | 0.71 | 358.3938 | 6.9649 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 6.9649 | CB11_Waihao Downs6.96488535745235 | DistributionFeederCB11_Waihao Downs11.22358.3938 | DistributionFeederCB11_Waihao Downs11.22358.3938 | 6.9649 | 358.3938 | 358.3938 | BPD11 CB | Cable Joint | Cable-3-1c 400mm² AL XLPE | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao Downs3c 300mm² AL XLPE CWS MDPE11.22- | DistributionFeeder | CB11_Waihao Downs | Cable Joint | W630 ABS | 4 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE CWS MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 98.8 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB11_Waihao Downs7.63712890995778 | DistributionFeederCB11_Waihao Downs11.22392.9856 | DistributionFeederCB11_Waihao Downs11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | W630 ABS | Cable-3c 300mm² AL XLPE CWS MDPE | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsW63011.22- | DistributionFeeder | CB11_Waihao Downs | Cable 300 mm² | JAGUAR OH Line | 5 | GEMA | W630 | Air Break Switch | - | - | 11.22 | 600 | 11.6602 | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6602 | 11.6602 | 11.6602 | - | - | - | - | - | - | CB11_Waihao Downs11.6601660365537 | DistributionFeederCB11_Waihao Downs11.22600 | DistributionFeederCB11_Waihao Downs11.22600 | 11.6602 | 600 | 600 | Cable 300 mm² | JAGUAR OH Line | Air Break Switch - W630 | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsJAGUAR11.22- | DistributionFeeder | CB11_Waihao Downs | W630 ABS | W631 ABS | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3329.2 | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB11_Waihao Downs7.51941315127282 | DistributionFeederCB11_Waihao Downs11.22386.92827157178 | DistributionFeederCB11_Waihao Downs11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W630 ABS | W631 ABS | OH Line-JAGUAR | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsW63111.22- | DistributionFeeder | CB11_Waihao Downs | JAGUAR OH Line | JAGUAR OH Line | 7 | GEMA | W631 | Switch | - | - | 11.22 | 600 | 11.6602 | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6602 | 11.6602 | 11.6602 | - | - | - | - | - | - | CB11_Waihao Downs11.6601660365537 | DistributionFeederCB11_Waihao Downs11.22600 | DistributionFeederCB11_Waihao Downs11.22600 | 11.6602 | 600 | 600 | JAGUAR OH Line | JAGUAR OH Line | Switch - W631 | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsJAGUAR11.22- | DistributionFeeder | CB11_Waihao Downs | W631 ABS | W614 LK | 6 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB11_Waihao Downs7.51941315127282 | DistributionFeederCB11_Waihao Downs11.22386.92827157178 | DistributionFeederCB11_Waihao Downs11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W631 ABS | W614 LK | OH Line - JAGUAR | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao DownsW61411.22- | DistributionFeeder | CB11_Waihao Downs | JAGUAR OH Line | Cable 95 mm2 | 7 | GEMA | W614 | Link | - | - | 11.22 | 300 | 5.8301 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | 5.8301 | - | - | - | - | - | - | - | - | CB11_Waihao Downs5.83008301827684 | SubTransmissionCB1282_Clandeboye No.433.594600 | SubTransmissionCB1282_Clandeboye No.433.594600 | 5.8301 | 300 | 300 | JAGUAR OH Line | Cable 95 mm2 | Link - W614 | 11.22
DistributionFeederCB11_Waihao Downs11.22T2 | DistributionFeederCB11_Waihao Downs3c 95mm2 Al XLPE CWS HDPE11.22- | DistributionFeeder | CB11_Waihao Downs | W614 LK | W624 RMU | 8 | - | 3c 95mm2 Al XLPE CWS HDPE | Cable | - | - | 11.22 | 255 | 4.9556 | 255 | 4.9556 | 255 | 4.9556 | - | - | - | - | - | - | 255 | 4.9556 | - | - | - | - | - | - | - | 1 | 0.94 | 15 | 1 | 1.2 | 1 | 1 | 1 | 1 | 239.7 | 4.6582 | 4.9556 | 4.9556 | 4.9556 | - | - | - | - | - | 4.6582 | CB11_Waihao Downs4.6582363316032 | DistributionFeederCB11_Waihao Downs11.22239.7 | DistributionFeederCB11_Waihao Downs11.22239.7 | 4.6582 | 239.7 | 239.7 | W614 LK | W624 RMU | Cable - 3c 95mm2 Al XLPE CWS HDPE | 11.22
DistributionFeederCB12_Ikawai11.22T2 | DistributionFeederCB12_IkawaiBPD-T2-CB1211.22Protection | DistributionFeeder | CB12_Ikawai | 11 kV Bus | BPD12 CB | 1 | AEL 15000\RPS 860RP1685\AEL Transformer database | BPD-T2-CB12 | Circuit Breaker | Relay SEL 351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 400 | 7.7734 | - | - | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 7.7734 | - | 7.7734 | - | CB12_Ikawai7.77344402436912 | DistributionFeederCB12_Ikawai11.22400 | DistributionFeederCB12_Ikawai11.22400 | 7.7734 | 400 | 400 | 11 kV Bus | BPD12 CB | Circuit Breaker-BPD-T2-CB12-Protection | 11.22
DistributionFeederCB12_Ikawai11.22T2 | DistributionFeederCB12_Ikawai3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB12_Ikawai | BPD12 CB | Cable Joint | 3 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 705.5 | 1.5 | 0.95 | 15 | 1 | 1.2 | 1 | 5 | 0.4 | 0.75 | 339.15 | 6.5909 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 6.5909 | CB12_Ikawai6.59090885216197 | DistributionFeederCB12_Ikawai11.22339.15 | DistributionFeederCB12_Ikawai11.22339.15 | 6.5909 | 339.15 | 339.15 | BPD12 CB | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB12_Ikawai11.22T2 | DistributionFeederCB12_Ikawai3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB12_Ikawai | Cable Joint | W451 ABS | 4 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 1078.68 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB12_Ikawai7.63712890995778 | DistributionFeederCB12_Ikawai11.22392.9856 | DistributionFeederCB12_Ikawai11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | W451 ABS | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB12_Ikawai11.22T2 | DistributionFeederCB12_IkawaiJAGUAR11.22- | DistributionFeeder | CB12_Ikawai | W451 ABS | Cable 300 mm² | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB12_Ikawai7.51941315127282 | DistributionFeederCB12_Ikawai11.22386.92827157178 | DistributionFeederCB12_Ikawai11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W451 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22
DistributionFeederCB12_Ikawai11.22T2 | DistributionFeederCB12_IkawaiW45111.22- | DistributionFeeder | CB12_Ikawai | Cable 300 mm² | JAGUAR OH Line | 5 | GEMA | W451 | Air Break Switch | - | - | 11.22 | 400 | 7.7734 | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7734 | 7.7734 | 7.7734 | - | - | - | - | - | - | CB12_Ikawai7.77344402436912 | DistributionFeederCB12_Ikawai11.22400 | DistributionFeederCB12_Ikawai11.22400 | 7.7734 | 400 | 400 | Cable 300 mm² | JAGUAR OH Line | Air Break Switch - W451 | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_WaikakahiBPD-T2-CB1311.22Protection | DistributionFeeder | CB13_Waikakahi | 11 kV Bus | BPD13 CB | 1 | AEL 15000\RPS 860RP1685\AEL Transformer database | BPD-T2-CB13 | Circuit Breaker | Relay SEL 351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 400 | 7.7734 | - | - | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 7.7734 | - | 7.7734 | - | CB13_Waikakahi7.77344402436912 | DistributionFeederCB13_Waikakahi11.22400 | DistributionFeederCB13_Waikakahi11.22400 | 7.7734 | 400 | 400 | 11 kV Bus | BPD13 CB | Circuit Breaker-BPD-T2-CB13-Protection | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_Waikakahi3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB13_Waikakahi | BPD13 CB | Cable Joint | 3 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 707.1 | 1.5 | 0.95 | 15 | 1 | 1.2 | 1 | 5 | 0.4 | 0.75 | 339.15 | 6.5909 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 6.5909 | CB13_Waikakahi6.59090885216197 | DistributionFeederCB13_Waikakahi11.22339.15 | DistributionFeederCB13_Waikakahi11.22339.15 | 6.5909 | 339.15 | 339.15 | BPD13 CB | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_Waikakahi3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB13_Waikakahi | Cable Joint | Cable Joint | 4 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 692.5 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB13_Waikakahi7.63712890995778 | DistributionFeederCB13_Waikakahi11.22392.9856 | DistributionFeederCB13_Waikakahi11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_Waikakahi3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB13_Waikakahi | Cable Joint | W452 ABS | 5 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 331.5 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB13_Waikakahi7.63712890995778 | DistributionFeederCB13_Waikakahi11.22392.9856 | DistributionFeederCB13_Waikakahi11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | W452 ABS | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_WaikakahiJAGUAR11.22- | DistributionFeeder | CB13_Waikakahi | W452 ABS | Cable 300 mm² | 6 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB13_Waikakahi7.51941315127282 | DistributionFeederCB13_Waikakahi11.22386.92827157178 | DistributionFeederCB13_Waikakahi11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W452 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22
DistributionFeederCB13_Waikakahi11.22T2 | DistributionFeederCB13_WaikakahiW45211.22- | DistributionFeeder | CB13_Waikakahi | Cable 300 mm² | JAGUAR OH Line | 6 | GEMA | W452 | Air Break Switch | - | - | 11.22 | 400 | 7.7734 | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7734 | 7.7734 | 7.7734 | - | - | - | - | - | - | CB13_Waikakahi7.77344402436912 | DistributionFeederCB13_Waikakahi11.22400 | DistributionFeederCB13_Waikakahi11.22400 | 7.7734 | 400 | 400 | Cable 300 mm² | JAGUAR OH Line | Air Break Switch - W452 | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_WaihunaBPD-T1-CB111.22Protection | DistributionFeeder | CB1_Waihuna | 11 kV Bus | BPD1 CB | 1 | RPS 860RP2045\AEL Protection Database | BPD-T1-CB1 | Circuit Breaker | Relay SEL 751A | Protection | 11.22 | 800 | 15.5469 | 800 | 15.5469 | 800 | 15.5469 | - | - | - | - | 400 | 7.7734 | - | - | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5469 | 15.5469 | 15.5469 | - | - | 7.7734 | - | 7.7734 | - | CB1_Waihuna7.77344402436912 | DistributionFeederCB1_Waihuna11.22400 | DistributionFeederCB1_Waihuna11.22400 | 7.7734 | 400 | 400 | 11 kV Bus | BPD1 CB | Circuit Breaker-BPD-T1-CB1-Protection | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_Waihuna3-1c 400mm² AL XLPE11.22- | DistributionFeeder | CB1_Waihuna | BPD1 CB | Cable Joint | 2 | GEMA\AEL Drawing 12023 | 3-1c 400mm² AL XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 11.4 | 1.5 | 0.91 | 15 | 1 | 1.2 | 1 | 2 | 0.3 | 0.85 | 415.3695 | 8.0721 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 8.0721 | CB1_Waihuna8.07212889420047 | DistributionFeederCB1_Waihuna11.22415.3695 | DistributionFeederCB1_Waihuna11.22415.3695 | 8.0721 | 415.3695 | 415.3695 | BPD1 CB | Cable Joint | Cable-3-1c 400mm² AL XLPE | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_Waihuna3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB1_Waihuna | Cable Joint | Cable Joint | 3 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 83.3 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB1_Waihuna7.63712890995778 | DistributionFeederCB1_Waihuna11.22392.9856 | DistributionFeederCB1_Waihuna11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_Waihuna3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB1_Waihuna | Cable Joint | W636 ABS | 4 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 90.1 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.92 | 420.4032 | 8.17 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 8.17 | CB1_Waihuna8.16995185716414 | DistributionFeederCB1_Waihuna11.22420.4032 | DistributionFeederCB1_Waihuna11.22420.4032 | 8.17 | 420.4032 | 420.4032 | Cable Joint | W636 ABS | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_WaihunaJAGUAR11.22- | DistributionFeeder | CB1_Waihuna | W636 ABS | Cable 300 mm² | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB1_Waihuna7.51941315127282 | DistributionFeederCB1_Waihuna11.22386.92827157178 | DistributionFeederCB1_Waihuna11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W636 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22
DistributionFeederCB1_Waihuna11.22T1 | DistributionFeederCB1_WaihunaW63611.22- | DistributionFeeder | CB1_Waihuna | Cable 300 mm² | JAGUAR OH Line | 6 | GEMA | W636 | Air Break Switch | - | - | 11.22 | 600 | 11.6602 | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6602 | 11.6602 | 11.6602 | - | - | - | - | - | - | CB1_Waihuna11.6601660365537 | DistributionFeederCB1_Waihuna11.22600 | DistributionFeederCB1_Waihuna11.22600 | 11.6602 | 600 | 600 | Cable 300 mm² | JAGUAR OH Line | Air Break Switch - W636 | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_TawaiBPD-T1-CB211.22Protection | DistributionFeeder | CB2_Tawai | 11 kV Bus | BPD2 CB | 1 | RPS 860RP2045\AEL Protection Database | BPD-T1-CB2 | Circuit Breaker | Relay SEL 751A | Protection | 11.22 | 800 | 15.5469 | 800 | 15.5469 | 800 | 15.5469 | - | - | - | - | 400 | 7.7734 | - | - | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5469 | 15.5469 | 15.5469 | - | - | 7.7734 | - | 7.7734 | - | CB2_Tawai7.77344402436912 | DistributionFeederCB2_Tawai11.22400 | DistributionFeederCB2_Tawai11.22400 | 7.7734 | 400 | 400 | 11 kV Bus | BPD2 CB | Circuit Breaker-BPD-T1-CB2-Protection | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_Tawai3-1c 400mm² AL XLPE11.22- | DistributionFeeder | CB2_Tawai | BPD2 CB | Cable Joint | 2 | GEMA\AEL Drawing 12023 | 3-1c 400mm² AL XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 8.9 | 1.5 | 0.91 | 15 | 1 | 1.2 | 1 | 2 | 0.3 | 0.85 | 415.3695 | 8.0721 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 8.0721 | CB2_Tawai8.07212889420047 | DistributionFeederCB2_Tawai11.22415.3695 | DistributionFeederCB2_Tawai11.22415.3695 | 8.0721 | 415.3695 | 415.3695 | BPD2 CB | Cable Joint | Cable-3-1c 400mm² AL XLPE | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_Tawai3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB2_Tawai | Cable Joint | Cable Joint | 3 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 708.7 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB2_Tawai7.63712890995778 | DistributionFeederCB2_Tawai11.22392.9856 | DistributionFeederCB2_Tawai11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | Cable Joint | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_Tawai3c 300mm² AL XLPE MDPE11.22- | DistributionFeeder | CB2_Tawai | Cable Joint | W453 ABS | 4 | GEMA\AEL Drawing 12023 | 3c 300mm² AL XLPE MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | No | 1101.7 | 1.2 | 0.96 | 15 | 1 | 1.2 | 1 | 3 | 0.6 | 0.86 | 392.9856 | 7.6371 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.6371 | CB2_Tawai7.63712890995778 | DistributionFeederCB2_Tawai11.22392.9856 | DistributionFeederCB2_Tawai11.22392.9856 | 7.6371 | 392.9856 | 392.9856 | Cable Joint | W453 ABS | Cable-3c 300mm² AL XLPE MDPE | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_TawaiJAGUAR11.22- | DistributionFeeder | CB2_Tawai | W453 ABS | Cable 300 mm² | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11.22 | 523.1348 | 10.1664 | - | - | 386.9283 | 7.5194 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.1664 | - | 7.5194 | - | - | - | - | - | - | CB2_Tawai7.51941315127282 | DistributionFeederCB2_Tawai11.22386.92827157178 | DistributionFeederCB2_Tawai11.22386.92827157178 | 7.5194 | 386.9283 | 386.9283 | W453 ABS | Cable 300 mm² | OH Line-JAGUAR | 11.22
DistributionFeederCB2_Tawai11.22T1 | DistributionFeederCB2_TawaiW45311.22- | DistributionFeeder | CB2_Tawai | Cable 300 mm² | JAGUAR OH Line | 6 | GEMA | W453 | Air Break Switch | - | - | 11.22 | 400 | 7.7734 | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7734 | 7.7734 | 7.7734 | - | - | - | - | - | - | CB2_Tawai7.77344402436912 | DistributionFeederCB2_Tawai11.22400 | DistributionFeederCB2_Tawai11.22400 | 7.7734 | 400 | 400 | Cable 300 mm² | JAGUAR OH Line | Air Break Switch - W453 | 11.22
SubTransmissionCB522_CNR33T2 | SubTransmissionCB522_CNR524 ABS33- | SubTransmission | CB522_CNR | 33 kV Terminal | 524 ABS | 1 | GEMA\AEL 3266-02 Drawing | 524 ABS | Air Break Switch | - | - | 33 | 630 | 36.0093 | - | - | 630 | 36.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36 | - | 36 | - | - | - | - | - | - | CB522_CNR36 | SubTransmissionCB522_CNR33629.836657297774 | SubTransmissionCB522_CNR33630 | 36 | 629.8367 | 630 | 33 kV Terminal | 524 ABS | Air Break Switch-524 ABS | 33
SubTransmissionCB522_CNR33T2 | SubTransmissionCB522_CNRBPD-T2-CB52233Protection | SubTransmission | CB522_CNR | DS524 | CB522 | 2 | GEMA\AEL 3266-02\AEL Transformer database | BPD-T2-CB522 | Circuit Breaker | Relay SEL 311C | Protection | 33 | 3150 | 180.0467 | 3150 | 180.0467 | 3150 | 180.0467 | - | - | - | - | 370 | 21.1483 | - | - | - | - | 500 | 28.5788 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 180.0467 | 180.0467 | 180.0467 | - | - | 21.1483 | - | 28.5788 | - | CB522_CNR21.148340360416 | SubTransmissionCB522_CNR33370 | SubTransmissionCB522_CNR33370 | 21.1483 | 370 | 370 | DS524 | CB522 | Circuit Breaker-BPD-T2-CB522-Protection | 33
SubTransmissionCB522_CNR33T2 | SubTransmissionCB522_CNR526 ABS33- | SubTransmission | CB522_CNR | CB522 | 526 ABS | 3 | GEMA\AEL 3266-02 Drawing | 526 ABS | Air Break Switch | - | - | 33 | 630 | 36.0093 | - | - | 630 | 36.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | - | 36.0093 | - | - | - | - | - | - | CB522_CNR36.009336289357 | SubTransmissionCB522_CNR33630 | SubTransmissionCB522_CNR33630 | 36.0093 | 630 | 630 | CB522 | 526 ABS | Air Break Switch-526 ABS | 33
SubTransmissionCB3602_CNR33T1 | SubTransmissionCB3602_CNR3604 ABS33- | SubTransmission | CB3602_CNR | 33 kV Terminal | 3604 ABS | 1 | GEMA\AEL 3266-02 Drawing | 3604 ABS | Air Break Switch | - | - | 33 | - | - | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | - | - | - | - | - | - | CB3602_CNR45.7261413198184 | SubTransmissionCB3602_CNR33800 | SubTransmissionCB3602_CNR33800 | 45.7261 | 800 | 800 | 33 kV Terminal | 3604 ABS | Air Break Switch-3604 ABS | 33
SubTransmissionCB3602_CNR33T1 | SubTransmissionCB3602_CNRBPD-T1-CB360233Protection | SubTransmission | CB3602_CNR | DS3604 | CB3602 | 2 | GEMA\AEL 3266-02\AEL Transformer database | BPD-T1-CB3602 | Circuit Breaker | Relay SEL 387-6 | Protection | 33 | 3150 | 180.0467 | 3150 | 180.0467 | 3150 | 180.0467 | - | - | - | - | 492 | 28.1216 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 180.0467 | 180.0467 | 180.0467 | - | - | 28.1216 | - | - | - | CB3602_CNR28.1215769116883 | SubTransmissionCB3602_CNR33492 | SubTransmissionCB3602_CNR33492 | 28.1216 | 492 | 492 | DS3604 | CB3602 | Circuit Breaker-BPD-T1-CB3602-Protection | 33
SubTransmissionCB3602_CNR33T1 | SubTransmissionCB3602_CNR3606 ABS33- | SubTransmission | CB3602_CNR | CB3602 | 3606 ABS | 3 | GEMA\AEL 3266-02 Drawing | 3606 ABS | Air Break Switch | - | - | 33 | - | - | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | - | - | - | - | - | - | CB3602_CNR45.7261413198184 | SubTransmissionCB3602_CNR33800 | SubTransmissionCB3602_CNR33800 | 45.7261 | 800 | 800 | CB3602 | 3606 ABS | Air Break Switch-3606 ABS | 33
SubTransmissionCB522_CNR33 | SubTransmissionCB522_CNRCHAFER33- | SubTransmission | CB522_CNR | CB522/CB3602 | Pole 50593 | 1 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 73.1 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB522_CNR33.3732319248011 | SubTransmissionCB522_CNR33583.880134409446 | SubTransmissionCB522_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | CB522/CB3602 | Pole 50593 | OH Line-CHAFER | 33
SubTransmissionCB522_CNR33 | SubTransmissionCB522_CNRJAGUAR33- | SubTransmission | CB522_CNR | Pole 50593 | Pole 50738 | 2 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33 | 673.2838 | 38.4833 | - | - | 582.7931 | 33.3111 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11319 | - | - | - | - | - | - | - | - | - | - | - | 38.4833 | - | 33.3111 | - | - | - | - | - | - | CB522_CNR33.3110988840474 | SubTransmissionCB522_CNR33582.793088112333 | SubTransmissionCB522_CNR33582.793088112333 | 33.3111 | 582.7931 | 582.7931 | Pole 50593 | Pole 50738 | OH Line-JAGUAR | 33
SubTransmissionCB522_CNR33 | SubTransmissionCB522_CNRCHAFER33- | SubTransmission | CB522_CNR | Pole 50738 | CNR647 | 3 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 39.1 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB522_CNR33.3732319248011 | SubTransmissionCB522_CNR33583.880134409446 | SubTransmissionCB522_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | Pole 50738 | CNR647 | OH Line-CHAFER | 33
SubTransmissionCB522_CNR33 | SubTransmissionCB522_CNRCHAFER33- | SubTransmission | CB522_CNR | CNR647 | CNR644 | 4 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.8 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB522_CNR33.3732319248011 | SubTransmissionCB522_CNR33583.880134409446 | SubTransmissionCB522_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | CNR647 | CNR644 | OH Line-CHAFER | 33
SubTransmissionCB522_CNR33 | SubTransmissionCB522_CNRCNR-CB64233Protection | SubTransmission | CB522_CNR | CNR644 | CNR646 | 5 | GEMA\AEL Transformer database | CNR-CB642 | Circuit Breaker | - | Protection | 33 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | - | - | - | - | #N/A | #N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4471 | 71.4471 | 71.4471 | - | - | #N/A | - | - | - | #N/A | SubTransmissionCB522_CNR33 | #N/A | #N/A |  | #N/A | CNR644 | CNR646 | Circuit Breaker-CNR-CB642-Protection | 33
SubTransmissionCB642_CNR33 | SubTransmissionCB642_CNRCHAFER33- | SubTransmission | CB642_CNR | CB522/CB3602 | Pole 50593 | 1 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 73.1 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB642_CNR33.3732319248011 | SubTransmissionCB642_CNR33583.880134409446 | SubTransmissionCB642_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | CB522/CB3602 | Pole 50593 | OH Line-CHAFER | 33
SubTransmissionCB642_CNR33 | SubTransmissionCB642_CNRJAGUAR33- | SubTransmission | CB642_CNR | Pole 50593 | Pole 50738 | 2 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33 | 673.2838 | 38.4833 | - | - | 582.7931 | 33.3111 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11319 | - | - | - | - | - | - | - | - | - | - | - | 38.4833 | - | 33.3111 | - | - | - | - | - | - | CB642_CNR33.3110988840474 | SubTransmissionCB642_CNR33582.793088112333 | SubTransmissionCB642_CNR33582.793088112333 | 33.3111 | 582.7931 | 582.7931 | Pole 50593 | Pole 50738 | OH Line-JAGUAR | 33
SubTransmissionCB642_CNR33 | SubTransmissionCB642_CNRCHAFER33- | SubTransmission | CB642_CNR | Pole 50738 | CNR647 | 3 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 39.1 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB642_CNR33.3732319248011 | SubTransmissionCB642_CNR33583.880134409446 | SubTransmissionCB642_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | Pole 50738 | CNR647 | OH Line-CHAFER | 33
SubTransmissionCB642_CNR33 | SubTransmissionCB642_CNRCHAFER33- | SubTransmission | CB642_CNR | CNR647 | CNR644 | 4 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 33 | 674.4536 | 38.5502 | - | - | 583.8801 | 33.3732 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.8 | - | - | - | - | - | - | - | - | - | - | - | 38.5502 | - | 33.3732 | - | - | - | - | - | - | CB642_CNR33.3732319248011 | SubTransmissionCB642_CNR33583.880134409446 | SubTransmissionCB642_CNR33583.880134409445 | 33.3732 | 583.8801 | 583.8801 | CNR647 | CNR644 | OH Line-CHAFER | 33
SubTransmissionCB642_CNR33 | SubTransmissionCB642_CNRCNR-CB64233Protection | SubTransmission | CB642_CNR | CNR644 | CNR646 | 5 | GEMA\AEL Transformer database | CNR-CB642 | Circuit Breaker | - | Protection | 33 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | - | - | - | - | #N/A | #N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4471 | 71.4471 | 71.4471 | - | - | #N/A | - | - | - | #N/A | SubTransmissionCB642_CNR33 | #N/A | #N/A |  | #N/A | CNR644 | CNR646 | Circuit Breaker-CNR-CB642-Protection | 33
SecondarySubstationCNR33 | SecondarySubstationCNRT1/A141333HV Winding | SecondarySubstation | CNR | CNR642 | 11 kV Bus | 1 | AEL Transformer database | T1/A1413 | Transformer | - | HV Winding | 33 | 262.4319 | 15 | 262.4319 | 15 | 262.4319 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CNR | SecondarySubstationCNR33 | SecondarySubstationCNR33262.431940540739 |  |  | 262.4319 | CNR642 | 11 kV Bus | Transformer-T1/A1413-HV Winding | 33
SecondarySubstationCNR11 | SecondarySubstationCNRT1/A141311LV Winding | SecondarySubstation | CNR | CNR642 | 11 kV Bus | 2 | AEL Transformer database | T1/A1413 | Transformer | - | LV Winding | 11 | 787.2958 | 15 | 787.2958 | 15 | 787.2958 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CNR | SecondarySubstationCNR11 | SecondarySubstationCNR11787.295821622217 |  |  | 787.2958 | CNR642 | 11 kV Bus | Transformer-T1/A1413-LV Winding | 11
SecondarySubstationCNR11 | SecondarySubstationCNRCNR-CB3511Protection | SecondarySubstation | CNR | CNR642 | 11 kV Bus | 3 | GEMA\RPS 860RP1922\AEL Transformer database | CNR-CB35 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1104 | 21.034 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 21.034 | - | - | - | CNR21.0340250071164 | SecondarySubstationCNR111104 | SecondarySubstationCNR111104 | 21.034 | 1104 | 1104 | CNR642 | 11 kV Bus | Circuit Breaker-CNR-CB35-Protection | 11
SecondarySubstationCNR11 | SecondarySubstationCNR2x3x1c 630mm2 Al XLPE HDPE11- | SecondarySubstation | CNR | CNR642 | 11 kV Bus | 4 | GEMA\RPS 860RP1922\AEL Transformer database | 2x3x1c 630mm2 Al XLPE HDPE | Cable | - | - | 11 | 1336 | 25.4542 | 1336 | 25.4542 | 1336 | 25.4542 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 59.8 | 0.8 | 1 | 15 | 1 | 1.2 | 1 | 2 | 0.3 | 0.85 | 1135.6 | 21.6361 | 25.4542 | 25.4542 | 25.4542 | - | - | - | - | - | 21.6361 | CNR21.6360858678274 | SecondarySubstationCNR111135.6 | SecondarySubstationCNR111135.6 | 21.6361 | 1135.6 | 1135.6 | CNR642 | 11 kV Bus | Cable-2x3x1c 630mm2 Al XLPE HDPE | 11
DistributionFeederCB236_STU Incomer11.22 | DistributionFeederCB236_STU IncomerCNR-CB3611.22Protection | DistributionFeeder | CB236_STU Incomer | STU (limited) | 11 kV Bus | 7 | GEMA\RPS 860RP1922\AEL Transformer database | CNR-CB36 | Circuit Breaker | Relay SEL 751A | Protection | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 144 | 2.7984 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 2.7984 | - | - | - | CB236_STU Incomer2.79843984877288 | DistributionFeederCB236_STU Incomer11.22144 | DistributionFeederCB236_STU Incomer11.22144 | 2.7984 | 144 | 144 | STU (limited) | 11 kV Bus | Circuit Breaker-CNR-CB36-Protection | 11.22
DistributionFeederCB8_Drier 211 | DistributionFeederCB8_Drier 2CNR-CB811Protection | DistributionFeeder | CB8_Drier 2 | 11 kV Bus | CNR-CB8 | 1 | RPS 860RP1922\AEL Transformer database | CNR-CB8 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | 402 | 7.6591 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | 7.6591 | - | - | - | CB8_Drier 27.65912867106957 | DistributionFeederCB8_Drier 211402 | DistributionFeederCB8_Drier 211402 | 7.6591 | 402 | 402 | 11 kV Bus | CNR-CB8 | Circuit Breaker-CNR-CB8-Protection | 11
DistributionFeederCB8_Drier 211 | DistributionFeederCB8_Drier 23-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB8_Drier 2 | CNR-CB8 | Joint | 2 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 11.9 | 0.9 | 0.93 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 449.469 | 8.5635 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.5635 | CB8_Drier 28.56353458869893 | DistributionFeederCB8_Drier 211449.469 | DistributionFeederCB8_Drier 211449.469 | 8.5635 | 449.469 | 449.469 | CNR-CB8 | Joint | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB8_Drier 211 | DistributionFeederCB8_Drier 23-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB8_Drier 2 | Joint | Y815 | 3 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 440.8 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.3 | 0.72 | 378.9072 | 7.2192 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.2192 | CB8_Drier 27.21915173929028 | DistributionFeederCB8_Drier 211378.9072 | DistributionFeederCB8_Drier 211378.9072 | 7.2192 | 378.9072 | 378.9072 | Joint | Y815 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB9_WetProcess11 | DistributionFeederCB9_WetProcessCNR-CB911Protection | DistributionFeeder | CB9_WetProcess | 11 kV Bus | CNR-CB9 | 1 | RPS 860RP1922\AEL Transformer database | CNR-CB9 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | 402 | 7.6591 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | 7.6591 | - | - | - | CB9_WetProcess7.65912867106957 | DistributionFeederCB9_WetProcess11402 | DistributionFeederCB9_WetProcess11402 | 7.6591 | 402 | 402 | 11 kV Bus | CNR-CB9 | Circuit Breaker-CNR-CB9-Protection | 11
DistributionFeederCB9_WetProcess11 | DistributionFeederCB9_WetProcess3-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB9_WetProcess | CNR-CB9 | Joint | 2 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 13.1 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 473.634 | 9.0239 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 9.0239 | CB9_WetProcess9.02393967411285 | DistributionFeederCB9_WetProcess11473.634 | DistributionFeederCB9_WetProcess11473.634 | 9.0239 | 473.634 | 473.634 | CNR-CB9 | Joint | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB9_WetProcess11 | DistributionFeederCB9_WetProcess3-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB9_WetProcess | Joint | Y900 | 3 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 355.3 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.3 | 0.75 | 394.695 | 7.5199 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.5199 | CB9_WetProcess7.51994972842738 | DistributionFeederCB9_WetProcess11394.695 | DistributionFeederCB9_WetProcess11394.695 | 7.5199 | 394.695 | 394.695 | Joint | Y900 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB11_Boiler/Chiller 111 | DistributionFeederCB11_Boiler/Chiller 1CNR-CB1111Protection | DistributionFeeder | CB11_Boiler/Chiller 1 | 11 kV Bus | CNR-CB11 | 1 | RPS 860RP1922\AEL Transformer database | CNR-CB11 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | 402 | 7.6591 | - | - | - | - | - | - | - | - | - | - | 0.98 | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | 7.6591 | - | - | - | CB11_Boiler/Chiller 17.65912867106957 | DistributionFeederCB11_Boiler/Chiller 111402 | DistributionFeederCB11_Boiler/Chiller 111402 | 7.6591 | 402 | 402 | 11 kV Bus | CNR-CB11 | Circuit Breaker-CNR-CB11-Protection | 11
DistributionFeederCB11_Boiler/Chiller 111 | DistributionFeederCB11_Boiler/Chiller 13-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB11_Boiler/Chiller 1 | CNR-CB11 | Joint | 2 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 12.9 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 473.634 | 9.0239 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 9.0239 | CB11_Boiler/Chiller 19.02393967411285 | DistributionFeederCB11_Boiler/Chiller 111473.634 | DistributionFeederCB11_Boiler/Chiller 111473.634 | 9.0239 | 473.634 | 473.634 | CNR-CB11 | Joint | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB11_Boiler/Chiller 111 | DistributionFeederCB11_Boiler/Chiller 13-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB11_Boiler/Chiller 1 | Joint | Y1100 | 3 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 439.1 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.3 | 0.72 | 378.9072 | 7.2192 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.2192 | CB11_Boiler/Chiller 17.21915173929028 | DistributionFeederCB11_Boiler/Chiller 111378.9072 | DistributionFeederCB11_Boiler/Chiller 111378.9072 | 7.2192 | 378.9072 | 378.9072 | Joint | Y1100 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB12_Office11 | DistributionFeederCB12_OfficeCNR-CB1211Protection | DistributionFeeder | CB12_Office | 11 kV Bus | CNR-CB12 | 1 | RPS 860RP1922\AEL Transformer database | CNR-CB12 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 800 | 15.242 | 800 | 15.242 | 800 | 15.242 | - | - | - | - | 402 | 7.6591 | - | - | - | - | - | - | - | - | - | - | 0.98 | - | - | - | - | - | - | - | - | - | 15.242 | 15.242 | 15.242 | - | - | 7.6591 | - | - | - | CB12_Office7.65912867106957 | DistributionFeederCB12_Office11402 | DistributionFeederCB12_Office11402 | 7.6591 | 402 | 402 | 11 kV Bus | CNR-CB12 | Circuit Breaker-CNR-CB12-Protection | 11
DistributionFeederCB12_Office11 | DistributionFeederCB12_Office3-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB12_Office | CNR-CB12 | Joint | 2 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 13.8 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 473.634 | 9.0239 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 9.0239 | CB12_Office9.02393967411285 | DistributionFeederCB12_Office11473.634 | DistributionFeederCB12_Office11473.634 | 9.0239 | 473.634 | 473.634 | CNR-CB12 | Joint | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
DistributionFeederCB12_Office11 | DistributionFeederCB12_Office3-1c 400mm² AL XLPE CWS MDPE11- | DistributionFeeder | CB12_Office | Joint | Y1200 | 3 | GEMA\AEL Drawing No.3266-03 | 3-1c 400mm² AL XLPE CWS MDPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 238 | 0.9 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.3 | 0.75 | 394.695 | 7.5199 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.5199 | CB12_Office7.51994972842738 | DistributionFeederCB12_Office11394.695 | DistributionFeederCB12_Office11394.695 | 7.5199 | 394.695 | 394.695 | Joint | Y1200 | Cable-3-1c 400mm² AL XLPE CWS MDPE | 11
- | - | - | - | - | - | - | - | - | - | - | - | - | - | 4.9556 | - | 4.9556 | - | 4.9556 | - | 34.2946 | - | 34.2946 | - | #N/A | - | 4.9556 | - | 114.3154 | - | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | -
Note on N26: Author: Incomer cable ratings
Note on P26: Author: Incomer cable ratings
Note on R26: Author: Incomer cable ratings
Note on N28: Author: Incomer cable ratings
Note on P28: Author: Incomer cable ratings
Note on R28: Author: Incomer cable ratings
Note on N33: Author: Derated for 50 Degrees Celcius
Note on R33: Author: Author: Derated for 50 Degrees Celcius
Note on N41: Author: Derated for 50 Degrees Celcius
Note on R41: Author: Author: Derated for 50 Degrees Celcius
Note on N47: Author: Derated for 50 Degrees Celcius
Note on R47: Author: Author: Derated for 50 Degrees Celcius
Note on N53: Author: Derated for 50 Degrees Celcius
Note on R53: Author: Author: Derated for 50 Degrees Celcius
Note on N67: Author: Derated for 75 Degrees Celcius
Note on R67: Author: Derated for 75 Degrees Celcius
Note on N68: Author: Derated for 75 Degrees Celcius
Note on R68: Author: Derated for 75 Degrees Celcius
Note on N69: Author: Derated for 75 Degrees Celcius
Note on R69: Author: Derated for 75 Degrees Celcius
Note on N70: Author: Derated for 75 Degrees Celcius
Note on R70: Author: Derated for 75 Degrees Celcius
Note on R71: Author: Author: Derated for 50 Degrees Celcius
Note on N72: Author: Derated for 75 Degrees Celcius
Note on R72: Author: Derated for 75 Degrees Celcius
Note on N73: Author: Derated for 75 Degrees Celcius
Note on R73: Author: Derated for 75 Degrees Celcius
Note on N74: Author: Derated for 75 Degrees Celcius
Note on R74: Author: Derated for 75 Degrees Celcius
Note on N75: Author: Derated for 75 Degrees Celcius
Note on R75: Author: Derated for 75 Degrees Celcius
Note on R76: Author: Author: Derated for 50 Degrees Celcius
Note on P77: Author: ONAF Rating
Note on R77: Author: ONAF Rating
Note on P78: Author: ONAF Rating
Note on R78: Author: ONAF Rating
Note on D81: Author: Tie capability rather than supply capability, hence why it is not getting accounted for.

## STU_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of Data | ID | Type | Device ID | Device Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal Resistivity |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [10 empty] | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | (A) | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPSTU_GXP110T5 | GXPSTU_GXPT5110HV Winding | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report STU.TF.T5 | T5 | Transformer | - | HV Winding | 110 | 52 | 9.9073 | 52 | 9.9073 | 52 | 9.9073 | 62 | 11.8126 | 60 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STU_GXP | GXPSTU_GXP110 | GXPSTU_GXP11052 |  |  | 52 | 110 kV Bus | 11 kV Bus | Transformer-T5-HV Winding | 110
GXPSTU_GXP11.198T5 | GXPSTU_GXPT511.198Tap Changer | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 2 | TP Branch Report STU.TF.T5 | T5 | Transformer | STU-TF-T5B | Tap Changer | 11.198 | 600 | 11.6373 | 600 | 11.6373 | 600 | 11.6373 | 720 | 13.9648 | 720 | 13.9648 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6373 | 11.6373 | 11.6373 | 13.9648 | 13.9648 | - | - | - | - | STU_GXP11.6373029658938 | GXPSTU_GXP11.198600 | GXPSTU_GXP11.198600 | 11.6373 | 600 | 600 | 110 kV Bus | 11 kV Bus | Transformer-T5-Tap Changer | 11.198
GXPSTU_GXP11.198T5 | GXPSTU_GXPT511.198LV Winding | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 3 | TP Branch Report STU.TF.T5 | T5 | Transformer | - | LV Winding | 11.198 | 524 | 10.1632 | 524 | 10.1632 | 524 | 10.1632 | 646 | 12.5295 | 604 | 11.7149 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STU_GXP | GXPSTU_GXP11.198 | GXPSTU_GXP11.198524 |  |  | 524 | 110 kV Bus | 11 kV Bus | Transformer - T5 - LV Winding | 11.198
GXPSTU_GXP11.198T5 | GXPSTU_GXPSTU-CBL-281211.198Cable | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 4 | TP Branch Report STU.TF.T5 | STU-CBL-2812 | Cable | STU-CBL-2812 | Cable | 11.198 | 662 | 12.8398 | 662 | 12.8398 | 662 | 12.8398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71 | - | - | - | - | - | - | - | - | - | - | - | 12.8398 | 12.8398 | 12.8398 | - | - | - | - | - | - | STU_GXP12.8398242723695 | GXPSTU_GXP11.198662 | GXPSTU_GXP11.198662 | 12.8398 | 662 | 662 | 110 kV Bus | 11 kV Bus | Cable-STU-CBL-2812-Cable | 11.198
GXPSTU_GXP11.198T5 | GXPSTU_GXPSTU CB4\CB281211.198Protection | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 5 | GEMA\RPS 860RP1352\AEL Transformer database | STU CB4\CB2812 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 1250 | 24.2444 | 1250 | 24.2444 | 1250 | 24.2444 | - | - | - | - | 823 | 15.9625 | 823 | 15.9625 | 3600 | 69.8238 | 2400 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.2444 | 24.2444 | 24.2444 | - | - | 15.9625 | 69.8238 | 46.5492 | - | STU_GXP15.9625005682176 | GXPSTU_GXP11.198823 | GXPSTU_GXP11.198823 | 15.9625 | 823 | 823 | 110 kV Bus | 11 kV Bus | Circuit Breaker-STU CB4\CB2812-Protection | 11.198
GXPSTU_GXP110T6 | GXPSTU_GXPT6110HV Winding | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report STU.TF.T6 | T6 | Transformer | - | HV Winding | 110 | 52 | 9.9073 | 52 | 9.9073 | 52 | 9.9073 | 62 | 11.8126 | 60 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STU_GXP | GXPSTU_GXP110 | GXPSTU_GXP11052 |  |  | 52 | 110 kV Bus | 11 kV Bus | Transformer-T6-HV Winding | 110
GXPSTU_GXP11.198T6 | GXPSTU_GXPT611.198Tap Changer | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report STU.TF.T6 | T6 | Transformer | - | Tap Changer | 11.198 | 600 | 11.6373 | 600 | 11.6373 | 600 | 11.6373 | 720 | 13.9648 | 720 | 13.9648 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6373 | 11.6373 | 11.6373 | 13.9648 | 13.9648 | - | - | - | - | STU_GXP11.6373029658938 | GXPSTU_GXP11.198600 | GXPSTU_GXP11.198600 | 11.6373 | 600 | 600 | 110 kV Bus | 11 kV Bus | Transformer-T6-Tap Changer | 11.198
GXPSTU_GXP11.198T6 | GXPSTU_GXPT611.198LV Winding | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report STU.TF.T6 | T6 | Transformer | - | LV Winding | 11.198 | 524 | 10.1632 | 524 | 10.1632 | 524 | 10.1632 | 646 | 12.5295 | 604 | 11.7149 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STU_GXP | GXPSTU_GXP11.198 | GXPSTU_GXP11.198524 |  |  | 524 | 110 kV Bus | 11 kV Bus | Transformer - T6 - LV Winding | 11.198
GXPSTU_GXP11.198T6 | GXPSTU_GXPSTU-CBL-277211.198Cable | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 2 | TP Branch Report STU.TF.T6 | STU-CBL-2772 | Cable | STU-CBL-2772 | Cable | 11.198 | 662 | 12.8398 | 662 | 12.8398 | 662 | 12.8398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | - | - | - | - | - | - | - | - | - | - | - | 12.8398 | 12.8398 | 12.8398 | - | - | - | - | - | - | STU_GXP12.8398242723695 | GXPSTU_GXP11.198662 | GXPSTU_GXP11.198662 | 12.8398 | 662 | 662 | 110 kV Bus | 11 kV Bus | Cable-STU-CBL-2772-Cable | 11.198
GXPSTU_GXP11.198T6 | GXPSTU_GXPSTU CB6\CB277211.198Protection | GXP | STU_GXP | 110 kV Bus | 11 kV Bus | 2 | GEMA\RPS 860RP1352\AEL Transformer database | STU CB6\CB2772 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 1250 | 24.2444 | 1250 | 24.2444 | 1250 | 24.2444 | - | - | - | - | 823 | 15.9625 | 823 | 15.9625 | 3600 | 69.8238 | 2400 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.2444 | 24.2444 | 24.2444 | - | - | 15.9625 | 69.8238 | 46.5492 | - | STU_GXP15.9625005682176 | GXPSTU_GXP11.198823 | GXPSTU_GXP11.198823 | 15.9625 | 823 | 823 | 110 kV Bus | 11 kV Bus | Circuit Breaker-STU CB6\CB2772-Protection | 11.198
GXPSTU 11.198 | GXPSTU STU-CB511.198Protection | GXP | STU | 11 kV Bus | 11 kV Bus | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB5 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 1250 | 24.2444 | 1250 | 24.2444 | 1250 | 24.2444 | - | - | - | - | 744 | 14.4303 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.2444 | 24.2444 | 24.2444 | - | - | 14.4303 | - | - | - | STU 14.4302556777083 | GXPSTU 11.198744 | GXPSTU 11.198744 | 14.4303 | 744 | 744 | 11 kV Bus | 11 kV Bus | Circuit Breaker-STU-CB5-Protection | 11.198
DistributionFeederCB1_Otaio11.198 | DistributionFeederCB1_OtaioSTU-CB111.198Protection | DistributionFeeder | CB1_Otaio | 11 kV Bus | STU-1 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB1 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 360 | 6.9824 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 6.9824 | - | 11.6373 | - | CB1_Otaio6.98238177953626 | DistributionFeederCB1_Otaio11.198360 | DistributionFeederCB1_Otaio11.198360 | 6.9824 | 360 | 360 | 11 kV Bus | STU-1 | Circuit Breaker-STU-CB1-Protection | 11.198
DistributionFeederCB1_Otaio11.198 | DistributionFeederCB1_Otaio3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB1_Otaio | STU-1 | Pole 31678 | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 60.2 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB1_Otaio6.84542561937549 | DistributionFeederCB1_Otaio11.198352.938768 | DistributionFeederCB1_Otaio11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-1 | Pole 31678 | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB1_Otaio11.198 | DistributionFeederCB1_OtaioCHAFER11.198- | DistributionFeeder | CB1_Otaio | Pole 31678 | W300 ABS | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4.1 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB1_Otaio7.52748942626711 | DistributionFeederCB1_Otaio11.198388.104844309464 | DistributionFeederCB1_Otaio11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | Pole 31678 | W300 ABS | OH Line-CHAFER | 11.198
DistributionFeederCB1_Otaio11.198 | DistributionFeederCB1_OtaioCHAFER11.198- | DistributionFeeder | CB1_Otaio | W300 ABS | A224 TX | 6 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 347.5 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB1_Otaio7.52748942626711 | DistributionFeederCB1_Otaio11.198388.104844309464 | DistributionFeederCB1_Otaio11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | W300 ABS | A224 TX | OH Line-CHAFER | 11.198
DistributionFeederCB1_Otaio11.198 | DistributionFeederCB1_OtaioW30011.198- | DistributionFeeder | CB1_Otaio | W300 ABS | - | 7 | GEMA | W300 | Air Break Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB1_Otaio7.75820197726251 | DistributionFeederCB1_Otaio11.198400 | DistributionFeederCB1_Otaio11.198400 | 7.7582 | 400 | 400 | W300 ABS | - | Air Break Switch-W300 | 11.198
DistributionFeederCB2_Glenavy11.198 | DistributionFeederCB2_GlenavySTU-CB211.198Protection | DistributionFeeder | CB2_Glenavy | 11 kV Bus | STU-2 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB2 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 300 | 5.8187 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 5.8187 | - | 11.6373 | - | CB2_Glenavy5.81865148294689 | DistributionFeederCB2_Glenavy11.198300 | DistributionFeederCB2_Glenavy11.198300 | 5.8187 | 300 | 300 | 11 kV Bus | STU-2 | Circuit Breaker-STU-CB2-Protection | 11.198
DistributionFeederCB2_Glenavy11.198 | DistributionFeederCB2_Glenavy3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB2_Glenavy | STU-2 | W405 ABS | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 62 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB2_Glenavy6.84542561937549 | DistributionFeederCB2_Glenavy11.198352.938768 | DistributionFeederCB2_Glenavy11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-2 | W405 ABS | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB2_Glenavy11.198 | DistributionFeederCB2_GlenavyCHAFER11.198- | DistributionFeeder | CB2_Glenavy | W405 ABS | TOA1089 | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 85.27 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB2_Glenavy7.52748942626711 | DistributionFeederCB2_Glenavy11.198388.104844309464 | DistributionFeederCB2_Glenavy11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | W405 ABS | TOA1089 | OH Line-CHAFER | 11.198
DistributionFeederCB2_Glenavy11.198 | DistributionFeederCB2_GlenavyW40511.198- | DistributionFeeder | CB2_Glenavy | W405 ABS | - | 6 | GEMA | W405 | Air Break Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB2_Glenavy7.75820197726251 | DistributionFeederCB2_Glenavy11.198400 | DistributionFeederCB2_Glenavy11.198400 | 7.7582 | 400 | 400 | W405 ABS | - | Air Break Switch-W405 | 11.198
DistributionFeederCB3_Waimate11.198 | DistributionFeederCB3_WaimateSTU-CB311.198Protection | DistributionFeeder | CB3_Waimate | 11 kV Bus | STD-3 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB3 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 300 | 5.8187 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 5.8187 | - | 11.6373 | - | CB3_Waimate5.81865148294689 | DistributionFeederCB3_Waimate11.198300 | DistributionFeederCB3_Waimate11.198300 | 5.8187 | 300 | 300 | 11 kV Bus | STD-3 | Circuit Breaker-STU-CB3-Protection | 11.198
DistributionFeederCB3_Waimate11.198 | DistributionFeederCB3_Waimate3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB3_Waimate | STU-3 | W400 ABS | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 61.8 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB3_Waimate6.84542561937549 | DistributionFeederCB3_Waimate11.198352.938768 | DistributionFeederCB3_Waimate11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-3 | W400 ABS | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB3_Waimate11.198 | DistributionFeederCB3_WaimateCHAFER11.198- | DistributionFeeder | CB3_Waimate | W400 ABS | A404 TX | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 561.3 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB3_Waimate7.52748942626711 | DistributionFeederCB3_Waimate11.198388.104844309464 | DistributionFeederCB3_Waimate11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | W400 ABS | A404 TX | OH Line-CHAFER | 11.198
DistributionFeederCB3_Waimate11.198 | DistributionFeederCB3_WaimateW40011.198- | DistributionFeeder | CB3_Waimate | W400 ABS | - | 6 | GEMA | W400 | Air Break Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB3_Waimate7.75820197726251 | DistributionFeederCB3_Waimate11.198400 | DistributionFeederCB3_Waimate11.198400 | 7.7582 | 400 | 400 | W400 ABS | - | Air Break Switch-W400 | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_WaihaorungaSTU-CB711.198Protection | DistributionFeeder | CB7_Waihaorunga | 11 kV Bus | STD-7 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB7 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 360 | 6.9824 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 6.9824 | - | 11.6373 | - | CB7_Waihaorunga6.98238177953626 | DistributionFeederCB7_Waihaorunga11.198360 | DistributionFeederCB7_Waihaorunga11.198360 | 6.9824 | 360 | 360 | 11 kV Bus | STD-7 | Circuit Breaker-STU-CB7-Protection | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_Waihaorunga3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB7_Waihaorunga | STU-7 | W406 | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1116.4 | 0.7 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB7_Waihaorunga6.84542561937549 | DistributionFeederCB7_Waihaorunga11.198352.938768 | DistributionFeederCB7_Waihaorunga11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-7 | W406 | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_WaihaorungaW40611.198- | DistributionFeeder | CB7_Waihaorunga | W407 | W408 | 5 | GEMA | W406 | Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB7_Waihaorunga7.75820197726251 | DistributionFeederCB7_Waihaorunga11.198400 | DistributionFeederCB7_Waihaorunga11.198400 | 7.7582 | 400 | 400 | W407 | W408 | Switch - W406 | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_WaihaorungaW40811.198- | DistributionFeeder | CB7_Waihaorunga | W406 | W408 | 5 | GEMA | W408 | Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB7_Waihaorunga7.75820197726251 | DistributionFeederCB7_Waihaorunga11.198400 | DistributionFeederCB7_Waihaorunga11.198400 | 7.7582 | 400 | 400 | W406 | W408 | Switch-W408 | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_Waihaorunga3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB7_Waihaorunga | W408 | W661 | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 541 | 0.7 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB7_Waihaorunga6.84542561937549 | DistributionFeederCB7_Waihaorunga11.198352.938768 | DistributionFeederCB7_Waihaorunga11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | W408 | W661 | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB7_Waihaorunga11.198 | DistributionFeederCB7_WaihaorungaCHAFER11.198- | DistributionFeeder | CB7_Waihaorunga | W661 | Pole 00088 | 4 | GEMA | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3835 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB7_Waihaorunga7.52748942626711 | DistributionFeederCB7_Waihaorunga11.198388.104844309464 | DistributionFeederCB7_Waihaorunga11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | W661 | Pole 00088 | OH Line - CHAFER | 11.198
DistributionFeederCB8_Mt Studholme11.198 | DistributionFeederCB8_Mt StudholmeSTU-CB811.198Protection | DistributionFeeder | CB8_Mt Studholme | 11 kV Bus | STD-8 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB8 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 360 | 6.9824 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 6.9824 | - | 11.6373 | - | CB8_Mt Studholme6.98238177953626 | DistributionFeederCB8_Mt Studholme11.198360 | DistributionFeederCB8_Mt Studholme11.198360 | 6.9824 | 360 | 360 | 11 kV Bus | STD-8 | Circuit Breaker-STU-CB8-Protection | 11.198
DistributionFeederCB8_Mt Studholme11.198 | DistributionFeederCB8_Mt Studholme3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB8_Mt Studholme | STU-8 | Pole 31677 | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 60.7 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB8_Mt Studholme6.84542561937549 | DistributionFeederCB8_Mt Studholme11.198352.938768 | DistributionFeederCB8_Mt Studholme11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-8 | Pole 31677 | Cable-3c-300mm² AL XLPE HDPE | 11.198
DistributionFeederCB8_Mt Studholme11.198 | DistributionFeederCB8_Mt StudholmeCHAFER11.198- | DistributionFeeder | CB8_Mt Studholme | Pole 31677 | W200 ABS | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11.198 | 524.3264 | 10.1696 | - | - | 388.1048 | 7.5275 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4.1 | - | - | - | - | - | - | - | - | - | - | - | 10.1696 | - | 7.5275 | - | - | - | - | - | - | CB8_Mt Studholme7.52748942626711 | DistributionFeederCB8_Mt Studholme11.198388.104844309464 | DistributionFeederCB8_Mt Studholme11.198388.104844309464 | 7.5275 | 388.1048 | 388.1048 | Pole 31677 | W200 ABS | OH Line-CHAFER | 11.198
DistributionFeederCB8_Mt Studholme11.198 | DistributionFeederCB8_Mt Studholme70mm² Cu11.198- | DistributionFeeder | CB8_Mt Studholme | W200 ABS | A1103 TX | 6 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 11.198 | 328 | 6.3617 | - | - | 247 | 4.7907 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 775.1 | - | - | - | - | - | - | - | - | - | - | - | 6.3617 | - | 4.7907 | - | - | - | - | - | - | CB8_Mt Studholme4.7906897209596 | DistributionFeederCB8_Mt Studholme11.198247 | DistributionFeederCB8_Mt Studholme11.198247 | 4.7907 | 247 | 247 | W200 ABS | A1103 TX | OH Line-70mm² Cu | 11.198
DistributionFeederCB8_Mt Studholme11.198 | DistributionFeederCB8_Mt StudholmeW20011.198- | DistributionFeeder | CB8_Mt Studholme | W200 ABS | - | 7 | GEMA | W200 | Air Break Switch | - | - | 11.198 | 400 | 7.7582 | 400 | 7.7582 | 400 | 7.7582 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7582 | 7.7582 | 7.7582 | - | - | - | - | - | - | CB8_Mt Studholme7.75820197726251 | DistributionFeederCB8_Mt Studholme11.198400 | DistributionFeederCB8_Mt Studholme11.198400 | 7.7582 | 400 | 400 | W200 ABS | - | Air Break Switch-W200 | 11.198
DistributionFeederCB9_Morven11.198 | DistributionFeederCB9_MorvenSTU-CB911.198Protection | DistributionFeeder | CB9_Morven | 11 kV Bus | STD-9 | 3 | GEMA\RPS 860RP1352\AEL Transformer database | STU-CB9 | Circuit Breaker | Relay SEL 351S | Protection | 11.198 | 630 | 12.2192 | 630 | 12.2192 | 630 | 12.2192 | - | - | - | - | 300 | 5.8187 | - | - | - | - | 600 | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2192 | 12.2192 | 12.2192 | - | - | 5.8187 | - | 11.6373 | - | CB9_Morven5.81865148294689 | DistributionFeederCB9_Morven11.198300 | DistributionFeederCB9_Morven11.198300 | 5.8187 | 300 | 300 | 11 kV Bus | STD-9 | Circuit Breaker-STU-CB9-Protection | 11.198
DistributionFeederCB9_Morven11.198 | DistributionFeederCB9_Morven3c-300mm² AL XLPE HDPE11.198- | DistributionFeeder | CB9_Morven | STU-9 | Pole 31989 | 4 | GEMA | 3c-300mm² AL XLPE HDPE | Cable | - | - | 11.198 | 476 | 9.2323 | 476 | 9.2323 | 476 | 9.2323 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 72.1 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.5 | 0.78 | 352.9388 | 6.8454 | 9.2323 | 9.2323 | 9.2323 | - | - | - | - | - | 6.8454 | CB9_Morven6.84542561937549 | DistributionFeederCB9_Morven11.198352.938768 | DistributionFeederCB9_Morven11.198352.938768 | 6.8454 | 352.9388 | 352.9388 | STU-9 | Pole 31989 | Cable-3c-300mm² AL XLPE HDPE | 11.198
[13 empty] | - | 6.3617 | - | 6.3617 | - | 6.3617 | - | 11.8126 | - | 11.4315 | - | 5.8187 | - | 15.9625 | - | 69.8238 | - | 11.6373 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | -
Note on N18: Author: Derated to 50 degress celcius operation
Note on R18: Author: Derated to 50 degress celcius operation
Note on N19: Author: Derated to 50 degress celcius operation
Note on R19: Author: Derated to 50 degress celcius operation
Note on N23: Author: Derated to 50 degress celcius operation
Note on R23: Author: Derated to 50 degress celcius operation
Note on N27: Author: Derated to 50 degress celcius operation
Note on R27: Author: Derated to 50 degress celcius operation
Note on N34: Author: Derated to 50 degress celcius operation
Note on R34: Author: Derated to 50 degress celcius operation
Note on N37: Author: Derated to 50 degress celcius operation
Note on R37: Author: Derated to 50 degress celcius operation
Note on N38: Author: Derated to 50 degress celcius operation
Note on R38: Author: Derated to 50 degress celcius operation

## TIM_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of Data | ID | Type | Device ID | Device Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal Resistivity |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [10 empty] | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | (A) | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPTIM_GXP110T3 | GXPTIM_GXPTIM-DS-94110HV Disconnector | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report TIM.TF.T3 | TIM-DS-94 | Disconnector | - | HV Disconnector | 110 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 152.4205 | 152.4205 | 152.4205 | - | - | - | - | - | - | TIM_GXP152.420471066061 | GXPTIM_GXP110800 | GXPTIM_GXP110800 | 152.4205 | 800 | 800 | 110 kV Bus | 11 kV Bus | Disconnector-TIM-DS-94-HV Disconnector | 110
GXPTIM_GXP110T3 | GXPTIM_GXPTIM-CT-CT92110Current Transformer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 2 | TP Branch Report TIM.TF.T3 | TIM-CT-CT92 | Circuit breaker |  | Current Transformer | 110 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | 238.157 | 238.157 | 238.157 | 238.157 | - | - | - | - | TIM_GXP238.156986040721 | GXPTIM_GXP1101250 | GXPTIM_GXP1101250 | 238.157 | 1250 | 1250 | 110 kV Bus | 11 kV Bus | Circuit breaker - TIM-CT-CT92 - Current Transformer | 110
GXPTIM_GXP110T3 | GXPTIM_GXPTIM-CB92110HV Circuit breaker | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 3 | TP Branch Report TIM.TF.T3 | TIM-CB92 | Circuit breaker | - | HV Circuit breaker | 110 | 2500 | 476.314 | - | - | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 446 | 84.9744 | 446 | 84.9744 | 1200 | 228.6307 | 600 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 476.314 | - | 476.314 | 476.314 | 476.314 | 84.9744 | 228.6307 | 114.3154 | - | TIM_GXP84.9744126193291 | GXPTIM_GXP110446 | GXPTIM_GXP110446 | 84.9744 | 446 | 446 | 110 kV Bus | 11 kV Bus | Circuit breaker-TIM-CB92-HV Circuit breaker | 110
GXPTIM_GXP110T3 | GXPTIM_GXPTIM-TF-T3110Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 6 | TP Branch Report TIM.TF.T3 | TIM-TF-T3 | Transformer |  | Bushings | 110 | 2100 | 400.1037 | 2100 | 400.1037 | 2100 | 400.1037 | 2520 | 480.1245 | 2520 | 480.1245 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400.1037 | 400.1037 | 400.1037 | 480.1245 | 480.1245 | - | - | - | - | TIM_GXP400.103736548411 | GXPTIM_GXP1102100 | GXPTIM_GXP1102100 | 400.1037 | 2100 | 2100 | 110 kV Bus | 11 kV Bus | Transformer - TIM-TF-T3 - Bushings | 110
GXPTIM_GXP110T3 | GXPTIM_GXPTIM.TF.T3110HV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 7 | TP Branch Report TIM.TF.T3 | TIM.TF.T3 | Transformer | - | HV Winding | 110 | 250 | 47.6314 | - | - | 250 | 47.6314 | 336 | 64.0166 | 323 | 61.5398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 64.0166 | 61.5398 | - | - | - | - | TIM_GXP61.5397651929222 | GXPTIM_GXP110323 | GXPTIM_GXP110250 | 61.5398 | 323 | 250 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T3-HV Winding | 110
GXPTIM_GXP11T3 | GXPTIM_GXPTIM.TF.T311LV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 8 | TP Branch Report TIM.TF.T3 | TIM.TF.T3 | Transformer | - | LV Winding | 11 | 2498 | 47.5933 | - | - | - | - | 3364 | 64.0928 | 3228 | 61.5017 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 64.0928 | 61.5017 | - | - | - | - | TIM_GXP61.5016600751557 | GXPTIM_GXP113228 | GXPTIM_GXP112498 | 61.5017 | 3228 | 2498 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T3-LV Winding | 11
GXPTIM_GXP110T3 | GXPTIM_GXPTIM.TF.T3110Tap Changer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 4 | TP Branch Report TIM.TF.T3 | TIM.TF.T3 | Tap Changer | - | Tap Changer | 110 | 250 | 47.6314 | - | - | 250 | 47.6314 | 323 | 61.5398 | 300 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | - | 47.6314 | 61.5398 | 57.1577 | - | - | - | - | TIM_GXP47.6313972081441 | GXPTIM_GXP110250 | GXPTIM_GXP110250 | 47.6314 | 250 | 250 | 110 kV Bus | 11 kV Bus | Tap Changer-TIM.TF.T3-Tap Changer | 110
GXPTIM_GXP11T3 | GXPTIM_GXPTIM.TF.T311Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 5 | TP Branch Report TIM.TF.T3 | TIM.TF.T3 | Transformer |  | Bushings | 11 | 5000 | 95.2628 | 5000 | 95.2628 | 5000 | 95.2628 | 6000 | 114.3154 | 6000 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2628 | 95.2628 | 95.2628 | 114.3154 | 114.3154 | - | - | - | - | TIM_GXP95.2627944162882 | GXPTIM_GXP115000 | GXPTIM_GXP115000 | 95.2628 | 5000 | 5000 | 110 kV Bus | 11 kV Bus | Transformer - TIM.TF.T3 - Bushings | 11
GXPTIM_GXP11T3 | GXPTIM_GXPTIM-CB275211Current Transformer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 9 | TP Branch Report TIM.TF.T3 | TIM-CB2752 | Circuit breaker |  | Current Transformer | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | 47.6314 | 47.6314 | - | - | - | - | TIM_GXP47.6313972081441 | GXPTIM_GXP112500 | GXPTIM_GXP112500 | 47.6314 | 2500 | 2500 | 110 kV Bus | 11 kV Bus | Circuit breaker - TIM-CB2752 - Current Transformer | 11
GXPTIM_GXP11T3 | GXPTIM_GXPTIM-CB275211Protection | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 10 | TP Branch Report TIM.TF.T3 | TIM-CB2752 | Circuit Breaker | Relay SEL 451-4 | Protection | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | 1544 | 29.4172 | - | - | 7200 | 137.1784 | 4800 | 91.4523 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | 29.4172 | 137.1784 | 91.4523 | - | TIM_GXP29.4171509157498 | GXPTIM_GXP111544 | GXPTIM_GXP111544 | 29.4172 | 1544 | 1544 | 110 kV Bus | 11 kV Bus | Circuit Breaker-TIM-CB2752-Protection | 11
GXPTIM_GXP11T3 | GXPTIM_GXPTIM-CB2752-OEL11Other Equipment | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 11 | TP Branch Report TIM.TF.T3 | TIM-CB2752-OEL | Other Equipment |  | Other Equipment | 11 | 2880 | 54.8714 | 2880 | 54.8714 | 2880 | 54.8714 | 2880 | 54.8714 | 2880 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 54.8714 | 54.8714 | 54.8714 | 54.8714 | 54.8714 | - | - | - | - | TIM_GXP54.871369583782 | GXPTIM_GXP112880 | GXPTIM_GXP112880 | 54.8714 | 2880 | 2880 | 110 kV Bus | 11 kV Bus | Other Equipment - TIM-CB2752-OEL - Other Equipment | 11
GXPTIM_GXP11T3 | GXPTIM_GXPTIM-CBL-T3-CB275211Cable | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 12 | TP Branch Report TIM.TF.T3 | TIM-CBL-T3-CB2752 | Cable | - | Cable | 11 | 2534 | 48.2792 | - | - | 2534 | 48.2792 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2534 | 48.2792 | 48.2792 | - | 48.2792 | - | - | - | - | - | 48.2792 | TIM_GXP48.2791842101749 | GXPTIM_GXP112534 | GXPTIM_GXP112534 | 48.2792 | 2534 | 2534 | 110 kV Bus | 11 kV Bus | Cable-TIM-CBL-T3-CB2752-Cable | 11
GXPTIM_GXP110T4 | GXPTIM_GXPTIM-DS-44110HV Disconnector | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report TIM.TF.T4 | TIM-DS-44 | Disconnector | - | HV Disconnector | 110 | 800 | 152.4205 | - | - | 800 | 152.4205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 152.4205 | - | 152.4205 | - | - | - | - | - | - | TIM_GXP152.420471066061 | GXPTIM_GXP110800 | GXPTIM_GXP110800 | 152.4205 | 800 | 800 | 110 kV Bus | 11 kV Bus | Disconnector - TIM-DS-44 - HV Disconnector | 110
GXPTIM_GXP110T4 | GXPTIM_GXPTIM-CB42110HV Circuit breaker | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 2 | TP Branch Report TIM.TF.T4 | TIM-CB42 | Circuit breaker | - | HV Circuit breaker | 110 | 3150 | 600.1556 | - | - | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | 446 | 84.9744 | 446 | 84.9744 | 900 | 171.473 | 600 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | - | 600.1556 | 600.1556 | 600.1556 | 84.9744 | 171.473 | 114.3154 | - | TIM_GXP84.9744126193291 | GXPTIM_GXP110446 | GXPTIM_GXP110446 | 84.9744 | 446 | 446 | 110 kV Bus | 11 kV Bus | Circuit breaker - TIM-CB42 - HV Circuit breaker | 110
GXPTIM_GXP110T4 | GXPTIM_GXPTIM-CB42110Protection | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 3 | TP Branch Report TIM.TF.T4 | TIM-CB42 | Circuit breaker | - | Protection | 110 | - | - | - | - | - | - | - | - | - | - | 1308 | 249.2075 | 1308 | 249.2075 | 1200 | 228.6307 | 600 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 249.2075 | 228.6307 | 114.3154 | - | TIM_GXP114.315353299546 | GXPTIM_GXP110600 | GXPTIM_GXP110600 | 114.3154 | 600 | 600 | 110 kV Bus | 11 kV Bus | Circuit breaker - TIM-CB42 - Protection | 110
GXPTIM_GXP110T4 | GXPTIM_GXPTIM-CB42110Current Transformer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 4 | TP Branch Report TIM.TF.T4 | TIM-CB42 | Circuit breaker | - | Current Transformer | 110 | 1250 | 238.157 | - | - | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | - | 238.157 | 238.157 | 238.157 | - | - | - | - | TIM_GXP238.156986040721 | GXPTIM_GXP1101250 | GXPTIM_GXP1101250 | 238.157 | 1250 | 1250 | 110 kV Bus | 11 kV Bus | Circuit breaker - TIM-CB42 - Current Transformer | 110
GXPTIM_GXP110T4 | GXPTIM_GXPTIM-CB42110Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 5 | TP Branch Report TIM.TF.T4 | TIM-CB42 | Transformer | - | Bushings | 110 | 2100 | 400.1037 | - | - | 2100 | 400.1037 | 2520 | 480.1245 | 2520 | 480.1245 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400.1037 | - | 400.1037 | 480.1245 | 480.1245 | - | - | - | - | TIM_GXP400.103736548411 | GXPTIM_GXP1102100 | GXPTIM_GXP1102100 | 400.1037 | 2100 | 2100 | 110 kV Bus | 11 kV Bus | Transformer - TIM-CB42 - Bushings | 110
GXPTIM_GXP110T4 | GXPTIM_GXPTIM.TF.T4110HV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 6 | TP Branch Report TIM.TF.T4 | TIM.TF.T4 | Transformer | - | HV Winding | 110 | 246.686 | 47 | - | - | - | - | 336 | 64.0166 | 323 | 61.5398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 64.0166 | 61.5398 | - | - | - | - | TIM_GXP61.5397651929222 | GXPTIM_GXP110323 | GXPTIM_GXP110246.686024108295 | 61.5398 | 323 | 246.686 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T4-HV Winding | 110
GXPTIM_GXP11T4 | GXPTIM_GXPTIM.TF.T411LV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 7 | TP Branch Report TIM.TF.T4 | TIM.TF.T4 | Transformer | - | LV Winding | 11 | 2466.8602 | 47 | - | - | - | - | 3228 | 61.5017 | 3364 | 64.0928 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 61.5017 | 64.0928 | - | - | - | - | TIM_GXP61.5016600751557 | GXPTIM_GXP113228 | GXPTIM_GXP112466.86024108295 | 61.5017 | 3228 | 2466.8602 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T4-LV Winding | 11
GXPTIM_GXP110T4 | GXPTIM_GXPTIM.TF.T4110Tap changer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 8 | TP Branch Report TIM.TF.T4 | TIM.TF.T4 | Transformer | - | Tap changer | 110 | 250 | 47.6314 | - | - | 250 | 47.6314 | 300 | 57.1577 | 300 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | - | 47.6314 | 57.1577 | 57.1577 | - | - | - | - | TIM_GXP47.6313972081441 | GXPTIM_GXP110250 | GXPTIM_GXP110250 | 47.6314 | 250 | 250 | 110 kV Bus | 11 kV Bus | Transformer - TIM.TF.T4 - Tap changer | 110
GXPTIM_GXP11T4 | GXPTIM_GXPTIM-CB284211Protection | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 9 | TP Branch Report TIM.TF.T4 | TIM-CB2842 | Circuit Breaker | Relay SEL 451-4 | Protection | 11 | 2500 | 47.6314 | - | - | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | 1544 | 29.4172 | - | - | 7200 | 137.1784 | 4800 | 91.4523 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | - | 47.6314 | 47.6314 | 47.6314 | 29.4172 | 137.1784 | 91.4523 | - | TIM_GXP29.4171509157498 | GXPTIM_GXP111544 | GXPTIM_GXP111544 | 29.4172 | 1544 | 1544 | 110 kV Bus | 11 kV Bus | Circuit Breaker-TIM-CB2842-Protection | 11
GXPTIM_GXP11T4 | GXPTIM_GXPTIM.TF.T411Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 10 | TP Branch Report TIM.TF.T4 | TIM.TF.T4 | Transformer | - | Bushings | 11 | 5000 | 95.2628 | - | - | 5000 | 95.2628 | 6000 | 114.3154 | 6000 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2628 | - | 95.2628 | 114.3154 | 114.3154 | - | - | - | - | TIM_GXP95.2627944162882 | GXPTIM_GXP115000 | GXPTIM_GXP115000 | 95.2628 | 5000 | 5000 | 110 kV Bus | 11 kV Bus | Transformer - TIM.TF.T4 - Bushings | 11
GXPTIM_GXP11T4 | GXPTIM_GXPTIM-CB2841-OEL11OEL | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 11 | TP Branch Report TIM.TF.T4 | TIM-CB2841-OEL | OEL | - | OEL | 11 | 2880 | 54.8714 | - | - | 2880 | 54.8714 | 2880 | 54.8714 | 2800 | 53.3472 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 54.8714 | - | 54.8714 | 54.8714 | 53.3472 | - | - | - | - | TIM_GXP53.3471648731214 | GXPTIM_GXP112800 | GXPTIM_GXP112800 | 53.3472 | 2800 | 2800 | 110 kV Bus | 11 kV Bus | OEL-TIM-CB2841-OEL-OEL | 11
GXPTIM_GXP11T4 | GXPTIM_GXPTIM-CBT4-CB284211Cable | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 12 | TP Branch Report TIM.TF.T4 | TIM-CBT4-CB2842 | Cable | - | Cable | 11 | 2708 | 51.5943 | 2598 | 49.4985 | 2534 | 48.2792 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2534 | 48.2792 | 51.5943 | 49.4985 | 48.2792 | - | - | - | - | - | 48.2792 | TIM_GXP48.2791842101749 | GXPTIM_GXP112534 | GXPTIM_GXP112534 | 48.2792 | 2534 | 2534 | 110 kV Bus | 11 kV Bus | Cable-TIM-CBT4-CB2842-Cable | 11
GXPTIM_GXP110T6 | GXPTIM_GXPTIM-DCB102110HV Circuit Breaker | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 1 | TP Branch Report TIM.TF.T6 | TIM-DCB102 | Circuit Breaker | - | HV Circuit Breaker | 110 | 3150 | 600.1556 | - | - | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | 446 | 84.9744 | 446 | 84.9744 | 900 | 171.473 | 600 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | - | 600.1556 | 600.1556 | 600.1556 | 84.9744 | 171.473 | 114.3154 | - | TIM_GXP84.9744126193291 | GXPTIM_GXP110446 | GXPTIM_GXP110446 | 84.9744 | 446 | 446 | 110 kV Bus | 11 kV Bus | Circuit Breaker-TIM-DCB102-HV Circuit Breaker | 110
GXPTIM_GXP110T6 | GXPTIM_GXPTIM-CT-CT102110Current Transformer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 2 | TP Branch Report TIM.TF.T6 | TIM-CT-CT102 | Circuit breaker | - | Current Transformer | 110 | 1250 | 238.157 | - | - | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | - | 238.157 | 238.157 | 238.157 | - | - | - | - | TIM_GXP238.156986040721 | GXPTIM_GXP1101250 | GXPTIM_GXP1101250 | 238.157 | 1250 | 1250 | 110 kV Bus | 11 kV Bus | Circuit breaker-TIM-CT-CT102-Current Transformer | 110
GXPTIM_GXP110T6 | GXPTIM_GXPTIM.TF.T6110Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 3 | TP Branch Report TIM.TF.T6 | TIM.TF.T6 | Transformer | - | Bushings | 110 | 2100 | 400.1037 | - | - | 2100 | 400.1037 | 2100 | 400.1037 | 2100 | 400.1037 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 400.1037 | - | 400.1037 | 400.1037 | 400.1037 | - | - | - | - | TIM_GXP400.103736548411 | GXPTIM_GXP1102100 | GXPTIM_GXP1102100 | 400.1037 | 2100 | 2100 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T6-Bushings | 110
GXPTIM_GXP110T6 | GXPTIM_GXPTIM.TF.T6110Tap Changer | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 4 | TP Branch Report TIM.TF.T6 | TIM.TF.T6 | Transformer | - | Tap Changer | 110 | 250 | 47.6314 | - | - | 250 | 47.6314 | 300 | 57.1577 | 300 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | - | 47.6314 | 57.1577 | 57.1577 | - | - | - | - | TIM_GXP47.6313972081441 | GXPTIM_GXP110250 | GXPTIM_GXP110250 | 47.6314 | 250 | 250 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T6-Tap Changer | 110
GXPTIM_GXP110T6 | GXPTIM_GXPTIM.TF.T6110HV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 5 | TP Branch Report TIM.TF.T6 | TIM.TF.T6 | Transformer | - | HV Winding | 110 | 246.686 | 47 | - | - | - | - | 336 | 64.0166 | 323 | 61.5398 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 64.0166 | 61.5398 | - | - | - | - | TIM_GXP61.5397651929222 | GXPTIM_GXP110323 | GXPTIM_GXP110246.686024108295 | 61.5398 | 323 | 246.686 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T6-HV Winding | 110
GXPTIM_GXP11T6 | GXPTIM_GXPTIM.TF.T611LV Winding | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 6 | TP Branch Report TIM.TF.T6 | TIM.TF.T6 | Transformer | - | LV Winding | 11 | 2466.8602 | 47 | - | - | - | - | 3364 | 64.0928 | 3228 | 61.5017 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 64.0928 | 61.5017 | - | - | - | - | TIM_GXP61.5016600751557 | GXPTIM_GXP113228 | GXPTIM_GXP112466.86024108295 | 61.5017 | 3228 | 2466.8602 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T6-LV Winding | 11
GXPTIM_GXP11T6 | GXPTIM_GXPTIM.TF.T611Bushings | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 7 | TP Branch Report TIM.TF.T6 | TIM.TF.T6 | Transformer | - | Bushings | 11 | 5000 | 95.2628 | - | - | 5000 | 95.2628 | 6000 | 114.3154 | 6000 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2628 | - | 95.2628 | 114.3154 | 114.3154 | - | - | - | - | TIM_GXP95.2627944162882 | GXPTIM_GXP115000 | GXPTIM_GXP115000 | 95.2628 | 5000 | 5000 | 110 kV Bus | 11 kV Bus | Transformer-TIM.TF.T6-Bushings | 11
GXPTIM_GXP11T6 | GXPTIM_GXPTIM-CB293211Protection | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 8 | TP Branch Report TIM.TF.T6 | TIM-CB2932 | Circuit Breaker | Relay SEL 451-5 | Protection | 11 | 2500 | 47.6314 | - | - | 2500 | 47.6314 | - | - | - | - | 1544 | 29.4172 | - | - | 7200 | 137.1784 | 4800 | 91.4523 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | - | 47.6314 | - | - | 29.4172 | 137.1784 | 91.4523 | - | TIM_GXP29.4171509157498 | GXPTIM_GXP111544 | GXPTIM_GXP111544 | 29.4172 | 1544 | 1544 | 110 kV Bus | 11 kV Bus | Circuit Breaker-TIM-CB2932-Protection | 11
GXPTIM_GXP11T6 | GXPTIM_GXPTIM-CB2932-OEL11OEL | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 9 | TP Branch Report TIM.TF.T6 | TIM-CB2932-OEL | OEL | - | OEL | 11 | 2880 | 54.8714 | - | - | 2880 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 54.8714 | - | 54.8714 | - | - | - | - | - | - | TIM_GXP54.871369583782 | GXPTIM_GXP112880 | GXPTIM_GXP112880 | 54.8714 | 2880 | 2880 | 110 kV Bus | 11 kV Bus | OEL-TIM-CB2932-OEL-OEL | 11
GXPTIM_GXP11T6 | GXPTIM_GXPTIM-CBL-T6-CB293211- | GXP | TIM_GXP | 110 kV Bus | 11 kV Bus | 10 | TP Branch Report TIM.TF.T6 | TIM-CBL-T6-CB2932 | Cable | - | - | 11 | 2708 | 51.5943 | 2598 | 49.4985 | 2534 | 48.2792 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2534 | 48.2792 | 51.5943 | 49.4985 | 48.2792 | - | - | - | - | - | 48.2792 | TIM_GXP48.2791842101749 | GXPTIM_GXP112534 | GXPTIM_GXP112534 | 48.2792 | 2534 | 2534 | 110 kV Bus | 11 kV Bus | Cable-TIM-CBL-T6-CB2932 | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_WaipopoTIM-CB266211Protection | DistributionFeeder | CB2662_Waipopo | 11 kV Bus | CB2662 | 1 | TP Branch Report TIM.FDR.2662\AEL Transformer database | TIM-CB2662 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2662_Waipopo7.62102355330306 | DistributionFeederCB2662_Waipopo11400 | DistributionFeederCB2662_Waipopo11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2662 | Circuit Breaker-TIM-CB2662-Protection | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_Waipopo3/1c 1000mm² Al XLPE CWS MDPE11- | DistributionFeeder | CB2662_Waipopo | CB2662 | Joint | 2 | GEMA | 3/1c 1000mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | CB2662_Waipopo11.2626534480134 | DistributionFeederCB2662_Waipopo11591.136 | DistributionFeederCB2662_Waipopo11591.136 | 11.2627 | 591.136 | 591.136 | CB2662 | Joint | Cable - 3/1c 1000mm² Al XLPE CWS MDPE | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_Waipopo3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2662_Waipopo | Joint | L904 | 3 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.82 | 418.5872 | 7.9752 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9752 | CB2662_Waipopo7.97515735198818 | DistributionFeederCB2662_Waipopo11418.587204 | DistributionFeederCB2662_Waipopo11418.587204 | 7.9752 | 418.5872 | 418.5872 | Joint | L904 | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_WaipopoRingmain unit11- | DistributionFeeder | CB2662_Waipopo | L904 | L905 | 4 | GEMA | Ringmain unit | RMU | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB2662_Waipopo12.0031120964523 | DistributionFeederCB2662_Waipopo11630 | DistributionFeederCB2662_Waipopo11630 | 12.0031 | 630 | 630 | L904 | L905 | RMU - Ringmain unit | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_Waipopo3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2662_Waipopo | L905 | Joint | 5 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.74 | 377.7494 | 7.1971 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.1971 | CB2662_Waipopo7.1970932200869 | DistributionFeederCB2662_Waipopo11377.749428 | DistributionFeederCB2662_Waipopo11377.749428 | 7.1971 | 377.7494 | 377.7494 | L905 | Joint | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_Waipopo3c 240mm² AL PILC11- | DistributionFeeder | CB2662_Waipopo | Joint | Joint | 6 | GEMA | 3c 240mm² AL PILC | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | Yes | 9.5 | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.86 | 276.287 | 5.264 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.264 | CB2662_Waipopo5.26397509828096 | DistributionFeederCB2662_Waipopo11276.28704 | DistributionFeederCB2662_Waipopo11276.28704 | 5.264 | 276.287 | 276.287 | Joint | Joint | Cable - 3c 240mm² AL PILC | 11
DistributionFeederCB2662_Waipopo11 | DistributionFeederCB2662_Waipopo3c 300mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2662_Waipopo | Joint | L1230 | 7 | GEMA | 3c 300mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | yes | 9 | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.86 | 381.196 | 7.2628 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.2628 | CB2662_Waipopo7.26275984574417 | DistributionFeederCB2662_Waipopo11381.196032 | DistributionFeederCB2662_Waipopo11381.196032 | 7.2628 | 381.196 | 381.196 | Joint | L1230 | Cable - 3c 300mm² AL XLPE HDPE Screened | 11
SubTransmissionTIM_WSS_SUBTRANS11 | SubTransmissionTIM_WSS_SUBTRANSTIM-CB266211Protection | SubTransmission | TIM_WSS_SUBTRANS | 11 kV Bus | CB2662 | 1 | TP Branch Report TIM.FDR.2662\AEL Transformer database | TIM-CB2662 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | TIM_WSS_SUBTRANS7.62102355330306 | SubTransmissionTIM_WSS_SUBTRANS11400 | SubTransmissionTIM_WSS_SUBTRANS11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2662 | Circuit Breaker-TIM-CB2662-Protection | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_WashdykeTIM-CB267211Protection | DistributionFeeder | CB2672_Washdyke | 11 kV Bus | CB2672 | 1 | TP Branch Report TIM.FDR.2672\AEL Transformer database | TIM-CB2672 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2672_Washdyke7.62102355330306 | DistributionFeederCB2672_Washdyke11400 | DistributionFeederCB2672_Washdyke11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2672 | Circuit Breaker-TIM-CB2672-Protection | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_Washdyke3/1c 1000mm² Al XLPE CWS MDPE11- | DistributionFeeder | CB2672_Washdyke | CB2672 | Joint | 3 | GEMA | 3/1c 1000mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | CB2672_Washdyke11.2626534480134 | DistributionFeederCB2672_Washdyke11591.136 | DistributionFeederCB2672_Washdyke11591.136 | 11.2627 | 591.136 | 591.136 | CB2672 | Joint | Cable - 3/1c 1000mm² Al XLPE CWS MDPE | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_Washdyke3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2672_Washdyke | Joint | L910 | 2 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.82 | 418.5872 | 7.9752 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9752 | CB2672_Washdyke7.97515735198818 | DistributionFeederCB2672_Washdyke11418.587204 | DistributionFeederCB2672_Washdyke11418.587204 | 7.9752 | 418.5872 | 418.5872 | Joint | L910 | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_WashdykeRingmain unit11- | DistributionFeeder | CB2672_Washdyke | L910 | L912 | 4 | GEMA | Ringmain unit | RMU | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB2672_Washdyke12.0031120964523 | DistributionFeederCB2672_Washdyke11630 | DistributionFeederCB2672_Washdyke11630 | 12.0031 | 630 | 630 | L910 | L912 | RMU - Ringmain unit | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_Washdyke3c 240mm² AL PILC11- | DistributionFeeder | CB2672_Washdyke | L912 | LX25 | 5 | GEMA | 3c 240mm² AL PILC | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.86 | 276.287 | 5.264 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.264 | CB2672_Washdyke5.26397509828096 | DistributionFeederCB2672_Washdyke11276.28704 | DistributionFeederCB2672_Washdyke11276.28704 | 5.264 | 276.287 | 276.287 | L912 | LX25 | Cable - 3c 240mm² AL PILC | 11
DistributionFeederCB2672_Washdyke11 | DistributionFeederCB2672_WashdykeWeke11- | DistributionFeeder | CB2672_Washdyke | LX25 | B1110 | 6 | GEMA | Weke | OH Line | - | - | 11 | 277 | 5.2776 | 277 | 5.2776 | 277 | 5.2776 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.2776 | 5.2776 | 5.2776 | - | - | - | - | - | - | CB2672_Washdyke5.27755881066237 | DistributionFeederCB2672_Washdyke11277 | DistributionFeederCB2672_Washdyke11277 | 5.2776 | 277 | 277 | LX25 | B1110 | OH Line - Weke | 11
SubTransmissionTIM_WSS_SUBTRANS11 | SubTransmissionTIM_WSS_SUBTRANSTIM-CB267211Protection | SubTransmission | TIM_WSS_SUBTRANS | 11 kV Bus | CB2672 | 1 | TP Branch Report TIM.FDR.2672\AEL Transformer database | TIM-CB2672 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | TIM_WSS_SUBTRANS7.62102355330306 | SubTransmissionTIM_WSS_SUBTRANS11400 | SubTransmissionTIM_WSS_SUBTRANS11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2672 | Circuit Breaker-TIM-CB2672-Protection | 11
DistributionFeederCB2682_Showgrounds Hill11 | DistributionFeederCB2682_Showgrounds HillTIM-CB268211Protection | DistributionFeeder | CB2682_Showgrounds Hill | 11 kV Bus | CB2682 | 1 | TP Branch Report TIM.FDR.2682\AEL Transformer database | TIM-CB2682 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2682_Showgrounds Hill7.62102355330306 | DistributionFeederCB2682_Showgrounds Hill11400 | DistributionFeederCB2682_Showgrounds Hill11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2682 | Circuit Breaker-TIM-CB2682-Protection | 11
DistributionFeederCB2682_Showgrounds Hill11 | DistributionFeederCB2682_Showgrounds Hill3x 1c 400mm2 Al XLPE HDPE11- | DistributionFeeder | CB2682_Showgrounds Hill | CB2682 | L1080 | 1 | TP Branch Report TIM.FDR.2682 | 3x 1c 400mm2 Al XLPE HDPE | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | - | CB2682_Showgrounds Hill6.57313281472389 | DistributionFeederCB2682_Showgrounds Hill11345 | DistributionFeederCB2682_Showgrounds Hill11345 | 6.5731 | 345 | 345 | CB2682 | L1080 | Cable-3x 1c 400mm2 Al XLPE HDPE | 11
SubTransmissionCB2692_North ST.111 | SubTransmissionCB2692_North ST.1TIM-CB269211Protection | SubTransmission | CB2692_North ST.1 | 11 kV Bus | CB2692 | 1 | TP Branch Report TIM.FDR.2692\AEL Transformer database | TIM-CB2692 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1184 | 22.5582 | 1184 | 22.5582 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 22.5582 | 45.7261 | 30.4841 | - | CB2692_North ST.122.5582297177771 | SubTransmissionCB2692_North ST.1111184 | SubTransmissionCB2692_North ST.1111184 | 22.5582 | 1184 | 1184 | 11 kV Bus | CB2692 | Circuit Breaker-TIM-CB2692-Protection | 11
SubTransmissionCB2692_North ST.111 | SubTransmissionCB2692_North ST.13/1c 1200mm² Al XLPE CWS MDPE11- | SubTransmission | CB2692_North ST.1 | CB2692 | NST35 | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 1200mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 1025 | 19.5289 | 1025 | 19.5289 | 1025 | 19.5289 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 5632.6 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.6 | 0.9 | 806.265 | 15.3614 | 19.5289 | 19.5289 | 19.5289 | - | - | - | - | - | 15.3614 | CB2692_North ST.115.3614113880097 | SubTransmissionCB2692_North ST.111806.265 | SubTransmissionCB2692_North ST.111806.265 | 15.3614 | 806.265 | 806.265 | CB2692 | NST35 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANSTIM-CB269211Protection | SubTransmission | TIM_NST_SUBTRANS | 11 kV Bus | CB2692 | 1 | TP Branch Report TIM.FDR.2692\AEL Transformer database | TIM-CB2692 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1184 | 22.5582 | 1083 | 20.6339 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 22.5582 | 45.7261 | 30.4841 | - | TIM_NST_SUBTRANS22.5582297177771 | SubTransmissionTIM_NST_SUBTRANS111184 | SubTransmissionTIM_NST_SUBTRANS111083 | 22.5582 | 1184 | 1083 | 11 kV Bus | CB2692 | Circuit Breaker-TIM-CB2692-Protection | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANS3/1c 1200mm² Al XLPE CWS MDPE11- | SubTransmission | TIM_NST_SUBTRANS | CB2692 | NST35 | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 1200mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 1025 | 19.5289 | 1025 | 19.5289 | 1025 | 19.5289 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 5632.6 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.6 | 0.9 | 806.265 | 15.3614 | 19.5289 | 19.5289 | 19.5289 | - | - | - | - | - | 15.3614 | TIM_NST_SUBTRANS15.3614113880097 | SubTransmissionTIM_NST_SUBTRANS11806.265 | SubTransmissionTIM_NST_SUBTRANS11806.265 | 15.3614 | 806.265 | 806.265 | CB2692 | NST35 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans RdTIM-CB270211Protection | DistributionFeeder | CB2702_Morgans Rd | 11 kV Bus | CB2702 | 1 | TP Branch Report TIM.FDR.2702\AEL Transformer database | TIM-CB2702 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2702_Morgans Rd7.62102355330306 | DistributionFeederCB2702_Morgans Rd11400 | DistributionFeederCB2702_Morgans Rd11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2702 | Circuit Breaker-TIM-CB2702-Protection | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans Rd3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2702_Morgans Rd | CB2702 | L650 Link | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 99.3 | 1.1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 376.0826 | 7.1653 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.1653 | CB2702_Morgans Rd7.16533550041746 | DistributionFeederCB2702_Morgans Rd11376.08258 | DistributionFeederCB2702_Morgans Rd11376.08258 | 7.1653 | 376.0826 | 376.0826 | CB2702 | L650 Link | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans RdJAGUAR11- | DistributionFeeder | CB2702_Morgans Rd | L650 Link | L651 ABS | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11 | 387 | 7.3733 | 387 | 7.3733 | 387 | 7.3733 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1762.1 | - | - | - | - | - | - | - | - | - | - | - | 7.3733 | 7.3733 | 7.3733 | - | - | - | - | - | - | CB2702_Morgans Rd7.37334028782071 | DistributionFeederCB2702_Morgans Rd11387 | DistributionFeederCB2702_Morgans Rd11387 | 7.3733 | 387 | 387 | L650 Link | L651 ABS | OH Line-JAGUAR | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans Rd3c 185mm² Al XLPE HDPE11- | DistributionFeeder | CB2702_Morgans Rd | Pole 35185 | Pole 35229 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 185mm² Al XLPE HDPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 104.1 | 1.1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 260.4067 | 4.9614 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 4.9614 | CB2702_Morgans Rd4.96141369955643 | DistributionFeederCB2702_Morgans Rd11260.406685 | DistributionFeederCB2702_Morgans Rd11260.406685 | 4.9614 | 260.4067 | 260.4067 | Pole 35185 | Pole 35229 | Cable-3c 185mm² Al XLPE HDPE | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans RdWeke11- | DistributionFeeder | CB2702_Morgans Rd | Pole 35229 | Pole 35233 | 5 | GEMA/AEL OH Amp Calc. | Weke | OH Line | - | - | 11 | 277 | 5.2776 | 277 | 5.2776 | 277 | 5.2776 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.2776 | 5.2776 | 5.2776 | - | - | - | - | - | - | CB2702_Morgans Rd5.27755881066237 | DistributionFeederCB2702_Morgans Rd11277 | DistributionFeederCB2702_Morgans Rd11277 | 5.2776 | 277 | 277 | Pole 35229 | Pole 35233 | OH Line-Weke | 11
DistributionFeederCB2702_Morgans Rd11 | DistributionFeederCB2702_Morgans Rd3c 150mm² Al PILC STA11- | DistributionFeeder | CB2702_Morgans Rd | Pole 35233 | Joint | 6 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 150mm² Al PILC STA | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 150 | 1.1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 188.0321 | 3.5825 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5825 | CB2702_Morgans Rd3.58249218087862 | DistributionFeederCB2702_Morgans Rd11188.032075 | DistributionFeederCB2702_Morgans Rd11188.032075 | 3.5825 | 188.0321 | 188.0321 | Pole 35233 | Joint | Cable-3c 150mm² Al PILC STA | 11
DistributionFeederCB2712_Mountain View Rd11 | DistributionFeederCB2712_Mountain View RdTIM-CB271211Protection | DistributionFeeder | CB2712_Mountain View Rd | 11 kV Bus | CB2712 | 1 | TP Branch Report TIM.FDR.2712\AEL Transformer database | TIM-CB2712 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2712_Mountain View Rd7.62102355330306 | DistributionFeederCB2712_Mountain View Rd11400 | DistributionFeederCB2712_Mountain View Rd11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2712 | Circuit Breaker-TIM-CB2712-Protection | 11
DistributionFeederCB2712_Mountain View Rd11 | DistributionFeederCB2712_Mountain View Rd3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2712_Mountain View Rd | CB2712 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 650 | 12.3842 | 650 | 12.3842 | 650 | 12.3842 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 58.4 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.82 | 475.969 | 9.0684 | 12.3842 | 12.3842 | 12.3842 | - | - | - | - | - | 9.0684 | CB2712_Mountain View Rd9.06842739910526 | DistributionFeederCB2712_Mountain View Rd11475.969 | DistributionFeederCB2712_Mountain View Rd11475.969 | 9.0684 | 475.969 | 475.969 | CB2712 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2712_Mountain View Rd11 | DistributionFeederCB2712_Mountain View Rd3c 300mm² Al XLPE MDPE11- | DistributionFeeder | CB2712_Mountain View Rd | Joint | ABS L978 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 300mm² Al XLPE MDPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 662 | 1.4 | 0.95 | 18.5 | 0.97 | 1.2 | 1 | 3 | 0.45 | 0.84 | 368.4526 | 7.02 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.02 | CB2712_Mountain View Rd7.01996409508702 | DistributionFeederCB2712_Mountain View Rd11368.45256 | DistributionFeederCB2712_Mountain View Rd11368.45256 | 7.02 | 368.4526 | 368.4526 | Joint | ABS L978 | Cable-3c 300mm² Al XLPE MDPE | 11
SubTransmissionCB2732_ATM_T111 | SubTransmissionCB2732_ATM_T1TIM-CB273211Protection | SubTransmission | CB2732_ATM_T1 | 11 kV Bus | CB2732 | 1 | TP Branch Report TIM.FDR.2732\AEL Transformer database | TIM-CB2732 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1068 | 20.3481 | 976 | 18.5953 | 3600 | 68.5892 | 2400 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.3481 | 68.5892 | 45.7261 | - | CB2732_ATM_T120.3481328873192 | SubTransmissionCB2732_ATM_T1111068 | SubTransmissionCB2732_ATM_T111976 | 20.3481 | 1068 | 976 | 11 kV Bus | CB2732 | Circuit Breaker-TIM-CB2732-Protection | 11
SubTransmissionCB2732_ATM_T111 | SubTransmissionCB2732_ATM_T12 x 3/1c 630mm² Cu 11- | SubTransmission | CB2732_ATM_T1 | CB2732 | B774/T1 | 2 | AEL DWG 11422 | 2 x 3/1c 630mm² Cu | Cable | - | - | 11 | 1600 | 30.4841 | 1600 | 30.4841 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | 2 x 3/1c | - | 87.2 | 1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 1120.544 | 21.3492 | 30.4841 | 30.4841 | 30.4841 | - | - | - | - | - | 21.3492 | CB2732_ATM_T121.3492305412811 | SubTransmissionCB2732_ATM_T1111120.544 | SubTransmissionCB2732_ATM_T1111120.544 | 21.3492 | 1120.544 | 1120.544 | CB2732 | B774/T1 | Cable-2 x 3/1c 630mm² Cu | 11
DistributionFeederCB2742_Levels Plain11 | DistributionFeederCB2742_Levels PlainTIM-CB274211Protection | DistributionFeeder | CB2742_Levels Plain | 11 kV Bus | CB2742 | 1 | TP Branch Report TIM.FDR.2742\AEL Transformer database | TIM-CB2742 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2742_Levels Plain7.62102355330306 | DistributionFeederCB2742_Levels Plain11400 | DistributionFeederCB2742_Levels Plain11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2742 | Circuit Breaker-TIM-CB2742-Protection | 11
DistributionFeederCB2742_Levels Plain11 | DistributionFeederCB2742_Levels Plain3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2742_Levels Plain | CB2742 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 89.3 | 1.2 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.3 | 0.85 | 416.2824 | 7.9312 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9312 | CB2742_Levels Plain7.93124493806381 | DistributionFeederCB2742_Levels Plain11416.2824 | DistributionFeederCB2742_Levels Plain11416.2824 | 7.9312 | 416.2824 | 416.2824 | CB2742 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2742_Levels Plain11 | DistributionFeederCB2742_Levels Plain3c 300mm² Al XLPE MDPE11- | DistributionFeeder | CB2742_Levels Plain | Joint | ABS L767 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 300mm² Al XLPE MDPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 2553.1 | 1.2 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.89 | 394.4936 | 7.5161 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.5161 | CB2742_Levels Plain7.5161119333864 | DistributionFeederCB2742_Levels Plain11394.493568 | DistributionFeederCB2742_Levels Plain11394.493568 | 7.5161 | 394.4936 | 394.4936 | Joint | ABS L767 | Cable-3c 300mm² Al XLPE MDPE | 11
DistributionFeederCB2762_AEL Yard11 | DistributionFeederCB2762_AEL YardTIM-CB276211Protection | DistributionFeeder | CB2762_AEL Yard | 11 kV Bus | CB2762 | 1 | TP Branch Report TIM.FDR.2762\AEL Transformer database | TIM-CB2762 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2762_AEL Yard7.62102355330306 | DistributionFeederCB2762_AEL Yard11400 | DistributionFeederCB2762_AEL Yard11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2762 | Circuit Breaker-TIM-CB2762-Protection | 11
DistributionFeederCB2762_AEL Yard11 | DistributionFeederCB2762_AEL Yard3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2762_AEL Yard | CB2762 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 85.5 | 1.18 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.81 | 396.6926 | 7.558 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.558 | CB2762_AEL Yard7.55800988215493 | DistributionFeederCB2762_AEL Yard11396.69264 | DistributionFeederCB2762_AEL Yard11396.69264 | 7.558 | 396.6926 | 396.6926 | CB2762 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2762_AEL Yard11 | DistributionFeederCB2762_AEL Yard3c 240mm² AL PILC STA11- | DistributionFeeder | CB2762_AEL Yard | Joint | ABS L516 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 240mm² AL PILC STA | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 2404.3 | 1.18 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.45 | 0.89 | 280.0296 | 5.3353 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.3353 | CB2762_AEL Yard5.33528044305509 | DistributionFeederCB2762_AEL Yard11280.0296 | DistributionFeederCB2762_AEL Yard11280.0296 | 5.3353 | 280.0296 | 280.0296 | Joint | ABS L516 | Cable-3c 240mm² AL PILC STA | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANSTIM-CB277211Protection | SubTransmission | TIM_GRM_SUBTRANS | 11 kV Bus | CB2772 | 1 | TP Branch Report TIM.FDR.2772\AEL Transformer database | TIM-CB2772 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRM_SUBTRANS11.4315353299546 | SubTransmissionTIM_GRM_SUBTRANS11600 | SubTransmissionTIM_GRM_SUBTRANS11549 | 11.4315 | 600 | 549 | 11 kV Bus | CB2772 | Circuit Breaker-TIM-CB2772-Protection | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | CB2772 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 79.3 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2772 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | TEGRASMERE19 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1790.7 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRM_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | TEGRASMERE19 | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANSTIM-CB281211Protection | SubTransmission | TIM_GRM_SUBTRANS | 11 kV Bus | CB2812 | 1 | TP Branch Report TIM.FDR.2812\AEL Transformer database | TIM-CB2812 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 810 | 15.4326 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 15.4326 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRM_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRM_SUBTRANS11550 | SubTransmissionTIM_GRM_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2812 | Circuit Breaker-TIM-CB2812-Protection | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | CB2812 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 84.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2812 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 1782.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRM_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | TEGRASMERE14 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 8.2 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE14 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANSTIM-CB282211Protection | SubTransmission | TIM_GRM_SUBTRANS | 11 kV Bus | CB2822 | 1 | TP Branch Report TIM.FDR.2822\AEL Transformer database | TIM-CB2822 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRM_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRM_SUBTRANS11550 | SubTransmissionTIM_GRM_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2822 | Circuit Breaker-TIM-CB2822-Protection | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | CB2822 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 81.1 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2822 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1906.4 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRM_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | TEGRASMERE8 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 19.6 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE8 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMD_SUBTRANS11 | SubTransmissionTIM_GRMD_SUBTRANSTIM-CB277211Protection | SubTransmission | TIM_GRMD_SUBTRANS | 11 kV Bus | CB2772 | 1 | TP Branch Report TIM.FDR.2772\AEL Transformer database | TIM-CB2772 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRMD_SUBTRANS11.4315353299546 | SubTransmissionTIM_GRMD_SUBTRANS11600 | SubTransmissionTIM_GRMD_SUBTRANS11549 | 11.4315 | 600 | 549 | 11 kV Bus | CB2772 | Circuit Breaker-TIM-CB2772-Protection | 11
SubTransmissionTIM_GRMD_SUBTRANS11 | SubTransmissionTIM_GRMD_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMD_SUBTRANS | CB2772 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 79.3 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMD_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMD_SUBTRANS11607.5972 | SubTransmissionTIM_GRMD_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2772 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMD_SUBTRANS11 | SubTransmissionTIM_GRMD_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRMD_SUBTRANS | Joint | TEGRASMERE19 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1790.7 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRMD_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRMD_SUBTRANS11412.566 | SubTransmissionTIM_GRMD_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | TEGRASMERE19 | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRMC_SUBTRANS11 | SubTransmissionTIM_GRMC_SUBTRANSTIM-CB281211Protection | SubTransmission | TIM_GRMC_SUBTRANS | 11 kV Bus | CB2812 | 1 | TP Branch Report TIM.FDR.2812\AEL Transformer database | TIM-CB2812 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 810 | 15.4326 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 15.4326 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRMC_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRMC_SUBTRANS11550 | SubTransmissionTIM_GRMC_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2812 | Circuit Breaker-TIM-CB2812-Protection | 11
SubTransmissionTIM_GRMC_SUBTRANS11 | SubTransmissionTIM_GRMC_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMC_SUBTRANS | CB2812 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 84.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMC_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMC_SUBTRANS11607.5972 | SubTransmissionTIM_GRMC_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2812 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMC_SUBTRANS11 | SubTransmissionTIM_GRMC_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRMC_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 1782.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRMC_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRMC_SUBTRANS11412.566 | SubTransmissionTIM_GRMC_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRMC_SUBTRANS11 | SubTransmissionTIM_GRMC_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMC_SUBTRANS | Joint | TEGRASMERE14 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 8.2 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMC_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMC_SUBTRANS11607.5972 | SubTransmissionTIM_GRMC_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE14 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMB_SUBTRANS11 | SubTransmissionTIM_GRMB_SUBTRANSTIM-CB282211Protection | SubTransmission | TIM_GRMB_SUBTRANS | 11 kV Bus | CB2822 | 1 | TP Branch Report TIM.FDR.2822\AEL Transformer database | TIM-CB2822 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRMB_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRMB_SUBTRANS11550 | SubTransmissionTIM_GRMB_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2822 | Circuit Breaker-TIM-CB2822-Protection | 11
SubTransmissionTIM_GRMB_SUBTRANS11 | SubTransmissionTIM_GRMB_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMB_SUBTRANS | CB2822 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 81.1 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMB_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMB_SUBTRANS11607.5972 | SubTransmissionTIM_GRMB_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2822 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMB_SUBTRANS11 | SubTransmissionTIM_GRMB_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRMB_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1906.4 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRMB_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRMB_SUBTRANS11412.566 | SubTransmissionTIM_GRMB_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRMB_SUBTRANS11 | SubTransmissionTIM_GRMB_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMB_SUBTRANS | Joint | TEGRASMERE8 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 19.6 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMB_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMB_SUBTRANS11607.5972 | SubTransmissionTIM_GRMB_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE8 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
DistributionFeederCB2832_Grants Rd11 | DistributionFeederCB2832_Grants RdTIM-CB283211Protection | DistributionFeeder | CB2832_Grants Rd | 11 kV Bus | CB2832 | 1 | TP Branch Report TIM.FDR.2832\AEL Transformer database | TIM-CB2832 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2832_Grants Rd7.62102355330306 | DistributionFeederCB2832_Grants Rd11400 | DistributionFeederCB2832_Grants Rd11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2832 | Circuit Breaker-TIM-CB2832-Protection | 11
DistributionFeederCB2832_Grants Rd11 | DistributionFeederCB2832_Grants Rd3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2832_Grants Rd | CB2832 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 49 | 1.18 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.81 | 406.296 | 7.741 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.741 | CB2832_Grants Rd7.74097846403205 | DistributionFeederCB2832_Grants Rd11406.296 | DistributionFeederCB2832_Grants Rd11406.296 | 7.741 | 406.296 | 406.296 | CB2832 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2832_Grants Rd11 | DistributionFeederCB2832_Grants Rd3c 240mm² AL PILC STA11- | DistributionFeeder | CB2832_Grants Rd | Joint | L773 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 240mm² AL PILC STA | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 367.9 | 1.18 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.6 | 0.89 | 280.0296 | 5.3353 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.3353 | CB2832_Grants Rd5.33528044305509 | DistributionFeederCB2832_Grants Rd11280.0296 | DistributionFeederCB2832_Grants Rd11280.0296 | 5.3353 | 280.0296 | 280.0296 | Joint | L773 | Cable-3c 240mm² AL PILC STA | 11
DistributionFeederCB2852_Hadlow11 | DistributionFeederCB2852_HadlowTIM-CB285211Protection | DistributionFeeder | CB2852_Hadlow | 11 kV Bus | CB2852 | 1 | TP Branch Report TIM.FDR.2852\AEL Transformer database | TIM-CB2852 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2852_Hadlow7.62102355330306 | DistributionFeederCB2852_Hadlow11400 | DistributionFeederCB2852_Hadlow11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2852 | Circuit Breaker-TIM-CB2852-Protection | 11
DistributionFeederCB2852_Hadlow11 | DistributionFeederCB2852_Hadlow3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2852_Hadlow | CB2852 | L800 | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 110.3 | 1.1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 385.187 | 7.3388 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.3388 | CB2852_Hadlow7.33879799856536 | DistributionFeederCB2852_Hadlow11385.187 | DistributionFeederCB2852_Hadlow11385.187 | 7.3388 | 385.187 | 385.187 | CB2852 | L800 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2852_Hadlow11 | DistributionFeederCB2852_HadlowJAGUAR11- | DistributionFeeder | CB2852_Hadlow | L800 | L801 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11 | 523.1348 | 9.9671 | 550 | 10.4789 | 386.9283 | 7.372 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1762.1 | - | - | - | - | - | - | - | - | - | - | - | 9.9671 | 10.4789 | 7.372 | - | - | - | - | - | - | CB2852_Hadlow7.37197367771845 | DistributionFeederCB2852_Hadlow11386.92827157178 | DistributionFeederCB2852_Hadlow11386.92827157178 | 7.372 | 386.9283 | 386.9283 | L800 | L801 | OH Line-JAGUAR | 11
DistributionFeederCB2852_Hadlow11 | DistributionFeederCB2852_HadlowJAGUAR11- | DistributionFeeder | CB2852_Hadlow | L801 | Pole 25185 | 4 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11 | 523.1348 | 9.9671 | 550 | 10.4789 | 386.9283 | 7.372 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16.5 | - | - | - | - | - | - | - | - | - | - | - | 9.9671 | 10.4789 | 7.372 | - | - | - | - | - | - | CB2852_Hadlow7.37197367771845 | DistributionFeederCB2852_Hadlow11386.92827157178 | DistributionFeederCB2852_Hadlow11386.92827157178 | 7.372 | 386.9283 | 386.9283 | L801 | Pole 25185 | OH Line-JAGUAR | 11
DistributionFeederCB2852_Hadlow11 | DistributionFeederCB2852_Hadlow3c 185mm² Al XLPE HDPE11- | DistributionFeeder | CB2852_Hadlow | Pole 25185 | Pole 35228 | 5 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 185mm² Al XLPE HDPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 104.1 | 1.1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 260.4067 | 4.9614 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 4.9614 | CB2852_Hadlow4.96141369955643 | DistributionFeederCB2852_Hadlow11260.406685 | DistributionFeederCB2852_Hadlow11260.406685 | 4.9614 | 260.4067 | 260.4067 | Pole 25185 | Pole 35228 | Cable-3c 185mm² Al XLPE HDPE | 11
DistributionFeederCB2862_Meadows Rd11 | DistributionFeederCB2862_Meadows RdTIM-CB286211Protection | DistributionFeeder | CB2862_Meadows Rd | 11 kV Bus | CB2862 | 1 | TP Branch Report TIM.FDR.2862\AEL Transformer database | TIM-CB2862 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2862_Meadows Rd7.62102355330306 | DistributionFeederCB2862_Meadows Rd11400 | DistributionFeederCB2862_Meadows Rd11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2862 | Circuit Breaker-TIM-CB2862-Protection | 11
DistributionFeederCB2862_Meadows Rd11 | DistributionFeederCB2862_Meadows Rd3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2862_Meadows Rd | CB2862 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 645 | 12.2889 | 645 | 12.2889 | 645 | 12.2889 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 72.1 | 1.18 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.81 | 476.4744 | 9.0781 | 12.2889 | 12.2889 | 12.2889 | - | - | - | - | - | 9.0781 | CB2862_Meadows Rd9.07805656236486 | DistributionFeederCB2862_Meadows Rd11476.4744 | DistributionFeederCB2862_Meadows Rd11476.4744 | 9.0781 | 476.4744 | 476.4744 | CB2862 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2862_Meadows Rd11 | DistributionFeederCB2862_Meadows Rd3c 300mm² Al XLPE HDPE11- | DistributionFeeder | CB2862_Meadows Rd | Joint | RMU L420 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 300mm² Al XLPE HDPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 2221.4 | 1.18 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 3 | 0.45 | 0.89 | 394.4936 | 7.5161 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.5161 | CB2862_Meadows Rd7.5161119333864 | DistributionFeederCB2862_Meadows Rd11394.493568 | DistributionFeederCB2862_Meadows Rd11394.493568 | 7.5161 | 394.4936 | 394.4936 | Joint | RMU L420 | Cable-3c 300mm² Al XLPE HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANSTIM-CB291211Protection | SubTransmission | TIM_GRM_SUBTRANS | 11 kV Bus | CB2912 | 1 | TP Branch Report TIM.FDR.2912\AEL Transformer database | TIM-CB2912 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRM_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRM_SUBTRANS11550 | SubTransmissionTIM_GRM_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2912 | Circuit Breaker-TIM-CB2912-Protection | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | CB2912 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 86.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2912 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1755.45 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRM_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | SubTransmissionTIM_GRM_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRM_SUBTRANS11 | SubTransmissionTIM_GRM_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRM_SUBTRANS | Joint | TEGRASMERE3 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRM_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | SubTransmissionTIM_GRM_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE3 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMA_SUBTRANS11 | SubTransmissionTIM_GRMA_SUBTRANSTIM-CB291211Protection | SubTransmission | TIM_GRMA_SUBTRANS | 11 kV Bus | CB2912 | 1 | TP Branch Report TIM.FDR.2912\AEL Transformer database | TIM-CB2912 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | 600 | 11.4315 | 549 | 10.4599 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10.4789 | 10.4789 | 10.4789 | - | - | 11.4315 | 45.7261 | 30.4841 | - | TIM_GRMA_SUBTRANS10.4789073857917 | SubTransmissionTIM_GRMA_SUBTRANS11550 | SubTransmissionTIM_GRMA_SUBTRANS11549 | 10.4789 | 550 | 549 | 11 kV Bus | CB2912 | Circuit Breaker-TIM-CB2912-Protection | 11
SubTransmissionTIM_GRMA_SUBTRANS11 | SubTransmissionTIM_GRMA_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMA_SUBTRANS | CB2912 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 86.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMA_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMA_SUBTRANS11607.5972 | SubTransmissionTIM_GRMA_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | CB2912 | Joint | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionTIM_GRMA_SUBTRANS11 | SubTransmissionTIM_GRMA_SUBTRANS3c 400mm² Cu PILC SWA11- | SubTransmission | TIM_GRMA_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 400mm² Cu PILC SWA | Cable | - | - | 11 | 550 | 10.4789 | 550 | 10.4789 | 550 | 10.4789 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1755.45 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 412.566 | 7.8604 | 10.4789 | 10.4789 | 10.4789 | - | - | - | - | - | 7.8604 | TIM_GRMA_SUBTRANS7.86043800823007 | SubTransmissionTIM_GRMA_SUBTRANS11412.566 | SubTransmissionTIM_GRMA_SUBTRANS11412.566 | 7.8604 | 412.566 | 412.566 | Joint | Joint | Cable-3c 400mm² Cu PILC SWA | 11
SubTransmissionTIM_GRMA_SUBTRANS11 | SubTransmissionTIM_GRMA_SUBTRANS3/1c 630mm² XLPE Cu CWS PVC HDPE11- | SubTransmission | TIM_GRMA_SUBTRANS | Joint | TEGRASMERE3 | 4 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 630mm² XLPE Cu CWS PVC HDPE | Cable | - | - | 11 | 810 | 15.4326 | 810 | 15.4326 | 810 | 15.4326 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20.5 | 1.4 | 0.94 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.45 | 0.84 | 607.5972 | 11.5763 | 15.4326 | 15.4326 | 15.4326 | - | - | - | - | - | 11.5763 | TIM_GRMA_SUBTRANS11.5762814303025 | SubTransmissionTIM_GRMA_SUBTRANS11607.5972 | SubTransmissionTIM_GRMA_SUBTRANS11607.5972 | 11.5763 | 607.5972 | 607.5972 | Joint | TEGRASMERE3 | Cable-3/1c 630mm² XLPE Cu CWS PVC HDPE | 11
SubTransmissionCB2922_ATM_T211 | SubTransmissionCB2922_ATM_T2TIM-CB292211Protection | SubTransmission | CB2922_ATM_T2 | 11 kV Bus | CB2922 | 1 | TP Branch Report TIM.FDR.2922\AEL Transformer database | TIM-CB2922 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1068 | 20.3481 | 976 | 18.5953 | 3600 | 68.5892 | 2400 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.3481 | 68.5892 | 45.7261 | - | CB2922_ATM_T220.3481328873192 | SubTransmissionCB2922_ATM_T2111068 | SubTransmissionCB2922_ATM_T211976 | 20.3481 | 1068 | 976 | 11 kV Bus | CB2922 | Circuit Breaker-TIM-CB2922-Protection | 11
SubTransmissionCB2922_ATM_T211 | SubTransmissionCB2922_ATM_T22 x 3/1c 630mm² Cu 11- | SubTransmission | CB2922_ATM_T2 | CB2922 | B774/T2 | 2 | AEL DWG 11422 | 2 x 3/1c 630mm² Cu | Cable | - | - | 11 | 1600 | 30.4841 | 1600 | 30.4841 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | 2 x 3/1c | - | 96.9 | 1 | 0.97 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 1120.544 | 21.3492 | 30.4841 | 30.4841 | 30.4841 | - | - | - | - | - | 21.3492 | CB2922_ATM_T221.3492305412811 | SubTransmissionCB2922_ATM_T2111120.544 | SubTransmissionCB2922_ATM_T2111120.544 | 21.3492 | 1120.544 | 1120.544 | CB2922 | B774/T2 | Cable-2 x 3/1c 630mm² Cu | 11
DistributionFeederCB2942_Old North Rd11 | DistributionFeederCB2942_Old North RdTIM-CB294211Protection | DistributionFeeder | CB2942_Old North Rd | 11 kV Bus | CB2942 | 1 | TP Branch Report TIM.FDR.2942\AEL Transformer database | TIM-CB2942 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2942_Old North Rd7.62102355330306 | DistributionFeederCB2942_Old North Rd11400 | DistributionFeederCB2942_Old North Rd11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2942 | Circuit Breaker-TIM-CB2942-Protection | 11
DistributionFeederCB2942_Old North Rd11 | DistributionFeederCB2942_Old North Rd3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2942_Old North Rd | CB2942 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 44.1 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.45 | 0.89 | 417.7108 | 7.9585 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9585 | CB2942_Old North Rd7.95845999422384 | DistributionFeederCB2942_Old North Rd11417.71082 | DistributionFeederCB2942_Old North Rd11417.71082 | 7.9585 | 417.7108 | 417.7108 | CB2942 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2942_Old North Rd11 | DistributionFeederCB2942_Old North Rd3c 0.4in² Al PILC SWA11- | DistributionFeeder | CB2942_Old North Rd | Joint | L462 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 0.4in² Al PILC SWA | Cable | - | - | 11 | 361 | 6.878 | 361 | 6.878 | 361 | 6.878 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 753.9 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.45 | 0.89 | 280.8075 | 5.3501 | 6.878 | 6.878 | 6.878 | - | - | - | - | - | 5.3501 | CB2942_Old North Rd5.35010066650802 | DistributionFeederCB2942_Old North Rd11280.80746 | DistributionFeederCB2942_Old North Rd11280.80746 | 5.3501 | 280.8075 | 280.8075 | Joint | L462 | Cable-3c 0.4in² Al PILC SWA | 11
DistributionFeederCB2952_Highfield11 | DistributionFeederCB2952_HighfieldTIM-CB295211Protection | DistributionFeeder | CB2952_Highfield | 11 kV Bus | CB2952 | 1 | TP Branch Report TIM.FDR.2952\AEL Transformer database | TIM-CB2952 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2952_Highfield7.62102355330306 | DistributionFeederCB2952_Highfield11400 | DistributionFeederCB2952_Highfield11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2952 | Circuit Breaker-TIM-CB2952-Protection | 11
DistributionFeederCB2952_Highfield11 | DistributionFeederCB2952_Highfield3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2952_Highfield | CB2952 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 42 | 1.2 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.3 | 0.85 | 416.2824 | 7.9312 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9312 | CB2952_Highfield7.93124493806381 | DistributionFeederCB2952_Highfield11416.2824 | DistributionFeederCB2952_Highfield11416.2824 | 7.9312 | 416.2824 | 416.2824 | CB2952 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2952_Highfield11 | DistributionFeederCB2952_Highfield3c 240mm² Al PILC STA11- | DistributionFeeder | CB2952_Highfield | Joint | RMU L549 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 240mm² Al PILC STA | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 155.3 | 1.2 | 0.96 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.3 | 0.89 | 280.0296 | 5.3353 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.3353 | CB2952_Highfield5.33528044305509 | DistributionFeederCB2952_Highfield11280.0296 | DistributionFeederCB2952_Highfield11280.0296 | 5.3353 | 280.0296 | 280.0296 | Joint | RMU L549 | Cable-3c 240mm² Al PILC STA | 11
DistributionFeederCB2972_Smithfield11 | DistributionFeederCB2972_SmithfieldTIM-CB297211Protection | DistributionFeeder | CB2972_Smithfield | 11 kV Bus | CB2972 | 1 | TP Branch Report TIM.FDR.2972\AEL Transformer database | TIM-CB2972 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2972_Smithfield7.62102355330306 | DistributionFeederCB2972_Smithfield11400 | DistributionFeederCB2972_Smithfield11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2972 | Circuit Breaker-TIM-CB2972-Protection | 11
DistributionFeederCB2972_Smithfield11 | DistributionFeederCB2972_Smithfield3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB2972_Smithfield | CB2972 | Joint | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 40.6 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.45 | 0.88 | 413.0174 | 7.869 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.869 | CB2972_Smithfield7.86903909541233 | DistributionFeederCB2972_Smithfield11413.01744 | DistributionFeederCB2972_Smithfield11413.01744 | 7.869 | 413.0174 | 413.0174 | CB2972 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB2972_Smithfield11 | DistributionFeederCB2972_Smithfield3c 0.4in² Al PILC SWA11- | DistributionFeeder | CB2972_Smithfield | Joint | L461 | 3 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3c 0.4in² Al PILC SWA | Cable | - | - | 11 | 361 | 6.878 | 361 | 6.878 | 361 | 6.878 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 394.5 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.45 | 0.89 | 280.8075 | 5.3501 | 6.878 | 6.878 | 6.878 | - | - | - | - | - | 5.3501 | CB2972_Smithfield5.35010066650802 | DistributionFeederCB2972_Smithfield11280.80746 | DistributionFeederCB2972_Smithfield11280.80746 | 5.3501 | 280.8075 | 280.8075 | Joint | L461 | Cable-3c 0.4in² Al PILC SWA | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANSTIM-CB298211Protection | SubTransmission | TIM_NST_SUBTRANS | 11 kV Bus | CB2982 | 1 | TP Branch Report TIM.FDR.2982\AEL Transformer database | TIM-CB2982 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1184 | 22.5582 | 1083 | 20.6339 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 22.5582 | 45.7261 | 30.4841 | - | TIM_NST_SUBTRANS22.5582297177771 | SubTransmissionTIM_NST_SUBTRANS111184 | SubTransmissionTIM_NST_SUBTRANS111083 | 22.5582 | 1184 | 1083 | 11 kV Bus | CB2982 | Circuit Breaker-TIM-CB2982-Protection | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANS3/1c 1200mm² Al XLPE CWS MDPE11- | SubTransmission | TIM_NST_SUBTRANS | CB2982 | NST36 | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 1200mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 1025 | 19.5289 | 1025 | 19.5289 | 1025 | 19.5289 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 5903.8 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.6 | 0.9 | 806.265 | 15.3614 | 19.5289 | 19.5289 | 19.5289 | - | - | - | - | - | 15.3614 | TIM_NST_SUBTRANS15.3614113880097 | SubTransmissionTIM_NST_SUBTRANS11806.265 | SubTransmissionTIM_NST_SUBTRANS11806.265 | 15.3614 | 806.265 | 806.265 | CB2982 | NST36 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11
SubTransmissionCB2982_North ST.211 | SubTransmissionCB2982_North ST.2TIM-CB298211Protection | SubTransmission | CB2982_North ST.2 | 11 kV Bus | CB2982 | 1 | TP Branch Report TIM.FDR.2982\AEL Transformer database | TIM-CB2982 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1184 | 22.5582 | 1184 | 22.5582 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 22.5582 | 45.7261 | 30.4841 | - | CB2982_North ST.222.5582297177771 | SubTransmissionCB2982_North ST.2111184 | SubTransmissionCB2982_North ST.2111184 | 22.5582 | 1184 | 1184 | 11 kV Bus | CB2982 | Circuit Breaker-TIM-CB2982-Protection | 11
SubTransmissionCB2982_North ST.211 | SubTransmissionCB2982_North ST.23/1c 1200mm² Al XLPE CWS MDPE11- | SubTransmission | CB2982_North ST.2 | CB2982 | NST36 | 2 | GEMA\General Cable\TIM Scada alarms report Rev4 | 3/1c 1200mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 1025 | 19.5289 | 1025 | 19.5289 | 1025 | 19.5289 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 5903.8 | 1.8 | 0.92 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.6 | 0.9 | 806.265 | 15.3614 | 19.5289 | 19.5289 | 19.5289 | - | - | - | - | - | 15.3614 | CB2982_North ST.215.3614113880097 | SubTransmissionCB2982_North ST.211806.265 | SubTransmissionCB2982_North ST.211806.265 | 15.3614 | 806.265 | 806.265 | CB2982 | NST36 | Cable-3/1c 1200mm² Al XLPE CWS MDPE | 11
DistributionFeederCB2992_Goulds Road11 | DistributionFeederCB2992_Goulds RoadTIM-CB299211Protection | DistributionFeeder | CB2992_Goulds Road | 11 kV Bus | CB2992 | 1 | TP Branch Report TIM.FDR.2992\AEL Transformer database | TIM-CB2992 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB2992_Goulds Road7.62102355330306 | DistributionFeederCB2992_Goulds Road11400 | DistributionFeederCB2992_Goulds Road11366 | 7.621 | 400 | 366 | 11 kV Bus | CB2992 | Circuit Breaker-TIM-CB2992-Protection | 11
DistributionFeederCB2992_Goulds Road11 | DistributionFeederCB2992_Goulds RoadTIM-CB299211- | DistributionFeeder | CB2992_Goulds Road | CB2992 | L1075 | 1 | TP Branch Report TIM.FDR.2992 | TIM-CB2992 | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | - | CB2992_Goulds Road6.57313281472389 | DistributionFeederCB2992_Goulds Road11345 | DistributionFeederCB2992_Goulds Road11345 | 6.5731 | 345 | 345 | CB2992 | L1075 | Cable-TIM-CB2992 | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_ElginshireTIM-CB301211Protection | DistributionFeeder | CB3002_Elginshire | 11 kV Bus | CB3002 | 1 | TP Branch Report TIM.FDR.3012\AEL Transformer database | TIM-CB3012 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB3002_Elginshire7.62102355330306 | DistributionFeederCB3002_Elginshire11400 | DistributionFeederCB3002_Elginshire11366 | 7.621 | 400 | 366 | 11 kV Bus | CB3002 | Circuit Breaker-TIM-CB3012-Protection | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3/1c 1000mm² Al XLPE CWS MDPE11- | DistributionFeeder | CB3002_Elginshire | CB3002 | Joint | 2 | GEMA | 3/1c 1000mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | CB3002_Elginshire11.2626534480134 | DistributionFeederCB3002_Elginshire11591.136 | DistributionFeederCB3002_Elginshire11591.136 | 11.2627 | 591.136 | 591.136 | CB3002 | Joint | Cable - 3/1c 1000mm² Al XLPE CWS MDPE | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3002_Elginshire | Joint | L969 | 3 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.82 | 418.5872 | 7.9752 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9752 | CB3002_Elginshire7.97515735198818 | DistributionFeederCB3002_Elginshire11418.587204 | DistributionFeederCB3002_Elginshire11418.587204 | 7.9752 | 418.5872 | 418.5872 | Joint | L969 | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_ElginshireRingmain unit11- | DistributionFeeder | CB3002_Elginshire | L969 | L967 | 4 | GEMA | Ringmain unit | RMU | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB3002_Elginshire12.0031120964523 | DistributionFeederCB3002_Elginshire11630 | DistributionFeederCB3002_Elginshire11630 | 12.0031 | 630 | 630 | L969 | L967 | RMU - Ringmain unit | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3002_Elginshire | L967 | Joint | 5 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.82 | 418.5872 | 7.9752 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9752 | CB3002_Elginshire7.97515735198818 | DistributionFeederCB3002_Elginshire11418.587204 | DistributionFeederCB3002_Elginshire11418.587204 | 7.9752 | 418.5872 | 418.5872 | L967 | Joint | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3c 300mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3002_Elginshire | Joint | L868 | 6 | GEMA | 3c 300mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | yes | 9 | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.86 | 381.196 | 7.2628 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.2628 | CB3002_Elginshire7.26275984574417 | DistributionFeederCB3002_Elginshire11381.196032 | DistributionFeederCB3002_Elginshire11381.196032 | 7.2628 | 381.196 | 381.196 | Joint | L868 | Cable - 3c 300mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_ElginshireRingmain unit11 | DistributionFeeder | CB3002_Elginshire | L868 | L867 | 7 | GEME | Ringmain unit | RMU |  |  | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB3002_Elginshire12.0031120964523 | DistributionFeederCB3002_Elginshire11630 | DistributionFeederCB3002_Elginshire11630 | 12.0031 | 630 | 630 | L868 | L867 | RMU - Ringmain unit - | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3c 300mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3002_Elginshire | L876 | Joint | 8 | GEMA | 3c 300mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 9 | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.86 | 381.196 | 7.2628 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.2628 | CB3002_Elginshire7.26275984574417 | DistributionFeederCB3002_Elginshire11381.196032 | DistributionFeederCB3002_Elginshire11381.196032 | 7.2628 | 381.196 | 381.196 | L876 | Joint | Cable - 3c 300mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3002_Elginshire11 | DistributionFeederCB3002_Elginshire3c 240mm² AL PILC11- | DistributionFeeder | CB3002_Elginshire | Joint | B1541 | 9 | GEMA | 3c 240mm² AL PILC | Cable | - | - | 11 | 288 | 5.4871 | 288 | 5.4871 | 288 | 5.4871 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | Yes | 64 | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0 | 0.88 | 236.0033 | 4.4965 | 5.4871 | 5.4871 | 5.4871 | - | - | - | - | - | 4.4965 | CB3002_Elginshire4.49646730336477 | DistributionFeederCB3002_Elginshire11236.003328 | DistributionFeederCB3002_Elginshire11236.003328 | 4.4965 | 236.0033 | 236.0033 | Joint | B1541 | Cable - 3c 240mm² AL PILC | 11
SubTransmissionTIM_WSS_SUBTRANS11 | SubTransmissionTIM_WSS_SUBTRANSTIM-CB300211Protection | SubTransmission | TIM_WSS_SUBTRANS | 11 kV Bus | CB3002 | 1 | TP Branch Report TIM.FDR.3002\AEL Transformer database | TIM-CB3002 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | TIM_WSS_SUBTRANS7.62102355330306 | SubTransmissionTIM_WSS_SUBTRANS11400 | SubTransmissionTIM_WSS_SUBTRANS11366 | 7.621 | 400 | 366 | 11 kV Bus | CB3002 | Circuit Breaker-TIM-CB3002-Protection | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_ArowhenuaTIM-CB301211Protection | DistributionFeeder | CB3012_Arowhenua | 11 kV Bus | CB3012 | 1 | TP Branch Report TIM.FDR.3012\AEL Transformer database | TIM-CB3012 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | CB3012_Arowhenua7.62102355330306 | DistributionFeederCB3012_Arowhenua11400 | DistributionFeederCB3012_Arowhenua11366 | 7.621 | 400 | 366 | 11 kV Bus | CB3012 | Circuit Breaker-TIM-CB3012-Protection | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3/1c 1000mm² Al XLPE CWS MDPE11- | DistributionFeeder | CB3012_Arowhenua | CB3012 | Joint | 2 | GEMA | 3/1c 1000mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | CB3012_Arowhenua11.2626534480134 | DistributionFeederCB3012_Arowhenua11591.136 | DistributionFeederCB3012_Arowhenua11591.136 | 11.2627 | 591.136 | 591.136 | CB3012 | Joint | Cable - 3/1c 1000mm² Al XLPE CWS MDPE | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3012_Arowhenua | Joint | L901 | 3 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.82 | 418.5872 | 7.9752 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.9752 | CB3012_Arowhenua7.97515735198818 | DistributionFeederCB3012_Arowhenua11418.587204 | DistributionFeederCB3012_Arowhenua11418.587204 | 7.9752 | 418.5872 | 418.5872 | Joint | L901 | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_ArowhenuaRingmain unit11- | DistributionFeeder | CB3012_Arowhenua | L901 | L900 | 4 | GEMA | Ringmain unit | RMU | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB3012_Arowhenua12.0031120964523 | DistributionFeederCB3012_Arowhenua11630 | DistributionFeederCB3012_Arowhenua11630 | 12.0031 | 630 | 630 | L901 | L900 | RMU - Ringmain unit | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3/1c 400mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3012_Arowhenua | L900 | Joint | 5 | GEMA | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | - | 0.9 | 0.98 | 18.5 | 0.97 | 1.2 | 1 | 4 | 0.3 | 0.92 | 469.6344 | 8.9477 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.9477 | CB3012_Arowhenua8.94773751686479 | DistributionFeederCB3012_Arowhenua11469.634424 | DistributionFeederCB3012_Arowhenua11469.634424 | 8.9477 | 469.6344 | 469.6344 | L900 | Joint | Cable - 3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3c 300mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3012_Arowhenua | Joint | L873 | 6 | GEMA | 3c 300mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.8 | 354.601 | 6.7561 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.7561 | CB3012_Arowhenua6.75605567045969 | DistributionFeederCB3012_Arowhenua11354.60096 | DistributionFeederCB3012_Arowhenua11354.60096 | 6.7561 | 354.601 | 354.601 | Joint | L873 | Cable - 3c 300mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3c 300mm² AL XLPE HDPE Screened11- | DistributionFeeder | CB3012_Arowhenua | L872 | Joint | 7 | GEMA | 3c 300mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.8 | 354.601 | 6.7561 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.7561 | CB3012_Arowhenua6.75605567045969 | DistributionFeederCB3012_Arowhenua11354.60096 | DistributionFeederCB3012_Arowhenua11354.60096 | 6.7561 | 354.601 | 354.601 | L872 | Joint | Cable - 3c 300mm² AL XLPE HDPE Screened | 11
DistributionFeederCB3012_Arowhenua11 | DistributionFeederCB3012_Arowhenua3c 150mm² Al PILC STA11- | DistributionFeeder | CB3012_Arowhenua | Joint | L357 | 7 | GEMA | 3c 150mm² Al PILC STA | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 0.96 | 18.5 | 0.97 | 1.2 | 1 | 2 | 0.3 | 0.8 | 197.4144 | 3.7612 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.7612 | CB3012_Arowhenua3.76124948040298 | DistributionFeederCB3012_Arowhenua11197.4144 | DistributionFeederCB3012_Arowhenua11197.4144 | 3.7612 | 197.4144 | 197.4144 | Joint | L357 | Cable - 3c 150mm² Al PILC STA | 11
SubTransmissionTIM_WSS_SUBTRANS11 | SubTransmissionTIM_WSS_SUBTRANSTIM-CB301211Protection | SubTransmission | TIM_WSS_SUBTRANS | 11 kV Bus | CB3012 | 1 | TP Branch Report TIM.FDR.3012\AEL Transformer database | TIM-CB3012 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | 366 | 6.9732 | 2400 | 45.7261 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 45.7261 | 30.4841 | - | TIM_WSS_SUBTRANS7.62102355330306 | SubTransmissionTIM_WSS_SUBTRANS11400 | SubTransmissionTIM_WSS_SUBTRANS11366 | 7.621 | 400 | 366 | 11 kV Bus | CB3012 | Circuit Breaker-TIM-CB3012-Protection | 11
--- | ----- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | --- | --- |  |  |  | - | - | --- | -
DistributionFeederCB2_White St11 | DistributionFeederCB2_White StGRM-CB211Protection | DistributionFeeder | CB2_White St | 11 kV Bus | TEGRASMERE2 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB2 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB2_White St5.79197790051033 | DistributionFeederCB2_White St11304 | DistributionFeederCB2_White St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE2 | Circuit Breaker-GRM-CB2-Protection | 11
DistributionFeederCB2_White St11 | DistributionFeederCB2_White St3c 300mm² AL XLPE11- | DistributionFeeder | CB2_White St | TEGRASMERE2 | Joint | 2 | GEMA\General Cable | 3c 300mm² AL XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 88 | 0.78 | 1 | 18.5 | 0.97 | 1.2 | 1 | 3 | 0.26 | 0.8 | 369.376 | 7.0376 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.0376 | CB2_White St7.03755799006218 | DistributionFeederCB2_White St11369.376 | DistributionFeederCB2_White St11369.376 | 7.0376 | 369.376 | 369.376 | TEGRASMERE2 | Joint | Cable-3c 300mm² AL XLPE | 11
DistributionFeederCB2_White St11 | DistributionFeederCB2_White St3c 0.25in² Cu PILC STAS11- | DistributionFeeder | CB2_White St | Joint | Joint | 3 | GEMA\General Cable | 3c 0.25in² Cu PILC STAS | Cable | - | - | 11 | 315 | 6.0016 | 315 | 6.0016 | 315 | 6.0016 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 204.6 | 0.78 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0 | 0.69 | 206.4825 | 3.934 | 6.0016 | 6.0016 | 6.0016 | - | - | - | - | - | 3.934 | CB2_White St3.93401998961225 | DistributionFeederCB2_White St11206.4825 | DistributionFeederCB2_White St11206.4825 | 3.934 | 206.4825 | 206.4825 | Joint | Joint | Cable-3c 0.25in² Cu PILC STAS | 11
DistributionFeederCB2_White St11 | DistributionFeederCB2_White St3c 0.15in² Cu PILC STAS11- | DistributionFeeder | CB2_White St | Joint | Joint | 4 | GEMA\General Cable | 3c 0.15in² Cu PILC STAS | Cable | - | - | 11 | 245 | 4.6679 | 245 | 4.6679 | 245 | 4.6679 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 174.4 | 0.78 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0 | 0.69 | 160.5975 | 3.0598 | 4.6679 | 4.6679 | 4.6679 | - | - | - | - | - | 3.0598 | CB2_White St3.05979332525397 | DistributionFeederCB2_White St11160.5975 | DistributionFeederCB2_White St11160.5975 | 3.0598 | 160.5975 | 160.5975 | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11
DistributionFeederCB2_White St11 | DistributionFeederCB2_White St3c 185mm² Al PILC HDPE11- | DistributionFeeder | CB2_White St | Joint | TE64 | 5 | GEMA\General Cable | 3c 185mm² Al PILC HDPE | Cable | - | - | 11 | 253 | 4.8203 | 253 | 4.8203 | 253 | 4.8203 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 7.2 | 0.78 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.26 | 0.8 | 192.28 | 3.6634 | 4.8203 | 4.8203 | 4.8203 | - | - | - | - | - | 3.6634 | CB2_White St3.66342602207278 | DistributionFeederCB2_White St11192.28 | DistributionFeederCB2_White St11192.28 | 3.6634 | 192.28 | 192.28 | Joint | TE64 | Cable-3c 185mm² Al PILC HDPE | 11
SubTransmissionCB4_GRM-HNT A11 | SubTransmissionCB4_GRM-HNT AGRM-CB411Protection | SubTransmission | CB4_GRM-HNT A | 11 kV Bus | TEGRASMERE4 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB4 | Circuit Breaker | Relay SEL 311L | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | CB4_GRM-HNT A7.62102355330306 | SubTransmissionCB4_GRM-HNT A11400 | SubTransmissionCB4_GRM-HNT A11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE4 | Circuit Breaker-GRM-CB4-Protection | 11
SubTransmissionCB4_GRM-HNT A11 | SubTransmissionCB4_GRM-HNT A3c 0.3in² Cu PILC SWA 11- | SubTransmission | CB4_GRM-HNT A | TEGRASMERE 4 | TEHUNT3 | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWA | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1629.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB4_GRM-HNT A5.66745037564935 | SubTransmissionCB4_GRM-HNT A11297.464 | SubTransmissionCB4_GRM-HNT A11297.464 | 5.6675 | 297.464 | 297.464 | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANSGRM-CB411Protection | SubTransmission | GRM_HNT_SUBTRANS | 11 kV Bus | TEGRASMERE4 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB4 | Circuit Breaker | Relay SEL 311L | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_HNT_SUBTRANS7.62102355330306 | SubTransmissionGRM_HNT_SUBTRANS11400 | SubTransmissionGRM_HNT_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE4 | Circuit Breaker-GRM-CB4-Protection | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANS3c 0.3in² Cu PILC SWA 11- | SubTransmission | GRM_HNT_SUBTRANS | TEGRASMERE 4 | TEHUNT3 | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWA | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1629.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | GRM_HNT_SUBTRANS5.66745037564935 | SubTransmissionGRM_HNT_SUBTRANS11297.464 | SubTransmissionGRM_HNT_SUBTRANS11297.464 | 5.6675 | 297.464 | 297.464 | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11
DistributionFeederCB5_Nile St11 | DistributionFeederCB5_Nile StGRM-CB511Protection | DistributionFeeder | CB5_Nile St | 11 kV Bus | TEGRASMERE5 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB5 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB5_Nile St5.79197790051033 | DistributionFeederCB5_Nile St11304 | DistributionFeederCB5_Nile St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE5 | Circuit Breaker-GRM-CB5-Protection | 11
DistributionFeederCB5_Nile St11 | DistributionFeederCB5_Nile St3c 300mm² Al PILC SWAS11- | DistributionFeeder | CB5_Nile St | TEGRASMERE5 | TEE1 RMU | 2 | GEMA\General Cable | 3c 300mm² Al PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 504.4 | 0.77 | 1 | 18.5 | 0.95 | 1.2 | 1 | 6 | 0.11 | 0.63 | 233.415 | 4.4472 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 4.4472 | CB5_Nile St4.44715303173558 | DistributionFeederCB5_Nile St11233.415 | DistributionFeederCB5_Nile St11233.415 | 4.4472 | 233.415 | 233.415 | TEGRASMERE5 | TEE1 RMU | Cable-3c 300mm² Al PILC SWAS | 11
DistributionFeederCB6_Parkview Terrace11 | DistributionFeederCB6_Parkview TerraceGRM-CB611Protection | DistributionFeeder | CB6_Parkview Terrace | 11 kV Bus | TEGRASMERE6 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB6 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB6_Parkview Terrace5.79197790051033 | DistributionFeederCB6_Parkview Terrace11304 | DistributionFeederCB6_Parkview Terrace11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE6 | Circuit Breaker-GRM-CB6-Protection | 11
DistributionFeederCB6_Parkview Terrace11 | DistributionFeederCB6_Parkview Terrace3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB6_Parkview Terrace | TEGRASMERE6 | TER1RMU | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 2342.2 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 228 | 4.344 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.344 | CB6_Parkview Terrace4.34398342538274 | DistributionFeederCB6_Parkview Terrace11228 | DistributionFeederCB6_Parkview Terrace11228 | 4.344 | 228 | 228 | TEGRASMERE6 | TER1RMU | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB7_Douglas St11 | DistributionFeederCB7_Douglas StGRM-CB711Protection | DistributionFeeder | CB7_Douglas St | 11 kV Bus | TEGRASMERE7 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB7 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB7_Douglas St5.79197790051033 | DistributionFeederCB7_Douglas St11304 | DistributionFeederCB7_Douglas St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE7 | Circuit Breaker-GRM-CB7-Protection | 11
DistributionFeederCB7_Douglas St11 | DistributionFeederCB7_Douglas St3c 0.4in² Cu PILC STAS 11- | DistributionFeeder | CB7_Douglas St | TEGRASMERE7 | Joint | 2 | GEMA\General Cable | 3c 0.4in² Cu PILC STAS | Cable | - | - | 11 | 435 | 8.2879 | 435 | 8.2879 | 435 | 8.2879 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 66 | 0.75 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.76 | 314.07 | 5.9838 | 8.2879 | 8.2879 | 8.2879 | - | - | - | - | - | 5.9838 | CB7_Douglas St5.98383716846473 | DistributionFeederCB7_Douglas St11314.07 | DistributionFeederCB7_Douglas St11314.07 | 5.9838 | 314.07 | 314.07 | TEGRASMERE7 | Joint | Cable-3c 0.4in² Cu PILC STAS | 11
DistributionFeederCB7_Douglas St11 | DistributionFeederCB7_Douglas St3c 300mm² Al PILC SWAS11- | DistributionFeeder | CB7_Douglas St | Joint | Joint | 3 | GEMA\General Cable | 3c 300mm² Al PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 117.4 | 0.75 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.76 | 281.58 | 5.3648 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 5.3648 | CB7_Douglas St5.36481953034769 | DistributionFeederCB7_Douglas St11281.58 | DistributionFeederCB7_Douglas St11281.58 | 5.3648 | 281.58 | 281.58 | Joint | Joint | Cable-3c 300mm² Al PILC SWAS | 11
DistributionFeederCB7_Douglas St11 | DistributionFeederCB7_Douglas St3c 185mm² Al XLPE HDPE11- | DistributionFeeder | CB7_Douglas St | Joint | TEF13 RMU | 4 | GEMA\General Cable | 3c 185mm² Al XLPE HDPE | Cable | - | - | 11 | 320 | 6.0968 | 320 | 6.0968 | 320 | 6.0968 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 281.2 | 0.75 | 1 | 18.5 | 0.97 | 1.2 | 1 | 3 | 0.3 | 0.76 | 235.904 | 4.4946 | 6.0968 | 6.0968 | 6.0968 | - | - | - | - | - | 4.4946 | CB7_Douglas St4.49457485079601 | DistributionFeederCB7_Douglas St11235.904 | DistributionFeederCB7_Douglas St11235.904 | 4.4946 | 235.904 | 235.904 | Joint | TEF13 RMU | Cable-3c 185mm² Al XLPE HDPE | 11
SubTransmissionCB9_GRM-NST A11 | SubTransmissionCB9_GRM-NST AGRM-CB911Protection | SubTransmission | CB9_GRM-NST A | 11 kV Bus | TEGRASMERE9 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB9 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | 7.621 | 15.242 | 15.242 | - | CB9_GRM-NST A7.62102355330306 | SubTransmissionCB9_GRM-NST A11400 | SubTransmissionCB9_GRM-NST A11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE9 | Circuit Breaker-GRM-CB9-Protection | 11
SubTransmissionCB9_GRM-NST A11 | SubTransmissionCB9_GRM-NST A3c 400mm² AL11- | SubTransmission | CB9_GRM-NST A | TEGRASMERE9 | Joint | 2 | GEMA\General Cable | 3c 400mm² AL | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 7.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB9_GRM-NST A8.00900224137816 | SubTransmissionCB9_GRM-NST A11420.3636 | SubTransmissionCB9_GRM-NST A11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE9 | Joint | Cable-3c 400mm² AL | 11
SubTransmissionCB9_GRM-NST A11 | SubTransmissionCB9_GRM-NST A3c 0.3in² Cu PILC STAS11- | SubTransmission | CB9_GRM-NST A | Joint | Joint | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC STAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 3032.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB9_GRM-NST A5.66745037564935 | SubTransmissionCB9_GRM-NST A11297.464 | SubTransmissionCB9_GRM-NST A11297.464 | 5.6675 | 297.464 | 297.464 | Joint | Joint | Cable-3c 0.3in² Cu PILC STAS | 11
SubTransmissionCB9_GRM-NST A11 | SubTransmissionCB9_GRM-NST A3/1c 400mm² AL XLPE HDPE Screened11- | SubTransmission | CB9_GRM-NST A | Joint | NST06 | 4 | GEMA\General Cable | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 66.8 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB9_GRM-NST A8.00900224137816 | SubTransmissionCB9_GRM-NST A11420.3636 | SubTransmissionCB9_GRM-NST A11420.3636 | 8.009 | 420.3636 | 420.3636 | Joint | NST06 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANSGRM-CB911Protection | SubTransmission | GRM_HNT_SUBTRANS | 11 kV Bus | TEGRASMERE9 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB9 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_HNT_SUBTRANS7.62102355330306 | SubTransmissionGRM_HNT_SUBTRANS11400 | SubTransmissionGRM_HNT_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE9 | Circuit Breaker-GRM-CB9-Protection | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3c 400mm² AL11- | SubTransmission | GRM_NST_SUBTRANS | TEGRASMERE9 | Joint | 2 | GEMA\General Cable | 3c 400mm² AL | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 7.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | GRM_NST_SUBTRANS8.00900224137816 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE9 | Joint | Cable-3c 400mm² AL | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3c 0.3in² Cu PILC STAS11- | SubTransmission | GRM_NST_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC STAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 3032.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | GRM_NST_SUBTRANS5.66745037564935 | SubTransmissionGRM_NST_SUBTRANS11297.464 | SubTransmissionGRM_NST_SUBTRANS11297.464 | 5.6675 | 297.464 | 297.464 | Joint | Joint | Cable-3c 0.3in² Cu PILC STAS | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3/1c 400mm² AL XLPE HDPE Screened11- | SubTransmission | GRM_NST_SUBTRANS | Joint | NST06 | 4 | GEMA\General Cable | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 66.8 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | GRM_NST_SUBTRANS8.00900224137816 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | 8.009 | 420.3636 | 420.3636 | Joint | NST06 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB10_Ashbury Park11 | DistributionFeederCB10_Ashbury ParkGRM-CB1011Protection | DistributionFeeder | CB10_Ashbury Park | 11 kV Bus | TEGRASMERE10 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB10 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB10_Ashbury Park5.79197790051033 | DistributionFeederCB10_Ashbury Park11304 | DistributionFeederCB10_Ashbury Park11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE10 | Circuit Breaker-GRM-CB10-Protection | 11
DistributionFeederCB10_Ashbury Park11 | DistributionFeederCB10_Ashbury Park3c 0.4in² Al PILC STAS11- | DistributionFeeder | CB10_Ashbury Park | TEGRASMERE10 | Joint | 2 | GEMA\General Cable | 3c 0.4in² Al PILC STAS | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 547.8 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 262.2 | 4.9956 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 4.9956 | CB10_Ashbury Park4.99558093919016 | DistributionFeederCB10_Ashbury Park11262.2 | DistributionFeederCB10_Ashbury Park11262.2 | 4.9956 | 262.2 | 262.2 | TEGRASMERE10 | Joint | Cable-3c 0.4in² Al PILC STAS | 11
DistributionFeederCB10_Ashbury Park11 | DistributionFeederCB10_Ashbury Park3c 0.25in² Al PILC STAS11- | DistributionFeeder | CB10_Ashbury Park | Joint | Joint | 3 | GEMA\General Cable | 3c 0.25in² Al PILC STAS | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 155.3 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 201.4 | 3.8372 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.8372 | CB10_Ashbury Park3.83718535908809 | DistributionFeederCB10_Ashbury Park11201.4 | DistributionFeederCB10_Ashbury Park11201.4 | 3.8372 | 201.4 | 201.4 | Joint | Joint | Cable-3c 0.25in² Al PILC STAS | 11
DistributionFeederCB10_Ashbury Park11 | DistributionFeederCB10_Ashbury Park3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB10_Ashbury Park | Joint | TEM1 RMU | 4 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 47 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 228 | 4.344 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.344 | CB10_Ashbury Park4.34398342538274 | DistributionFeederCB10_Ashbury Park11228 | DistributionFeederCB10_Ashbury Park11228 | 4.344 | 228 | 228 | Joint | TEM1 RMU | Cable-3c 185mm² Al PILC SWAS | 11
ZoneSubstationGRM11 | ZoneSubstationGRM11 kV Switchboard11- | ZoneSubstation | GRM | 11 kV Bus | 11 kV Bus |  | GEMA\TECH 1 | 11 kV Switchboard | Switchboard | - | - | 11 | 3000 | 57.1577 | 3000 | 57.1577 | 3000 | 57.1577 | - | - | - | - | 3000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 57.1577 | 57.1577 | 57.1577 | - | - | 57.1577 | - | - | - | GRM57.1576766497729 | ZoneSubstationGRM113000 | ZoneSubstationGRM113000 | 57.1577 | 3000 | 3000 | 11 kV Bus | 11 kV Bus | Switchboard - 11 kV Switchboard | 11
SubTransmissionGRM11 | SubTransmissionGRMGRM-CB3111Protection | SubTransmission | GRM | TEGRASMERE31 | TEGRASMERE32 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB31 | Circuit Breaker | Relay SEL 751A | Protection | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GRM | SubTransmissionGRM11 | SubTransmissionGRM11 |  |  |  | TEGRASMERE31 | TEGRASMERE32 | Circuit Breaker-GRM-CB31-Protection | 11
DistributionFeederCB12_Selwyn St11 | DistributionFeederCB12_Selwyn StGRM-CB1211Protection | DistributionFeeder | CB12_Selwyn St | 11 kV Bus | TEGRASMERE12 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB12 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB12_Selwyn St5.79197790051033 | DistributionFeederCB12_Selwyn St11304 | DistributionFeederCB12_Selwyn St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE12 | Circuit Breaker-GRM-CB12-Protection | 11
DistributionFeederCB12_Selwyn St11 | DistributionFeederCB12_Selwyn St3c 300mm² Al XLPE PVC11- | DistributionFeeder | CB12_Selwyn St | TEGRASMERE12 | Joint | 2 | GEMA\General Cable | 3c 300mm² Al XLPE PVC | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 1.05 | 0.99 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0 | 0.63 | 224.3075 | 4.2736 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 4.2736 | CB12_Selwyn St4.27363124202443 | DistributionFeederCB12_Selwyn St11224.307468 | DistributionFeederCB12_Selwyn St11224.307468 | 4.2736 | 224.3075 | 224.3075 | TEGRASMERE12 | Joint | Cable-3c 300mm² Al XLPE PVC | 11
DistributionFeederCB12_Selwyn St11 | DistributionFeederCB12_Selwyn St3c 300mm² Al PILC11- | DistributionFeeder | CB12_Selwyn St | Joint | TEL6 RMU | 2 | GEMA\General Cable | 3c 300mm² Al PILC | Cable | - | - | 11 | 322 | 6.1349 | 322 | 6.1349 | 322 | 6.1349 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 0.9 | 1.01 | 18.5 | 0.95 | 1.2 | 1 | 5 | 0 | 0.57 | 176.1066 | 3.3553 | 6.1349 | 6.1349 | 6.1349 | - | - | - | - | - | 3.3553 | CB12_Selwyn St3.35528193780707 | DistributionFeederCB12_Selwyn St11176.10663 | DistributionFeederCB12_Selwyn St11176.10663 | 3.3553 | 176.1066 | 176.1066 | Joint | TEL6 RMU | Cable-3c 300mm² Al PILC | 11
SubTransmissionCB13_GRM-HNT B11 | SubTransmissionCB13_GRM-HNT BGRM-CB1311Protection | SubTransmission | CB13_GRM-HNT B | 11 kV Bus | TEGRASMERE13 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB13 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | CB13_GRM-HNT B7.62102355330306 | SubTransmissionCB13_GRM-HNT B11400 | SubTransmissionCB13_GRM-HNT B11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE13 | Circuit Breaker-GRM-CB13-Protection | 11
SubTransmissionCB13_GRM-HNT B11 | SubTransmissionCB13_GRM-HNT B3c 400mm² AL11- | SubTransmission | CB13_GRM-HNT B | TEGRASMERE 13 | Joint | 2 | GEMA\General Cable | 3c 400mm² AL | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 9.5 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB13_GRM-HNT B8.00900224137816 | SubTransmissionCB13_GRM-HNT B11420.3636 | SubTransmissionCB13_GRM-HNT B11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE 13 | Joint | Cable-3c 400mm² AL | 11
SubTransmissionCB13_GRM-HNT B11 | SubTransmissionCB13_GRM-HNT B3c 0.3in² Cu PILC STAS11- | SubTransmission | CB13_GRM-HNT B | Joint | TEHUNT12 | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC STAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1651.1 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB13_GRM-HNT B5.66745037564935 | SubTransmissionCB13_GRM-HNT B11297.464 | SubTransmissionCB13_GRM-HNT B11297.464 | 5.6675 | 297.464 | 297.464 | Joint | TEHUNT12 | Cable-3c 0.3in² Cu PILC STAS | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANSGRM-CB1311Protection | SubTransmission | GRM_HNT_SUBTRANS | 11 kV Bus | TEGRASMERE13 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB13 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_HNT_SUBTRANS7.62102355330306 | SubTransmissionGRM_HNT_SUBTRANS11400 | SubTransmissionGRM_HNT_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE13 | Circuit Breaker-GRM-CB13-Protection | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANS3c 400mm² AL11- | SubTransmission | GRM_HNT_SUBTRANS | TEGRASMERE 13 | Joint | 2 | GEMA\General Cable | 3c 400mm² AL | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 9.5 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | GRM_HNT_SUBTRANS8.00900224137816 | SubTransmissionGRM_HNT_SUBTRANS11420.3636 | SubTransmissionGRM_HNT_SUBTRANS11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE 13 | Joint | Cable-3c 400mm² AL | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANS3c 0.3in² Cu PILC STAS11- | SubTransmission | GRM_HNT_SUBTRANS | Joint | TEHUNT12 | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC STAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1651.1 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | GRM_HNT_SUBTRANS5.66745037564935 | SubTransmissionGRM_HNT_SUBTRANS11297.464 | SubTransmissionGRM_HNT_SUBTRANS11297.464 | 5.6675 | 297.464 | 297.464 | Joint | TEHUNT12 | Cable-3c 0.3in² Cu PILC STAS | 11
DistributionFeederCB15_Park Lane11 | DistributionFeederCB15_Park LaneGRM-CB1511Protection | DistributionFeeder | CB15_Park Lane | 11 kV Bus | TEGRASMERE15 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB15 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB15_Park Lane5.79197790051033 | DistributionFeederCB15_Park Lane11304 | DistributionFeederCB15_Park Lane11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE15 | Circuit Breaker-GRM-CB15-Protection | 11
DistributionFeederCB15_Park Lane11 | DistributionFeederCB15_Park Lane3c 300mm² Al PILC SWA11- | DistributionFeeder | CB15_Park Lane | TEGRASMERE15 | TEE28 RMU | 2 | GEMA\General Cable | 3c 300mm² Al PILC SWA | Cable | - | - | 11 | 322 | 6.1349 | 322 | 6.1349 | 322 | 6.1349 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 671.4 | 1.2 | 0.99 | 18.5 | 0.95 | 1.2 | 1 | 5 | 0.3 | 0.57 | 172.6194 | 3.2888 | 6.1349 | 6.1349 | 6.1349 | - | - | - | - | - | 3.2888 | CB15_Park Lane3.28884071131584 | DistributionFeederCB15_Park Lane11172.61937 | DistributionFeederCB15_Park Lane11172.61937 | 3.2888 | 172.6194 | 172.6194 | TEGRASMERE15 | TEE28 RMU | Cable-3c 300mm² Al PILC SWA | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans StGRM-CB1611Protection | DistributionFeeder | CB16_Evans St | 11 kV Bus | TEGRASMERE16 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB16 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB16_Evans St5.79197790051033 | DistributionFeederCB16_Evans St11304 | DistributionFeederCB16_Evans St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE16 | Circuit Breaker-GRM-CB16-Protection | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 0.4in² Al PILC DSTA11- | DistributionFeeder | CB16_Evans St | TEGRASMERE16 | Joint | 2 | GEMA\General Cable | 3c 0.4in² Al PILC DSTA | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 589.9 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 262.2 | 4.9956 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 4.9956 | CB16_Evans St4.99558093919016 | DistributionFeederCB16_Evans St11262.2 | DistributionFeederCB16_Evans St11262.2 | 4.9956 | 262.2 | 262.2 | TEGRASMERE16 | Joint | Cable-3c 0.4in² Al PILC DSTA | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 0.15in² Cu PILC STAS11- | DistributionFeeder | CB16_Evans St | Joint | Joint | 3 | GEMA\General Cable | 3c 0.15in² Cu PILC STAS | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 33 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 201.4 | 3.8372 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.8372 | CB16_Evans St3.83718535908809 | DistributionFeederCB16_Evans St11201.4 | DistributionFeederCB16_Evans St11201.4 | 3.8372 | 201.4 | 201.4 | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB16_Evans St | Joint | Joint | 4 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 58.9 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 228 | 4.344 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.344 | CB16_Evans St4.34398342538274 | DistributionFeederCB16_Evans St11228 | DistributionFeederCB16_Evans St11228 | 4.344 | 228 | 228 | Joint | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 0.15in² Cu PILC STAS11- | DistributionFeeder | CB16_Evans St | Joint | Joint | 5 | GEMA\General Cable | 3c 0.15in² Cu PILC STAS | Cable | - | - | 11 | 221 | 4.2106 | 221 | 4.2106 | 221 | 4.2106 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1331.5 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 167.96 | 3.2001 | 4.2106 | 4.2106 | 4.2106 | - | - | - | - | - | 3.2001 | CB16_Evans St3.20006779003196 | DistributionFeederCB16_Evans St11167.96 | DistributionFeederCB16_Evans St11167.96 | 3.2001 | 167.96 | 167.96 | Joint | Joint | Cable-3c 0.15in² Cu PILC STAS | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB16_Evans St | Joint | Joint | 6 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 122.4 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 228 | 4.344 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.344 | CB16_Evans St4.34398342538274 | DistributionFeederCB16_Evans St11228 | DistributionFeederCB16_Evans St11228 | 4.344 | 228 | 228 | Joint | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB16_Evans St11 | DistributionFeederCB16_Evans St3c 300mm² Al MDPE CWS11- | DistributionFeeder | CB16_Evans St | Joint | TER58 RMU | 7 | GEMA\General Cable | 3c 300mm² Al MDPE CWS | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 7 | 0.8 | 1 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.3 | 0.8 | 361.76 | 6.8925 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.8925 | CB16_Evans St6.89245370160729 | DistributionFeederCB16_Evans St11361.76 | DistributionFeederCB16_Evans St11361.76 | 6.8925 | 361.76 | 361.76 | Joint | TER58 RMU | Cable-3c 300mm² Al MDPE CWS | 11
DistributionFeederCB17_June St11 | DistributionFeederCB17_June StGRM-CB1711Protection | DistributionFeeder | CB17_June St | 11 kV Bus | TEGRASMERE17 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB17 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB17_June St5.79197790051033 | DistributionFeederCB17_June St11304 | DistributionFeederCB17_June St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE17 | Circuit Breaker-GRM-CB17-Protection | 11
DistributionFeederCB17_June St11 | DistributionFeederCB17_June St3c 300mm² Al PILC SWA11- | DistributionFeeder | CB17_June St | TEGRASMERE17 | Joint | 2 | GEMA\General Cable | 3c 300mm² Al PILC SWA | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 150.5 | 0.9 | 1 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.35 | 0.89 | 312.835 | 5.9603 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 5.9603 | CB17_June St5.96030725824391 | DistributionFeederCB17_June St11312.835 | DistributionFeederCB17_June St11312.835 | 5.9603 | 312.835 | 312.835 | TEGRASMERE17 | Joint | Cable-3c 300mm² Al PILC SWA | 11
DistributionFeederCB17_June St11 | DistributionFeederCB17_June St3c 0.4in² Al PILC SWA11- | DistributionFeeder | CB17_June St | Joint | TEF10 RMU | 3 | GEMA\General Cable | 3c 0.4in² Al PILC SWA | Cable | - | - | 11 | 288 | 5.4871 | 288 | 5.4871 | 288 | 5.4871 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 166 | 0.9 | 1 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.3 | 0.85 | 232.56 | 4.4309 | 5.4871 | 5.4871 | 5.4871 | - | - | - | - | - | 4.4309 | CB17_June St4.4308630938904 | DistributionFeederCB17_June St11232.56 | DistributionFeederCB17_June St11232.56 | 4.4309 | 232.56 | 232.56 | Joint | TEF10 RMU | Cable-3c 0.4in² Al PILC SWA | 11
SubTransmissionCB18_GRM-NST B11 | SubTransmissionCB18_GRM-NST BGRM-CB1811Protection | SubTransmission | CB18_GRM-NST B | 11 kV Bus | TEGRASMERE18 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB18 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | CB18_GRM-NST B7.62102355330306 | SubTransmissionCB18_GRM-NST B11400 | SubTransmissionCB18_GRM-NST B11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE18 | Circuit Breaker-GRM-CB18-Protection | 11
SubTransmissionCB18_GRM-NST B11 | SubTransmissionCB18_GRM-NST B3/1c 400mm² Al XLPE11- | SubTransmission | CB18_GRM-NST B | TEGRASMERE 18 | Joint | 2 | GEMA\General Cable | 3/1c 400mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 24.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB18_GRM-NST B8.00900224137816 | SubTransmissionCB18_GRM-NST B11420.3636 | SubTransmissionCB18_GRM-NST B11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE 18 | Joint | Cable-3/1c 400mm² Al XLPE | 11
SubTransmissionCB18_GRM-NST B11 | SubTransmissionCB18_GRM-NST B3c 0.3in² Cu PILC SWAS11- | SubTransmission | CB18_GRM-NST B | Joint | Joint | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 3004.3 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB18_GRM-NST B5.66745037564935 | SubTransmissionCB18_GRM-NST B11297.464 | SubTransmissionCB18_GRM-NST B11297.464 | 5.6675 | 297.464 | 297.464 | Joint | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionCB18_GRM-NST B11 | SubTransmissionCB18_GRM-NST B3/1c 400mm² AL XLPE HDPE Screened11- | SubTransmission | CB18_GRM-NST B | Joint | NST15 | 4 | GEMA\General Cable | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 72.4 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB18_GRM-NST B8.00900224137816 | SubTransmissionCB18_GRM-NST B11420.3636 | SubTransmissionCB18_GRM-NST B11420.3636 | 8.009 | 420.3636 | 420.3636 | Joint | NST15 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
SubTransmissionGRM_HNT_SUBTRANS11 | SubTransmissionGRM_HNT_SUBTRANSGRM-CB1811Protection | SubTransmission | GRM_HNT_SUBTRANS | 11 kV Bus | TEGRASMERE18 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB18 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_HNT_SUBTRANS7.62102355330306 | SubTransmissionGRM_HNT_SUBTRANS11400 | SubTransmissionGRM_HNT_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE18 | Circuit Breaker-GRM-CB18-Protection | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3/1c 400mm² Al XLPE11- | SubTransmission | GRM_NST_SUBTRANS | TEGRASMERE 18 | Joint | 2 | GEMA\General Cable | 3/1c 400mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 24.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | GRM_NST_SUBTRANS8.00900224137816 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE 18 | Joint | Cable-3/1c 400mm² Al XLPE | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3c 0.3in² Cu PILC SWAS11- | SubTransmission | GRM_NST_SUBTRANS | Joint | Joint | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 3004.3 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | GRM_NST_SUBTRANS5.66745037564935 | SubTransmissionGRM_NST_SUBTRANS11297.464 | SubTransmissionGRM_NST_SUBTRANS11297.464 | 5.6675 | 297.464 | 297.464 | Joint | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANS3/1c 400mm² AL XLPE HDPE Screened11- | SubTransmission | GRM_NST_SUBTRANS | Joint | NST15 | 4 | GEMA\General Cable | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 72.4 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | GRM_NST_SUBTRANS8.00900224137816 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | SubTransmissionGRM_NST_SUBTRANS11420.3636 | 8.009 | 420.3636 | 420.3636 | Joint | NST15 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
DistributionFeederCB20_Hobbs St11 | DistributionFeederCB20_Hobbs StGRM-CB2011Protection | DistributionFeeder | CB20_Hobbs St | 11 kV Bus | TEGRASMERE20 | 1 | GEMA\AEL Protection Database\860RP1877 | GRM-CB20 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | 113.3 | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB20_Hobbs St5.79197790051033 | DistributionFeederCB20_Hobbs St11304 | DistributionFeederCB20_Hobbs St11304 | 5.792 | 304 | 304 | 11 kV Bus | TEGRASMERE20 | Circuit Breaker-GRM-CB20-Protection | 11
DistributionFeederCB20_Hobbs St11 | DistributionFeederCB20_Hobbs St3c 0.4in² Al PILC DSTA11- | DistributionFeeder | CB20_Hobbs St | TEGRASMERE20 | TEM7 RMU | 2 | GEMA\General Cable | 3c 0.4in² Al PILC DSTA | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 1 | 0.98 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.3 | 0.63 | 202.7789 | 3.8635 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 3.8635 | CB20_Hobbs St3.86345609421962 | DistributionFeederCB20_Hobbs St11202.778856 | DistributionFeederCB20_Hobbs St11202.778856 | 3.8635 | 202.7789 | 202.7789 | TEGRASMERE20 | TEM7 RMU | Cable-3c 0.4in² Al PILC DSTA | 11
DistributionFeederCB1_Harper St11 | DistributionFeederCB1_Harper StHNT-CB111Protection | DistributionFeeder | CB1_Harper St | 11 kV Bus | TEHUNT1 | 1 | GEMA\AEL Protection Database | HNT-CB1 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB1_Harper St3.81051177665153 | DistributionFeederCB1_Harper St11200 | DistributionFeederCB1_Harper St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT1 | Circuit Breaker-HNT-CB1-Protection | 11
DistributionFeederCB1_Harper St11 | DistributionFeederCB1_Harper St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB1_Harper St | TEHUNT1 | TEJ17 | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 238.5 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 224.4375 | 4.2761 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.2761 | CB1_Harper St4.27610868436114 | DistributionFeederCB1_Harper St11224.4375 | DistributionFeederCB1_Harper St11224.4375 | 4.2761 | 224.4375 | 224.4375 | TEHUNT1 | TEJ17 | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB2_Wilson St11 | DistributionFeederCB2_Wilson StHNT-CB211Protection | DistributionFeeder | CB2_Wilson St | 11 kV Bus | TEHUNT2 | 1 | GEMA\AEL Protection Database | HNT-CB2 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB2_Wilson St3.81051177665153 | DistributionFeederCB2_Wilson St11200 | DistributionFeederCB2_Wilson St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT2 | Circuit Breaker-HNT-CB2-Protection | 11
DistributionFeederCB2_Wilson St11 | DistributionFeederCB2_Wilson St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB2_Wilson St | TEHUNT2 | TED18 | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 651.69 | 0.85 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.11 | 0.8 | 232.56 | 4.4309 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.4309 | CB2_Wilson St4.4308630938904 | DistributionFeederCB2_Wilson St11232.56 | DistributionFeederCB2_Wilson St11232.56 | 4.4309 | 232.56 | 232.56 | TEHUNT2 | TED18 | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB2_Wilson St11 | DistributionFeederCB2_Wilson StGOPHER11- | DistributionFeeder | CB2_Wilson St | TED18 | POLE 45041 | 3 | GEMA/AEL OH Amp Calc. | GOPHER | OH Line | - | - | 11 | 145.1667 | 2.7658 | - | - | 110.4061 | 2.1035 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 299.6 | - | - | - | - | - | - | - | - | - | - | - | 2.7658 | - | 2.1035 | - | - | - | - | - | - | CB2_Wilson St2.10351864636243 | DistributionFeederCB2_Wilson St11110.406096065704 | DistributionFeederCB2_Wilson St11110.406096065704 | 2.1035 | 110.4061 | 110.4061 | TED18 | POLE 45041 | OH Line-GOPHER | 11
SubTransmissionCB3_HNT-GRM A11 | SubTransmissionCB3_HNT-GRM AHNT-CB311Protection | SubTransmission | CB3_HNT-GRM A | 11 kV Bus | TEGRASMERE 4 | 1 | GEMA\AEL Protection Database\860RP1877 | HNT-CB3 | Circuit Breaker | Relay SEL 311L | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | CB3_HNT-GRM A7.62102355330306 | SubTransmissionCB3_HNT-GRM A11400 | SubTransmissionCB3_HNT-GRM A11400 | 7.621 | 400 | 400 | 11 kV Bus | TEGRASMERE 4 | Circuit Breaker-HNT-CB3-Protection | 11
SubTransmissionCB3_HNT-GRM A11 | SubTransmissionCB3_HNT-GRM A3c 0.3in² Cu PILC SWA 11- | SubTransmission | CB3_HNT-GRM A | TEGRASMERE 4 | TEHUNT3 | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWA | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1629.2 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB3_HNT-GRM A5.66745037564935 | SubTransmissionCB3_HNT-GRM A11297.464 | SubTransmissionCB3_HNT-GRM A11297.464 | 5.6675 | 297.464 | 297.464 | TEGRASMERE 4 | TEHUNT3 | Cable-3c 0.3in² Cu PILC SWA | 11
DistributionFeederCB4_Baker St11 | DistributionFeederCB4_Baker StHNT-CB411Protection | DistributionFeeder | CB4_Baker St | 11 kV Bus | TEHUNT4 | 1 | GEMA\AEL Protection Database | HNT-CB4 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB4_Baker St3.81051177665153 | DistributionFeederCB4_Baker St11200 | DistributionFeederCB4_Baker St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT4 | Circuit Breaker-HNT-CB4-Protection | 11
DistributionFeederCB4_Baker St11 | DistributionFeederCB4_Baker St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB4_Baker St | TEHUNT4 | Joint | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 519.6 | 0.85 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.11 | 0.8 | 232.56 | 4.4309 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.4309 | CB4_Baker St4.4308630938904 | DistributionFeederCB4_Baker St11232.56 | DistributionFeederCB4_Baker St11232.56 | 4.4309 | 232.56 | 232.56 | TEHUNT4 | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB4_Baker St11 | DistributionFeederCB4_Baker St3c 0.25in² Al PILC DSTA11- | DistributionFeeder | CB4_Baker St | Joint | TED5 | 3 | GEMA\General Cable | 3c 0.25in² Al PILC DSTA | Cable | - | - | 11 | 270 | 5.1442 | 270 | 5.1442 | 270 | 5.1442 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 192.7 | 0.85 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.11 | 0.8 | 209.304 | 3.9878 | 5.1442 | 5.1442 | 5.1442 | - | - | - | - | - | 3.9878 | CB4_Baker St3.98777678450136 | DistributionFeederCB4_Baker St11209.304 | DistributionFeederCB4_Baker St11209.304 | 3.9878 | 209.304 | 209.304 | Joint | TED5 | Cable-3c 0.25in² Al PILC DSTA | 11
DistributionFeederCB5_Le Cren St11 | DistributionFeederCB5_Le Cren StHNT-CB511Protection | DistributionFeeder | CB5_Le Cren St | 11 kV Bus | TEHUNT5 | 1 | GEMA\AEL Protection Database | HNT-CB5 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB5_Le Cren St3.81051177665153 | DistributionFeederCB5_Le Cren St11200 | DistributionFeederCB5_Le Cren St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT5 | Circuit Breaker-HNT-CB5-Protection | 11
DistributionFeederCB5_Le Cren St11 | DistributionFeederCB5_Le Cren St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB5_Le Cren St | TEHUNT5 | Joint | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 307.6 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0 | 0.7 | 205.485 | 3.915 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.915 | CB5_Le Cren St3.9150150621262 | DistributionFeederCB5_Le Cren St11205.485 | DistributionFeederCB5_Le Cren St11205.485 | 3.915 | 205.485 | 205.485 | TEHUNT5 | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB5_Le Cren St11 | DistributionFeederCB5_Le Cren St3c 0.25in² Al PILC SWA11- | DistributionFeeder | CB5_Le Cren St | Joint | TEK9 RMU | 3 | GEMA\General Cable | 3c 0.25in² Al PILC SWA | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 10.6 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0 | 0.7 | 181.5117 | 3.4583 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.4583 | CB5_Le Cren St3.45826330487814 | DistributionFeederCB5_Le Cren St11181.51175 | DistributionFeederCB5_Le Cren St11181.51175 | 3.4583 | 181.5117 | 181.5117 | Joint | TEK9 RMU | Cable-3c 0.25in² Al PILC SWA | 11
SubTransmissionCB6_HNT-NST A11 | SubTransmissionCB6_HNT-NST AHNT-CB611Protection | SubTransmission | CB6_HNT-NST A | 11 kV Bus | TEHUNT6 | 1 | GEMA\AEL Protection Database | HNT-CB6 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 400 | 7.621 | - | - | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.621 | 7.621 | 7.621 | - | CB6_HNT-NST A7.62102355330306 | SubTransmissionCB6_HNT-NST A11400 | SubTransmissionCB6_HNT-NST A11400 | 7.621 | 400 | 400 | 11 kV Bus | TEHUNT6 | Circuit Breaker-HNT-CB6-Protection | 11
SubTransmissionCB6_HNT-NST A11 | SubTransmissionCB6_HNT-NST A3c 0.3in² Cu PILC SWAS11- | SubTransmission | CB6_HNT-NST A | TEHUNT6 | Joint | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1151.2 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 291.7687 | 5.5589 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 5.5589 | CB6_HNT-NST A5.55894128966948 | SubTransmissionCB6_HNT-NST A11291.76875 | SubTransmissionCB6_HNT-NST A11291.76875 | 5.5589 | 291.7687 | 291.7687 | TEHUNT6 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionCB6_HNT-NST A11 | SubTransmissionCB6_HNT-NST A3/1c 400mm² Al XLPE HPDE Screened11- | SubTransmission | CB6_HNT-NST A | Joint | NST07 | 3 | GEMA\General Cable | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 79.4 | 0.7 | 1.04 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 397.917 | 7.5813 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.5813 | CB6_HNT-NST A7.58133707314923 | SubTransmissionCB6_HNT-NST A11397.917 | SubTransmissionCB6_HNT-NST A11397.917 | 7.5813 | 397.917 | 397.917 | Joint | NST07 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANSHNT-CB611Protection | SubTransmission | HNT_NST_SUBTRANS | 11 kV Bus | TEHUNT6 | 1 | GEMA\AEL Protection Database | HNT-CB6 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 400 | 7.621 | - | - | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.621 | 7.621 | 7.621 | - | HNT_NST_SUBTRANS7.62102355330306 | SubTransmissionHNT_NST_SUBTRANS11400 | SubTransmissionHNT_NST_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEHUNT6 | Circuit Breaker-HNT-CB6-Protection | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANS3c 0.3in² Cu PILC SWAS11- | SubTransmission | HNT_NST_SUBTRANS | TEHUNT6 | Joint | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1151.2 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 291.7687 | 5.5589 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 5.5589 | HNT_NST_SUBTRANS5.55894128966948 | SubTransmissionHNT_NST_SUBTRANS11291.76875 | SubTransmissionHNT_NST_SUBTRANS11291.76875 | 5.5589 | 291.7687 | 291.7687 | TEHUNT6 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANS3/1c 400mm² Al XLPE HPDE Screened11- | SubTransmission | HNT_NST_SUBTRANS | Joint | NST07 | 3 | GEMA\General Cable | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 79.4 | 0.7 | 1.04 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 397.917 | 7.5813 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.5813 | HNT_NST_SUBTRANS7.58133707314923 | SubTransmissionHNT_NST_SUBTRANS11397.917 | SubTransmissionHNT_NST_SUBTRANS11397.917 | 7.5813 | 397.917 | 397.917 | Joint | NST07 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB7_Church St SS11 | DistributionFeederCB7_Church St SSHNT-CB711Protection | DistributionFeeder | CB7_Church St SS | 11 kV Bus | TEHUNT7 | 1 | GEMA\AEL Protection Database | HNT-CB7 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB7_Church St SS3.81051177665153 | DistributionFeederCB7_Church St SS11200 | DistributionFeederCB7_Church St SS11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT7 | Circuit Breaker-HNT-CB7-Protection | 11
DistributionFeederCB7_Church St SS11 | DistributionFeederCB7_Church St SS3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB7_Church St SS | TEHUNT7 | Joint | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 224.1 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 234.84 | 4.4743 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.4743 | CB7_Church St SS4.47430292814423 | DistributionFeederCB7_Church St SS11234.84 | DistributionFeederCB7_Church St SS11234.84 | 4.4743 | 234.84 | 234.84 | TEHUNT7 | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB7_Church St SS11 | DistributionFeederCB7_Church St SS3c 0.15in² Al PILC STAS11- | DistributionFeeder | CB7_Church St SS | Joint | TEJ4 | 3 | GEMA\General Cable | 3c 0.15in² Al PILC STAS | Cable | - | - | 11 | 205 | 3.9058 | 205 | 3.9058 | 205 | 3.9058 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 211.4 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 160.474 | 3.0574 | 3.9058 | 3.9058 | 3.9058 | - | - | - | - | - | 3.0574 | CB7_Church St SS3.05744033423189 | DistributionFeederCB7_Church St SS11160.474 | DistributionFeederCB7_Church St SS11160.474 | 3.0574 | 160.474 | 160.474 | Joint | TEJ4 | Cable-3c 0.15in² Al PILC STAS | 11
DistributionFeederCB8_Spare11 | DistributionFeederCB8_SpareHNT-CB811Protection | DistributionFeeder | CB8_Spare | SPARE | TEHUNT8 | 1 | GEMA\AEL Protection Database | HNT-CB8 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB8_Spare3.81051177665153 | DistributionFeederCB8_Spare11200 | DistributionFeederCB8_Spare11200 | 3.8105 | 200 | 200 | SPARE | TEHUNT8 | Circuit Breaker-HNT-CB8-Protection | 11
DistributionFeederCB9_Bus coupler11 | DistributionFeederCB9_Bus couplerTEHUNT911- | DistributionFeeder | CB9_Bus coupler | 11 kV Bus | TEHUNT9 | 1 | GEMA\AEL Protection Database | TEHUNT9 | Bus Coupler | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB9_Bus coupler12.0031120964523 | DistributionFeederCB9_Bus coupler11630 | DistributionFeederCB9_Bus coupler11630 | 12.0031 | 630 | 630 | 11 kV Bus | TEHUNT9 | Bus Coupler-TEHUNT9 | 11
DistributionFeederCB10_Gibson St11 | DistributionFeederCB10_Gibson StHNT-CB1011Protection | DistributionFeeder | CB10_Gibson St | 11 kV Bus | TEHUNT10 | 1 | GEMA\AEL Protection Database | HNT-CB10 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB10_Gibson St3.81051177665153 | DistributionFeederCB10_Gibson St11200 | DistributionFeederCB10_Gibson St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT10 | Circuit Breaker-HNT-CB10-Protection | 11
DistributionFeederCB10_Gibson St11 | DistributionFeederCB10_Gibson St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB10_Gibson St | TEHUNT10 | TEJ8 RMU | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 532 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0 | 0.7 | 209.475 | 3.991 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.991 | CB10_Gibson St3.9910347720704 | DistributionFeederCB10_Gibson St11209.475 | DistributionFeederCB10_Gibson St11209.475 | 3.991 | 209.475 | 209.475 | TEHUNT10 | TEJ8 RMU | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB11_Rhodes St11 | DistributionFeederCB11_Rhodes StHNT-CB1111Protection | DistributionFeeder | CB11_Rhodes St | 11 kV Bus | TEHUNT11 | 1 | GEMA\AEL Protection Database | HNT-CB11 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB11_Rhodes St3.81051177665153 | DistributionFeederCB11_Rhodes St11200 | DistributionFeederCB11_Rhodes St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT11 | Circuit Breaker-HNT-CB11-Protection | 11
DistributionFeederCB11_Rhodes St11 | DistributionFeederCB11_Rhodes St3/1c 300mm² Al XLPE11- | DistributionFeeder | CB11_Rhodes St | TEHUNT11 | Joint | 2 | GEMA\General Cable | 3/1c 300mm² Al XLPE | Cable | - | - | 11 | 466 | 8.8785 | 466 | 8.8785 | 466 | 8.8785 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 3.5 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 1 | 0 | 1 | 464.835 | 8.8563 | 8.8785 | 8.8785 | 8.8785 | - | - | - | - | - | 8.8563 | CB11_Rhodes St8.85629620849907 | DistributionFeederCB11_Rhodes St11464.835 | DistributionFeederCB11_Rhodes St11464.835 | 8.8563 | 464.835 | 464.835 | TEHUNT11 | Joint | Cable-3/1c 300mm² Al XLPE | 11
DistributionFeederCB11_Rhodes St11 | DistributionFeederCB11_Rhodes St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB11_Rhodes St | Joint | TEJ7 Link | 3 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 251 | 4.7822 | 251 | 4.7822 | 251 | 4.7822 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 294.3 | 0.9 | 0.99 | 18.5 | 0.952 | 1.2 | 1 | 3 | 0 | 0.7 | 165.5937 | 3.155 | 4.7822 | 4.7822 | 4.7822 | - | - | - | - | - | 3.155 | CB11_Rhodes St3.15498440583862 | DistributionFeederCB11_Rhodes St11165.593736 | DistributionFeederCB11_Rhodes St11165.593736 | 3.155 | 165.5937 | 165.5937 | Joint | TEJ7 Link | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB11_Rhodes St11 | DistributionFeederCB11_Rhodes St70mm² Cu11- | DistributionFeeder | CB11_Rhodes St | TEJ7 Link | TOTE169 FUSE | 4 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 11 | 247 | 4.706 | - | - | 247 | 4.706 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 166.7 | - | - | - | - | - | - | - | - | - | - | - | 4.706 | - | 4.706 | - | - | - | - | - | - | CB11_Rhodes St4.70598204416464 | DistributionFeederCB11_Rhodes St11247 | DistributionFeederCB11_Rhodes St11247 | 4.706 | 247 | 247 | TEJ7 Link | TOTE169 FUSE | OH Line-70mm² Cu | 11
SubTransmissionCB12_HNT-GRM B11 | SubTransmissionCB12_HNT-GRM BHNT-CB1211Protection | SubTransmission | CB12_HNT-GRM B | TEGRASMERE13 | TEHUNT12 | 1 | GEMA\AEL Protection Database | HNT-CB12 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 400 | 7.621 | - | - | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.621 | 7.621 | 7.621 | - | CB12_HNT-GRM B7.62102355330306 | SubTransmissionCB12_HNT-GRM B11400 | SubTransmissionCB12_HNT-GRM B11400 | 7.621 | 400 | 400 | TEGRASMERE13 | TEHUNT12 | Circuit Breaker-HNT-CB12-Protection | 11
SubTransmissionCB12_HNT-GRM B11 | SubTransmissionCB12_HNT-GRM B3c 400mm² AL11- | SubTransmission | CB12_HNT-GRM B | TEGRASMERE 13 | Joint | 2 | GEMA\General Cable | 3c 400mm² AL | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 9.5 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 420.3636 | 8.009 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.009 | CB12_HNT-GRM B8.00900224137816 | SubTransmissionCB12_HNT-GRM B11420.3636 | SubTransmissionCB12_HNT-GRM B11420.3636 | 8.009 | 420.3636 | 420.3636 | TEGRASMERE 13 | Joint | Cable-3c 400mm² AL | 11
SubTransmissionCB12_HNT-GRM B11 | SubTransmissionCB12_HNT-GRM B3c 0.3in² Cu PILC STAS11- | SubTransmission | CB12_HNT-GRM B | Joint | TEHUNT12 | 3 | GEMA\General Cable | 3c 0.3in² Cu PILC STAS | Cable | - | - | 11 | 380 | 7.24 | 380 | 7.24 | 380 | 7.24 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1651.1 | 0.85 | 1.03 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.34 | 0.8 | 297.464 | 5.6675 | 7.24 | 7.24 | 7.24 | - | - | - | - | - | 5.6675 | CB12_HNT-GRM B5.66745037564935 | SubTransmissionCB12_HNT-GRM B11297.464 | SubTransmissionCB12_HNT-GRM B11297.464 | 5.6675 | 297.464 | 297.464 | Joint | TEHUNT12 | Cable-3c 0.3in² Cu PILC STAS | 11
DistributionFeederCB13_Clifton Terrace11 | DistributionFeederCB13_Clifton TerraceHNT-CB1311Protection | DistributionFeeder | CB13_Clifton Terrace | 11 kV Bus | TEHUNT13 | 1 | GEMA\AEL Protection Database | HNT-CB13 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB13_Clifton Terrace3.81051177665153 | DistributionFeederCB13_Clifton Terrace11200 | DistributionFeederCB13_Clifton Terrace11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT13 | Circuit Breaker-HNT-CB13-Protection | 11
DistributionFeederCB13_Clifton Terrace11 | DistributionFeederCB13_Clifton Terrace3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB13_Clifton Terrace | TEHUNT13 | TE62 | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 255.3 | 0.82 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 6 | 0.15 | 0.7 | 203.49 | 3.877 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.877 | CB13_Clifton Terrace3.8770052071541 | DistributionFeederCB13_Clifton Terrace11203.49 | DistributionFeederCB13_Clifton Terrace11203.49 | 3.877 | 203.49 | 203.49 | TEHUNT13 | TE62 | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB14_Church St NS11 | DistributionFeederCB14_Church St NSHNT-CB1411Protection | DistributionFeeder | CB14_Church St NS | 11 kV Bus | TEHUNT14 | 1 | GEMA\AEL Protection Database | HNT-CB14 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB14_Church St NS3.81051177665153 | DistributionFeederCB14_Church St NS11200 | DistributionFeederCB14_Church St NS11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT14 | Circuit Breaker-HNT-CB14-Protection | 11
DistributionFeederCB14_Church St NS11 | DistributionFeederCB14_Church St NS3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB14_Church St NS | TEHUNT14 | Joint | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1060.2 | 0.82 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 4 | 0 | 0.7 | 203.49 | 3.877 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.877 | CB14_Church St NS3.8770052071541 | DistributionFeederCB14_Church St NS11203.49 | DistributionFeederCB14_Church St NS11203.49 | 3.877 | 203.49 | 203.49 | TEHUNT14 | Joint | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB14_Church St NS11 | DistributionFeederCB14_Church St NS3c 95mm² AL PILC SWAS11- | DistributionFeeder | CB14_Church St NS | Joint | TER8 RMU | 3 | GEMA\General Cable | 3c 95mm² AL PILC SWAS | Cable | - | - | 11 | 171 | 3.258 | 171 | 3.258 | 171 | 3.258 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 61.7 | 0.82 | 1.02 | 18.5 | 0.95 | 1.2 | 1 | 2 | 0.3 | 0.95 | 157.4141 | 2.9991 | 3.258 | 3.258 | 3.258 | - | - | - | - | - | 2.9991 | CB14_Church St NS2.99914045667706 | DistributionFeederCB14_Church St NS11157.41405 | DistributionFeederCB14_Church St NS11157.41405 | 2.9991 | 157.4141 | 157.4141 | Joint | TER8 RMU | Cable-3c 95mm² AL PILC SWAS | 11
SubTransmissionCB15_HNT-NST B11 | SubTransmissionCB15_HNT-NST BHNT-CB1511Protection | SubTransmission | CB15_HNT-NST B | 11 kV Bus | TEHUNT15 | 1 | GEMA\AEL Protection Database | HNT-CB15 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 400 | 7.621 | - | - | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.621 | 7.621 | 7.621 | - | CB15_HNT-NST B7.62102355330306 | SubTransmissionCB15_HNT-NST B11400 | SubTransmissionCB15_HNT-NST B11400 | 7.621 | 400 | 400 | 11 kV Bus | TEHUNT15 | Circuit Breaker-HNT-CB15-Protection | 11
SubTransmissionCB15_HNT-NST B11 | SubTransmissionCB15_HNT-NST B3c 0.3in² Cu PILC SWAS11- | SubTransmission | CB15_HNT-NST B | TEHUNT15 | Joint | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1153.4 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 291.7687 | 5.5589 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 5.5589 | CB15_HNT-NST B5.55894128966948 | SubTransmissionCB15_HNT-NST B11291.76875 | SubTransmissionCB15_HNT-NST B11291.76875 | 5.5589 | 291.7687 | 291.7687 | TEHUNT15 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionCB15_HNT-NST B11 | SubTransmissionCB15_HNT-NST B3/1c 400mm² Al XLPE HPDE Screened11- | SubTransmission | CB15_HNT-NST B | Joint | NST14 | 3 | GEMA\General Cable | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 93.4 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 401.7431 | 7.6542 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.6542 | CB15_HNT-NST B7.65423454500644 | SubTransmissionCB15_HNT-NST B11401.743125 | SubTransmissionCB15_HNT-NST B11401.743125 | 7.6542 | 401.7431 | 401.7431 | Joint | NST14 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANSHNT-CB1511Protection | SubTransmission | HNT_NST_SUBTRANS | 11 kV Bus | TEHUNT15 | 1 | GEMA\AEL Protection Database | HNT-CB15 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 400 | 7.621 | - | - | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.621 | 7.621 | 7.621 | - | HNT_NST_SUBTRANS7.62102355330306 | SubTransmissionHNT_NST_SUBTRANS11400 | SubTransmissionHNT_NST_SUBTRANS11400 | 7.621 | 400 | 400 | 11 kV Bus | TEHUNT15 | Circuit Breaker-HNT-CB15-Protection | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANS3c 0.3in² Cu PILC SWAS11- | SubTransmission | HNT_NST_SUBTRANS | TEHUNT15 | Joint | 2 | GEMA\General Cable | 3c 0.3in² Cu PILC SWAS | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1153.4 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 291.7687 | 5.5589 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 5.5589 | HNT_NST_SUBTRANS5.55894128966948 | SubTransmissionHNT_NST_SUBTRANS11291.76875 | SubTransmissionHNT_NST_SUBTRANS11291.76875 | 5.5589 | 291.7687 | 291.7687 | TEHUNT15 | Joint | Cable-3c 0.3in² Cu PILC SWAS | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANS3/1c 400mm² Al XLPE HPDE Screened11- | SubTransmission | HNT_NST_SUBTRANS | Joint | NST14 | 3 | GEMA\General Cable | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 93.4 | 0.7 | 1.05 | 18.5 | 0.97 | 1.2 | 1 | 3 | 0.2 | 0.75 | 410.2009 | 7.8154 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.8154 | HNT_NST_SUBTRANS7.81537632490131 | SubTransmissionHNT_NST_SUBTRANS11410.200875 | SubTransmissionHNT_NST_SUBTRANS11410.200875 | 7.8154 | 410.2009 | 410.2009 | Joint | NST14 | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB16_Arthur St11 | DistributionFeederCB16_Arthur StHNT-CB1611Protection | DistributionFeeder | CB16_Arthur St | 11 kV Bus | TEHUNT16 | 1 | GEMA\AEL Protection Database | HNT-CB16 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | CB16_Arthur St3.81051177665153 | DistributionFeederCB16_Arthur St11200 | DistributionFeederCB16_Arthur St11200 | 3.8105 | 200 | 200 | 11 kV Bus | TEHUNT16 | Circuit Breaker-HNT-CB16-Protection | 11
DistributionFeederCB16_Arthur St11 | DistributionFeederCB16_Arthur St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB16_Arthur St | TEHUNT16 | TEJ16 RMU | 2 | GEMA\General Cable | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 212.8 | 0.7 | 1.05 | 18.5 | 0.95 | 1.2 | 1 | 3 | 0.2 | 0.75 | 224.4375 | 4.2761 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.2761 | CB16_Arthur St4.27610868436114 | DistributionFeederCB16_Arthur St11224.4375 | DistributionFeederCB16_Arthur St11224.4375 | 4.2761 | 224.4375 | 224.4375 | TEHUNT16 | TEJ16 RMU | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeeder11 | DistributionFeederHNT-CB1711Protection | DistributionFeeder |  | SPARE | TEHUNT17 | 1 | GEMA\AEL Protection Database | HNT-CB17 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 3.8105 | 15.242 | 15.242 | - | 3.81051177665153 | DistributionFeeder11200 | DistributionFeeder11200 | 3.8105 | 200 | 200 | SPARE | TEHUNT17 | Circuit Breaker-HNT-CB17-Protection | 11
ZoneSubstationHNT11 | ZoneSubstationHNT11 | ZoneSubstation | HNT | 11 kV Bus | 11 kV Bus | 0 | GEMA\Tech 1 |  | Swictchboard |  |  | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1250 | 23.8157 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 23.8157 | - | - | - | HNT23.8156986040721 | ZoneSubstationHNT111250 | ZoneSubstationHNT111250 | 23.8157 | 1250 | 1250 | 11 kV Bus | 11 kV Bus | Swictchboard-- | 11
DistributionFeederCB3_Redruth 111 | DistributionFeederCB3_Redruth 1NST-CB311Protection | DistributionFeeder | CB3_Redruth 1 | 11 kV Bus | NST03 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB3 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB3_Redruth 15.79197790051033 | DistributionFeederCB3_Redruth 111304 | DistributionFeederCB3_Redruth 111304 | 5.792 | 304 | 304 | 11 kV Bus | NST03 | Circuit Breaker-NST-CB3-Protection | 11
DistributionFeederCB3_Redruth 111 | DistributionFeederCB3_Redruth 13/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB3_Redruth 1 | NST03 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 214 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB3_Redruth 18.05524737440196 | DistributionFeederCB3_Redruth 111422.79084 | DistributionFeederCB3_Redruth 111422.79084 | 8.0552 | 422.7908 | 422.7908 | NST03 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB3_Redruth 111 | DistributionFeederCB3_Redruth 13/1c 300mm² Al CWS11- | DistributionFeeder | CB3_Redruth 1 | Joint | L748 RMU | 3 | GEMA\General Cable\FB248 | 3/1c 300mm² Al CWS | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 2866.1 | 0.78 | 1 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.45 | 0.76 | 273.3264 | 5.2076 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 5.2076 | CB3_Redruth 15.20756733034883 | DistributionFeederCB3_Redruth 111273.3264 | DistributionFeederCB3_Redruth 111273.3264 | 5.2076 | 273.3264 | 273.3264 | Joint | L748 RMU | Cable-3/1c 300mm² Al CWS | 11
DistributionFeederCB4_Rose St11 | DistributionFeederCB4_Rose StNST-CB411Protection | DistributionFeeder | CB4_Rose St | 11 kV Bus | NST04 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB4 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB4_Rose St5.79197790051033 | DistributionFeederCB4_Rose St11304 | DistributionFeederCB4_Rose St11304 | 5.792 | 304 | 304 | 11 kV Bus | NST04 | Circuit Breaker-NST-CB4-Protection | 11
DistributionFeederCB4_Rose St11 | DistributionFeederCB4_Rose St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB4_Rose St | NST04 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 86.3 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB4_Rose St8.05524737440196 | DistributionFeederCB4_Rose St11422.79084 | DistributionFeederCB4_Rose St11422.79084 | 8.0552 | 422.7908 | 422.7908 | NST04 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB4_Rose St11 | DistributionFeederCB4_Rose St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB4_Rose St | Joint | TEQ21 RMU | 3 | GEMA\General Cable\FB248 | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 109.6 | 0.78 | 1 | 18.5 | 0.952 | 1.2 | 1 | 2 | touch | 0.8 | 228.48 | 4.3531 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.3531 | CB4_Rose St4.35312865364671 | DistributionFeederCB4_Rose St11228.48 | DistributionFeederCB4_Rose St11228.48 | 4.3531 | 228.48 | 228.48 | Joint | TEQ21 RMU | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB5_Craigie Ave11 | DistributionFeederCB5_Craigie AveNST-CB511Protection | DistributionFeeder | CB5_Craigie Ave | 11 kV Bus | NST05 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB5 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB5_Craigie Ave5.79197790051033 | DistributionFeederCB5_Craigie Ave11304 | DistributionFeederCB5_Craigie Ave11304 | 5.792 | 304 | 304 | 11 kV Bus | NST05 | Circuit Breaker-NST-CB5-Protection | 11
DistributionFeederCB5_Craigie Ave11 | DistributionFeederCB5_Craigie Ave3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB5_Craigie Ave | NST05 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 87.3 | 0.93 | 1.01 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.5 | 0.82 | 432.2906 | 8.2362 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.2362 | CB5_Craigie Ave8.23624182157988 | DistributionFeederCB5_Craigie Ave11432.2905848 | DistributionFeederCB5_Craigie Ave11432.2905848 | 8.2362 | 432.2906 | 432.2906 | NST05 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB5_Craigie Ave11 | DistributionFeederCB5_Craigie Ave3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB5_Craigie Ave | Joint | TEQ25 RMU | 3 | GEMA\General Cable\FB248 | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 56.4 | 0.9 | 1.01 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.3 | 0.7 | 201.9192 | 3.8471 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.8471 | CB5_Craigie Ave3.84707744766028 | DistributionFeederCB5_Craigie Ave11201.9192 | DistributionFeederCB5_Craigie Ave11201.9192 | 3.8471 | 201.9192 | 201.9192 | Joint | TEQ25 RMU | Cable-3c 185mm² Al PILC SWAS | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANSNST-CB611Protection | SubTransmission | GRM_NST_SUBTRANS | Grasmere | NST6 | - | GEMA\860RP1788\AEL Transformer database | NST-CB6 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_NST_SUBTRANS7.62102355330306 | SubTransmissionGRM_NST_SUBTRANS11400 | SubTransmissionGRM_NST_SUBTRANS11400 | 7.621 | 400 | 400 | Grasmere | NST6 | Circuit Breaker-NST-CB6-Protection | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANSNST-CB3511Protection | SubTransmission | TIM_NST_SUBTRANS | Timaru | NST35 | 3 | GEMA\860RP1788\AEL Transformer database | NST-CB35 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | 1188 | 22.6344 | - | - | 1200 | 22.8631 | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | 22.6344 | 22.8631 | 22.8631 | - | TIM_NST_SUBTRANS22.6344399533101 | SubTransmissionTIM_NST_SUBTRANS111188 | SubTransmissionTIM_NST_SUBTRANS111188 | 22.6344 | 1188 | 1188 | Timaru | NST35 | Circuit Breaker-NST-CB35-Protection | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANSNST-CB711Protection | SubTransmission | HNT_NST_SUBTRANS | Hunt | NST7 | - | GEMA\860RP1788\AEL Transformer database | NST-CB7 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | HNT_NST_SUBTRANS7.62102355330306 | SubTransmissionHNT_NST_SUBTRANS11400 | SubTransmissionHNT_NST_SUBTRANS11400 | 7.621 | 400 | 400 | Hunt | NST7 | Circuit Breaker-NST-CB7-Protection | 11
DistributionFeederCB8_Barnard St11 | DistributionFeederCB8_Barnard StNST-CB811Protection | DistributionFeeder | CB8_Barnard St | 11 kV Bus | NST08 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB8 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 3.8105 | 15.242 | 15.242 | - | CB8_Barnard St3.81051177665153 | DistributionFeederCB8_Barnard St11200 | DistributionFeederCB8_Barnard St11200 | 3.8105 | 200 | 200 | 11 kV Bus | NST08 | Circuit Breaker-NST-CB8-Protection | 11
DistributionFeederCB8_Barnard St11 | DistributionFeederCB8_Barnard St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB8_Barnard St | NST08 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 194.9 | 0.93 | 1.01 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.54 | 0.82 | 432.2906 | 8.2362 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.2362 | CB8_Barnard St8.23624182157988 | DistributionFeederCB8_Barnard St11432.2905848 | DistributionFeederCB8_Barnard St11432.2905848 | 8.2362 | 432.2906 | 432.2906 | NST08 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB8_Barnard St11 | DistributionFeederCB8_Barnard St3c 0.15in² Cu PILC STA11- | DistributionFeeder | CB8_Barnard St | Joint | TEW1 | 3 | GEMA\General Cable\FB248 | 3c 0.15in² Cu PILC STA | Cable | - | - | 11 | 221 | 4.2106 | 221 | 4.2106 | 221 | 4.2106 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 332.67 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 172.5214 | 3.287 | 4.2106 | 4.2106 | 4.2106 | - | - | - | - | - | 3.287 | CB8_Barnard St3.2869748942244 | DistributionFeederCB8_Barnard St11172.52144 | DistributionFeederCB8_Barnard St11172.52144 | 3.287 | 172.5214 | 172.5214 | Joint | TEW1 | Cable-3c 0.15in² Cu PILC STA | 11
DistributionFeederCB9_Port 111 | DistributionFeederCB9_Port 1NST-CB911Protection | DistributionFeeder | CB9_Port 1 | 11 kV Bus | NST09 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB9 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB9_Port 15.79197790051033 | DistributionFeederCB9_Port 111304 | DistributionFeederCB9_Port 111304 | 5.792 | 304 | 304 | 11 kV Bus | NST09 | Circuit Breaker-NST-CB9-Protection | 11
DistributionFeederCB9_Port 111 | DistributionFeederCB9_Port 13/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB9_Port 1 | NST09 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 48.5 | 0.8 | 1 | 18.5 | 1 | 1.2 | 1 | 5 | 0.6 | 0.81 | 434.97 | 8.2873 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.2873 | CB9_Port 18.28729153745058 | DistributionFeederCB9_Port 111434.97 | DistributionFeederCB9_Port 111434.97 | 8.2873 | 434.97 | 434.97 | NST09 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB9_Port 111 | DistributionFeederCB9_Port 13c 300mm² Al XLPE MDPE11- | DistributionFeeder | CB9_Port 1 | Joint | TEX47 RMU | 3 | GEMA\General Cable\FB248 | 3c 300mm² Al XLPE MDPE | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1285.5 | 1.5 | 0.95 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.3 | 0.8 | 273.3264 | 5.2076 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 5.2076 | CB9_Port 15.20756733034883 | DistributionFeederCB9_Port 111273.3264 | DistributionFeederCB9_Port 111273.3264 | 5.2076 | 273.3264 | 273.3264 | Joint | TEX47 RMU | Cable-3c 300mm² Al XLPE MDPE | 11
DistributionFeederCB10_Fraser St11 | DistributionFeederCB10_Fraser StNST-CB1011Protection | DistributionFeeder | CB10_Fraser St | 11 kV Bus | NST10 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB10 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB10_Fraser St5.79197790051033 | DistributionFeederCB10_Fraser St11304 | DistributionFeederCB10_Fraser St11304 | 5.792 | 304 | 304 | 11 kV Bus | NST10 | Circuit Breaker-NST-CB10-Protection | 11
DistributionFeederCB10_Fraser St11 | DistributionFeederCB10_Fraser St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB10_Fraser St | NST10 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 160 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB10_Fraser St8.05524737440196 | DistributionFeederCB10_Fraser St11422.79084 | DistributionFeederCB10_Fraser St11422.79084 | 8.0552 | 422.7908 | 422.7908 | NST10 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB10_Fraser St11 | DistributionFeederCB10_Fraser St3c 300mm² Al XLPE11- | DistributionFeeder | CB10_Fraser St | Joint | Joint | 3 | GEMA\General Cable\FB248 | 3c 300mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 129.7 | 0.78 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 374.7643 | 7.1402 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.1402 | CB10_Fraser St7.14021927414401 | DistributionFeederCB10_Fraser St11374.76432 | DistributionFeederCB10_Fraser St11374.76432 | 7.1402 | 374.7643 | 374.7643 | Joint | Joint | Cable-3c 300mm² Al XLPE | 11
DistributionFeederCB10_Fraser St11 | DistributionFeederCB10_Fraser St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB10_Fraser St | Joint | TEW33 RMU | 4 | GEMA\General Cable\FB248 | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 251 | 4.7822 | 251 | 4.7822 | 251 | 4.7822 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | - | 1.4 | 0.95 | 18.5 | 0.952 | 1.2 | 1 | 2 | 0.3 | 0.88 | 199.7639 | 3.806 | 4.7822 | 4.7822 | 4.7822 | - | - | - | - | - | 3.806 | CB10_Fraser St3.80601293402754 | DistributionFeederCB10_Fraser St11199.763872 | DistributionFeederCB10_Fraser St11199.763872 | 3.806 | 199.7639 | 199.7639 | Joint | TEW33 RMU | Cable-3c 185mm² Al PILC SWAS | 11
Switching StationNST11 | Switching StationNSTNST-CB3111- | Switching Station | NST | NST32 | NST31 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB31 | Circuit Breaker | - | - | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | - | - | - | - | NST47.6313972081441 | Switching StationNST112500 | Switching StationNST112500 | 47.6314 | 2500 | 2500 | NST32 | NST31 | Circuit Breaker-NST-CB31 | 11
Switching StationNST11 | Switching StationNSTNST-CB3211- | Switching Station | NST | NST31 | NST32 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB32 | Circuit Breaker | - | - | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | - | - | - | - | NST47.6313972081441 | Switching StationNST112500 | Switching StationNST112500 | 47.6314 | 2500 | 2500 | NST31 | NST32 | Circuit Breaker-NST-CB32 | 11
DistributionFeederCB11_Hayes St11 | DistributionFeederCB11_Hayes StNST-CB1111Protection | DistributionFeeder | CB11_Hayes St | 11 kV Bus | NST11 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB11 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB11_Hayes St5.79197790051033 | DistributionFeederCB11_Hayes St11304 | DistributionFeederCB11_Hayes St11304 | 5.792 | 304 | 304 | 11 kV Bus | NST11 | Circuit Breaker-NST-CB11-Protection | 11
DistributionFeederCB11_Hayes St11 | DistributionFeederCB11_Hayes St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB11_Hayes St | NST11 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 184 | 0.93 | 1.01 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 423.3957 | 8.0668 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0668 | CB11_Hayes St8.06677182525108 | DistributionFeederCB11_Hayes St11423.3957168 | DistributionFeederCB11_Hayes St11423.3957168 | 8.0668 | 423.3957 | 423.3957 | NST11 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB11_Hayes St11 | DistributionFeederCB11_Hayes St3c 0.25in² Al PILC STAS11- | DistributionFeeder | CB11_Hayes St | Joint | TEW7 RMU | 3 | GEMA\General Cable\FB248 | 3c 0.25in² Al PILC STAS | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 275.7 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 206.8696 | 3.9414 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.9414 | CB11_Hayes St3.94139523515596 | DistributionFeederCB11_Hayes St11206.8696 | DistributionFeederCB11_Hayes St11206.8696 | 3.9414 | 206.8696 | 206.8696 | Joint | TEW7 RMU | Cable-3c 0.25in² Al PILC STAS | 11
DistributionFeederCB12_High St11 | DistributionFeederCB12_High StNST-CB1211Protection | DistributionFeeder | CB12_High St | 11 kV Bus | NST12 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB12 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB12_High St5.79197790051033 | DistributionFeederCB12_High St11304 | DistributionFeederCB12_High St11304 | 5.792 | 304 | 304 | 11 kV Bus | NST12 | Circuit Breaker-NST-CB12-Protection | 11
DistributionFeederCB12_High St11 | DistributionFeederCB12_High St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB12_High St | NST12 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 184 | 0.93 | 1.01 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.54 | 0.82 | 432.2906 | 8.2362 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.2362 | CB12_High St8.23624182157988 | DistributionFeederCB12_High St11432.2905848 | DistributionFeederCB12_High St11432.2905848 | 8.2362 | 432.2906 | 432.2906 | NST12 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB12_High St11 | DistributionFeederCB12_High St3c 185mm² Al PILC SWA11- | DistributionFeeder | CB12_High St | Joint | Joint | 3 | GEMA\General Cable\FB248 | 3c 185mm² Al PILC SWA | Cable | - | - | 11 | 315 | 6.0016 | 315 | 6.0016 | 315 | 6.0016 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 324.3 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 245.9016 | 4.6851 | 6.0016 | 6.0016 | 6.0016 | - | - | - | - | - | 4.6851 | CB12_High St4.68505471348727 | DistributionFeederCB12_High St11245.9016 | DistributionFeederCB12_High St11245.9016 | 4.6851 | 245.9016 | 245.9016 | Joint | Joint | Cable-3c 185mm² Al PILC SWA | 11
DistributionFeederCB12_High St11 | DistributionFeederCB12_High St3c 0.25in² Al PILC SWA11- | DistributionFeeder | CB12_High St | Joint | Joint | 4 | GEMA\General Cable\FB248 | 3c 0.25in² Al PILC SWA | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 42 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 206.8696 | 3.9414 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.9414 | CB12_High St3.94139523515596 | DistributionFeederCB12_High St11206.8696 | DistributionFeederCB12_High St11206.8696 | 3.9414 | 206.8696 | 206.8696 | Joint | Joint | Cable-3c 0.25in² Al PILC SWA | 11
DistributionFeederCB12_High St11 | DistributionFeederCB12_High St3c 185mm² Al XLPE11- | DistributionFeeder | CB12_High St | Joint | TEW37 RMU | 5 | GEMA\General Cable\FB248 | 3c 185mm² Al XLPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 7 | 1 | 1 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.54 | 0.82 | 292.5137 | 5.5731 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 5.5731 | CB12_High St5.57313411235839 | DistributionFeederCB12_High St11292.51368 | DistributionFeederCB12_High St11292.51368 | 5.5731 | 292.5137 | 292.5137 | Joint | TEW37 RMU | Cable-3c 185mm² Al XLPE | 11
DistributionFeederCB13_Port 211 | DistributionFeederCB13_Port 2NST-CB1311Protection | DistributionFeeder | CB13_Port 2 | 11 kV Bus | NST13 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB13 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB13_Port 25.79197790051033 | DistributionFeederCB13_Port 211304 | DistributionFeederCB13_Port 211304 | 5.792 | 304 | 304 | 11 kV Bus | NST13 | Circuit Breaker-NST-CB13-Protection | 11
DistributionFeederCB13_Port 211 | DistributionFeederCB13_Port 23/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB13_Port 2 | NST13 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 54.1 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB13_Port 28.05524737440196 | DistributionFeederCB13_Port 211422.79084 | DistributionFeederCB13_Port 211422.79084 | 8.0552 | 422.7908 | 422.7908 | NST13 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB13_Port 211 | DistributionFeederCB13_Port 23c 300mm² Al XLPE MDPE11- | DistributionFeeder | CB13_Port 2 | Joint | TEX50 RMU | 3 | GEMA\General Cable\FB248 | 3c 300mm² Al XLPE MDPE | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 1289.2 | 1.5 | 0.95 | 18.5 | 0.972 | 1.2 | 1 | 3 | 0.3 | 0.8 | 273.3264 | 5.2076 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 5.2076 | CB13_Port 25.20756733034883 | DistributionFeederCB13_Port 211273.3264 | DistributionFeederCB13_Port 211273.3264 | 5.2076 | 273.3264 | 273.3264 | Joint | TEX50 RMU | Cable-3c 300mm² Al XLPE MDPE | 11
SubTransmissionHNT_NST_SUBTRANS11 | SubTransmissionHNT_NST_SUBTRANSNST-CB1411Protection | SubTransmission | HNT_NST_SUBTRANS | Hunt | NST14 | - | GEMA\860RP1788\AEL Transformer database | NST-CB14 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | HNT_NST_SUBTRANS7.62102355330306 | SubTransmissionHNT_NST_SUBTRANS11400 | SubTransmissionHNT_NST_SUBTRANS11400 | 7.621 | 400 | 400 | Hunt | NST14 | Circuit Breaker-NST-CB14-Protection | 11
SubTransmissionTIM_NST_SUBTRANS11 | SubTransmissionTIM_NST_SUBTRANSNST-CB3611Protection | SubTransmission | TIM_NST_SUBTRANS | Timaru | NST36 | 3 | GEMA\860RP1788\AEL Transformer database | NST-CB36 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 2500 | 47.6314 | 2500 | 47.6314 | 2500 | 47.6314 | - | - | - | - | 1188 | 22.6344 | - | - | 1200 | 22.8631 | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 47.6314 | 47.6314 | 47.6314 | - | - | 22.6344 | 22.8631 | 22.8631 | - | TIM_NST_SUBTRANS22.6344399533101 | SubTransmissionTIM_NST_SUBTRANS111188 | SubTransmissionTIM_NST_SUBTRANS111188 | 22.6344 | 1188 | 1188 | Timaru | NST36 | Circuit Breaker-NST-CB36-Protection | 11
SubTransmissionGRM_NST_SUBTRANS11 | SubTransmissionGRM_NST_SUBTRANSNST-CB1511Protection | SubTransmission | GRM_NST_SUBTRANS | Grasmere | NST15 | - | GEMA\860RP1788\AEL Transformer database | NST-CB15 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 400 | 7.621 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 7.621 | 15.242 | 15.242 | - | GRM_NST_SUBTRANS7.62102355330306 | SubTransmissionGRM_NST_SUBTRANS11400 | SubTransmissionGRM_NST_SUBTRANS11400 | 7.621 | 400 | 400 | Grasmere | NST15 | Circuit Breaker-NST-CB15-Protection | 11
DistributionFeederCB16_Victoria St11 | DistributionFeederCB16_Victoria StNST-CB1611Protection | DistributionFeeder | CB16_Victoria St | 11 kV Bus | NST16 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB16 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB16_Victoria St5.79197790051033 | DistributionFeederCB16_Victoria St11304 | DistributionFeederCB16_Victoria St11304 | 5.792 | 304 | 304 | 11 kV Bus | NST16 | Circuit Breaker-NST-CB16-Protection | 11
DistributionFeederCB16_Victoria St11 | DistributionFeederCB16_Victoria St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB16_Victoria St | NST16 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 194.2 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB16_Victoria St8.05524737440196 | DistributionFeederCB16_Victoria St11422.79084 | DistributionFeederCB16_Victoria St11422.79084 | 8.0552 | 422.7908 | 422.7908 | NST16 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB16_Victoria St11 | DistributionFeederCB16_Victoria St3c 185mm² Al PILC SWAS11- | DistributionFeeder | CB16_Victoria St | Joint | TEP12 RMU | 3 | GEMA\General Cable\FB248 | 3c 185mm² Al PILC SWAS | Cable | - | - | 11 | 315 | 6.0016 | 315 | 6.0016 | 315 | 6.0016 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 119.3 | 0.78 | 1 | 18.5 | 0.952 | 1.2 | 1 | 5 | touch | 0.7 | 209.916 | 3.9994 | 6.0016 | 6.0016 | 6.0016 | - | - | - | - | - | 3.9994 | CB16_Victoria St3.99943695053791 | DistributionFeederCB16_Victoria St11209.916 | DistributionFeederCB16_Victoria St11209.916 | 3.9994 | 209.916 | 209.916 | Joint | TEP12 RMU | Cable-3c 185mm² Al PILC SWAS | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford StNST-CB1711Protection | DistributionFeeder | CB17_Stafford St | 11 kV Bus | NST17 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB17 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 200 | 3.8105 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 3.8105 | 15.242 | 15.242 | - | CB17_Stafford St3.81051177665153 | DistributionFeederCB17_Stafford St11200 | DistributionFeederCB17_Stafford St11200 | 3.8105 | 200 | 200 | 11 kV Bus | NST17 | Circuit Breaker-NST-CB17-Protection | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford St3/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB17_Stafford St | NST17 | Joint | 2 | GEMA\General Cable | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 187.9 | 0.9 | 1.01 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.54 | 0.82 | 432.2906 | 8.2362 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.2362 | CB17_Stafford St8.23624182157988 | DistributionFeederCB17_Stafford St11432.2905848 | DistributionFeederCB17_Stafford St11432.2905848 | 8.2362 | 432.2906 | 432.2906 | NST17 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford St3c 0.15in² Cu PILC SWA11- | DistributionFeeder | CB17_Stafford St | Joint | Joint | 3 | GEMA\General Cable\FB248 | 3c 0.15in² Cu PILC SWA | Cable | - | - | 11 | 221 | 4.2106 | 221 | 4.2106 | 221 | 4.2106 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 239.7 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 172.5214 | 3.287 | 4.2106 | 4.2106 | 4.2106 | - | - | - | - | - | 3.287 | CB17_Stafford St3.2869748942244 | DistributionFeederCB17_Stafford St11172.52144 | DistributionFeederCB17_Stafford St11172.52144 | 3.287 | 172.5214 | 172.5214 | Joint | Joint | Cable-3c 0.15in² Cu PILC SWA | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford St3c 0.25in² Al PILC DSTAS11- | DistributionFeeder | CB17_Stafford St | Joint | Joint | 4 | GEMA\General Cable\FB248 | 3c 0.25in² Al PILC DSTAS | Cable | - | - | 11 | 280 | 5.3347 | 280 | 5.3347 | 280 | 5.3347 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 397.3 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 218.5792 | 4.1645 | 5.3347 | 5.3347 | 5.3347 | - | - | - | - | - | 4.1645 | CB17_Stafford St4.16449307865535 | DistributionFeederCB17_Stafford St11218.5792 | DistributionFeederCB17_Stafford St11218.5792 | 4.1645 | 218.5792 | 218.5792 | Joint | Joint | Cable-3c 0.25in² Al PILC DSTAS | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford St3c 0.075in² Cu PILC STAS11- | DistributionFeeder | CB17_Stafford St | Joint | Joint | 5 | GEMA\General Cable\FB248 | 3c 0.075in² Cu PILC STAS | Cable | - | - | 11 | 174 | 3.3151 | 174 | 3.3151 | 174 | 3.3151 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 118 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 135.8314 | 2.5879 | 3.3151 | 3.3151 | 3.3151 | - | - | - | - | - | 2.5879 | CB17_Stafford St2.58793498459297 | DistributionFeederCB17_Stafford St11135.83136 | DistributionFeederCB17_Stafford St11135.83136 | 2.5879 | 135.8314 | 135.8314 | Joint | Joint | Cable-3c 0.075in² Cu PILC STAS | 11
DistributionFeederCB17_Stafford St11 | DistributionFeederCB17_Stafford St3c 0.25in² Cu PILC STAS11- | DistributionFeeder | CB17_Stafford St | Joint | TEW13 RMU | 6 | GEMA\General Cable\FB248 | 3c 0.25in² Cu PILC STAS | Cable | - | - | 11 | 340 | 6.4779 | 340 | 6.4779 | 340 | 6.4779 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | - | 30.8 | 1 | 1 | 18.5 | 0.952 | 1.2 | 1 | 4 | 0.54 | 0.82 | 265.4176 | 5.0569 | 6.4779 | 6.4779 | 6.4779 | - | - | - | - | - | 5.0569 | CB17_Stafford St5.05688445265292 | DistributionFeederCB17_Stafford St11265.4176 | DistributionFeederCB17_Stafford St11265.4176 | 5.0569 | 265.4176 | 265.4176 | Joint | TEW13 RMU | Cable-3c 0.25in² Cu PILC STAS | 11
DistributionFeederCB18_Redruth 211 | DistributionFeederCB18_Redruth 2NST-CB1811Protection | DistributionFeeder | CB18_Redruth 2 | 11 kV Bus | NST18 | 1 | GEMA\860RP1788\AEL Transformer database | NST-CB18 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 304 | 5.792 | - | - | 800 | 15.242 | 800 | 15.242 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 5.792 | 15.242 | 15.242 | - | CB18_Redruth 25.79197790051033 | DistributionFeederCB18_Redruth 211304 | DistributionFeederCB18_Redruth 211304 | 5.792 | 304 | 304 | 11 kV Bus | NST18 | Circuit Breaker-NST-CB18-Protection | 11
DistributionFeederCB18_Redruth 211 | DistributionFeederCB18_Redruth 23/1c 400mm² Al XLPE HPDE Screened11- | DistributionFeeder | CB18_Redruth 2 | NST18 | Joint | 2 | GEMA\General Cable\FB248 | 3/1c 400mm² Al XLPE HPDE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 217.5 | 0.8 | 1 | 18.5 | 0.972 | 1.2 | 1 | 5 | 0.6 | 0.81 | 422.7908 | 8.0552 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 8.0552 | CB18_Redruth 28.05524737440196 | DistributionFeederCB18_Redruth 211422.79084 | DistributionFeederCB18_Redruth 211422.79084 | 8.0552 | 422.7908 | 422.7908 | NST18 | Joint | Cable-3/1c 400mm² Al XLPE HPDE Screened | 11
DistributionFeederCB18_Redruth 211 | DistributionFeederCB18_Redruth 23c 300mm² Al XLPE CWS MDPE11- | DistributionFeeder | CB18_Redruth 2 | Joint | L783 RMU | 3 | GEMA\General Cable\FB248 | 3c 300mm² Al XLPE CWS MDPE | Cable | - | - | 11 | 370 | 7.0494 | 370 | 7.0494 | 370 | 7.0494 | - | - | - | - | - | - | - | - | - | - | - | - | 3c | Yes | 2194.6 | 0.78 | 1 | 18.5 | 0.972 | 1.2 | 1 | 4 | 0.45 | 0.76 | 273.3264 | 5.2076 | 7.0494 | 7.0494 | 7.0494 | - | - | - | - | - | 5.2076 | CB18_Redruth 25.20756733034883 | DistributionFeederCB18_Redruth 211273.3264 | DistributionFeederCB18_Redruth 211273.3264 | 5.2076 | 273.3264 | 273.3264 | Joint | L783 RMU | Cable-3c 300mm² Al XLPE CWS MDPE | 11
DistributionFeederNST11 | DistributionFeederNST11- | DistributionFeeder | NST | 11 kV Bus | 11 kV Bus | 0 | GEMA\Tech 1 |  | Switchboard | - | - | 11 | 3000 | 57.1577 | 3000 | 57.1577 | 3000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 57.1577 | 57.1577 | 57.1577 | - | - | - | - | - | - | NST57.1576766497729 | DistributionFeederNST113000 | DistributionFeederNST113000 | 57.1577 | 3000 | 3000 | 11 kV Bus | 11 kV Bus | Switchboard- | 11
--- | ----- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | --- | --- |  |  |  | - | - | --- | -
SubTransmissionATM11 | SubTransmissionATMTIM-CB273211Protection | SubTransmission | ATM | 11 kV Bus | CB2732 | 1 | TP Branch Report TIM.FDR.2732\AEL Transformer database | TIM-CB2732 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1068 | 20.3481 | 976 | 18.5953 | 3600 | 68.5892 | 2400 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.3481 | 68.5892 | 45.7261 | - | ATM20.3481328873192 | SubTransmissionATM111068 | SubTransmissionATM11976 | 20.3481 | 1068 | 976 | 11 kV Bus | CB2732 | Circuit Breaker-TIM-CB2732-Protection | 11
SubTransmissionATM11 | SubTransmissionATM2 x 3/1c 630mm² Cu 11- | SubTransmission | ATM | CB2732 | B774/T1 | 2 | AEL DWG 11422 | 2 x 3/1c 630mm² Cu | Cable | - | - | 11 | 1600 | 30.4841 | 1600 | 30.4841 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | 2 x 3/1c | - | 87.2 | 1 | 0.97 | 20 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 1120.544 | 21.3492 | 30.4841 | 30.4841 | 30.4841 | - | - | - | - | - | 21.3492 | ATM21.3492305412811 | SubTransmissionATM111120.544 | SubTransmissionATM111120.544 | 21.3492 | 1120.544 | 1120.544 | CB2732 | B774/T1 | Cable-2 x 3/1c 630mm² Cu | 11
ZoneSubstationATM33 | ZoneSubstationATMB774/T133HV Winding | ZoneSubstation | ATM | CB2732 | B774/T1 | 1 | AEL Transformer Database | B774/T1 | Transformer | - | HV Winding | 33 | 437.3866 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM | ZoneSubstationATM33 | ZoneSubstationATM33437.386567567898 |  |  | 437.3866 | CB2732 | B774/T1 | Transformer-B774/T1-HV Winding | 33
ZoneSubstationATM11 | ZoneSubstationATMB774/T111LV Winding | ZoneSubstation | ATM | CB2732 | B774/T1 | 1 | AEL Transformer Database | B774/T1 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM | ZoneSubstationATM11 | ZoneSubstationATM111312.1597027037 |  |  | 1312.1597 | CB2732 | B774/T1 | Transformer-B774/T1-LV Winding | 11
ZoneSubstationATM_233 | ZoneSubstationATM_2B774/T233HV Winding | ZoneSubstation | ATM_2 | CB2922 | B774/T2 | 1 | AEL Transformer Database | B774/T2 | Transformer | - | HV Winding | 33 | 437.3866 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM_2 | ZoneSubstationATM_233 | ZoneSubstationATM_233437.386567567898 |  |  | 437.3866 | CB2922 | B774/T2 | Transformer-B774/T2-HV Winding | 33
ZoneSubstationATM_211 | ZoneSubstationATM_2B774/T211LV Winding | ZoneSubstation | ATM_2 | CB2922 | B774/T2 | 1 | AEL Transformer Database | B774/T2 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM_2 | ZoneSubstationATM_211 | ZoneSubstationATM_2111312.1597027037 |  |  | 1312.1597 | CB2922 | B774/T2 | Transformer-B774/T2-LV Winding | 11
ZoneSubstationATM33 | ZoneSubstationATML40533- | ZoneSubstation | ATM | L405 | 33 kV Bus | 2 | GEMA | L405 | Air Break Switch | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM | ZoneSubstationATM33 | ZoneSubstationATM33 |  |  |  | L405 | 33 kV Bus | Air Break Switch-L405 | 33
SubTransmissionATM33 | SubTransmissionATMATM-L41333Protection | SubTransmission | ATM | 33 kV Bus | CB L413 | 3 | AEL Protection Database | ATM-L413 | Circuit Breaker | Relay Westinghouse RESCO | Protection | 33 | - | - | - | - | - | - | - | - | - | - | 240 | 13.7178 | - | - | 240 | 13.7178 | 240 | 13.7178 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 13.7178 | 13.7178 | 13.7178 | - | ATM13.7178423959455 | SubTransmissionATM33240 | SubTransmissionATM33240 | 13.7178 | 240 | 240 | 33 kV Bus | CB L413 | Circuit Breaker-ATM-L413-Protection | 33
SubTransmissionATM_211 | SubTransmissionATM_2TIM-CB292211Protection | SubTransmission | ATM_2 | 11 kV Bus | CB2922 | 1 | TP Branch Report TIM.FDR.2922\AEL Transformer database | TIM-CB2922 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1068 | 20.3481 | 976 | 18.5953 | 3600 | 68.5892 | 2400 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.3481 | 68.5892 | 45.7261 | - | ATM_220.3481328873192 | SubTransmissionATM_2111068 | SubTransmissionATM_211976 | 20.3481 | 1068 | 976 | 11 kV Bus | CB2922 | Circuit Breaker-TIM-CB2922-Protection | 11
SubTransmissionATM_211 | SubTransmissionATM_22 x 3/1c 630mm² Cu 11- | SubTransmission | ATM_2 | CB2922 | B774/T2 | 2 | AEL DWG 11422 | 2 x 3/1c 630mm² Cu | Cable | - | - | 11 | 1600 | 30.4841 | 1600 | 30.4841 | 1600 | 30.4841 | - | - | - | - | - | - | - | - | - | - | - | - | 2 x 3/1c | - | 96.9 | 1 | 0.97 | 20 | 0.95 | 1.2 | 1 | 4 | 0.45 | 0.76 | 1120.544 | 21.3492 | 30.4841 | 30.4841 | 30.4841 | - | - | - | - | - | 21.3492 | ATM_221.3492305412811 | SubTransmissionATM_2111120.544 | SubTransmissionATM_2111120.544 | 21.3492 | 1120.544 | 1120.544 | CB2922 | B774/T2 | Cable-2 x 3/1c 630mm² Cu | 11
ZoneSubstationATM_233 | ZoneSubstationATM_2L406 33- | ZoneSubstation | ATM_2 | L406 | 33 kV Bus | 2 | GEMA | L406 | Air Break Switch | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATM_2 | ZoneSubstationATM_233 | ZoneSubstationATM_233 |  |  |  | L406 | 33 kV Bus | Air Break Switch-L406 | 33
SubTransmissionATM_233 | SubTransmissionATM_2ATM-L41833Protection | SubTransmission | ATM_2 | 33 kV Bus | CB L418 | 3 | AEL Protection Database | ATM-L418 | Circuit Breaker | Relay Westinghouse RESCO | Protection | 33 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | 240 | 13.7178 | - | - | 240 | 13.7178 | 240 | 13.7178 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | - | 45.7261 | - | - | 13.7178 | 13.7178 | 13.7178 | - | ATM_213.7178423959455 | SubTransmissionATM_233240 | SubTransmissionATM_233240 | 13.7178 | 240 | 240 | 33 kV Bus | CB L418 | Circuit Breaker-ATM-L418-Protection | 33
SubTransmissionATM_233 | SubTransmissionATM_2ATM-L26933Protection | SubTransmission | ATM_2 | 33 kV Bus | CB L269 | 3 | AEL Protection Database | ATM-L269 | Circuit Breaker | Relay Westinghouse RESCO | Protection | 33 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | 240 | 13.7178 | - | - | 240 | 13.7178 | 240 | 13.7178 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | - | 45.7261 | - | - | 13.7178 | 13.7178 | 13.7178 | - | ATM_213.7178423959455 | SubTransmissionATM_233240 | SubTransmissionATM_233240 | 13.7178 | 240 | 240 | 33 kV Bus | CB L269 | Circuit Breaker-ATM-L269-Protection | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_PareoraDOG33- | SubTransmission | L413_L418_Pareora | CB L413 | Pole 03575 | 1 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.7 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | L413_L418_Pareora14.6814364082846 | SubTransmissionL413_L418_Pareora33256.858523103439 | SubTransmissionL413_L418_Pareora33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | CB L413 | Pole 03575 | OH Line-DOG | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_PareoraQuail33- | SubTransmission | L413_L418_Pareora | Pole 03575 | Pole 51637 | 2 | GEMA/AEL OH Amp Calc. | Quail | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 196.6 | 11.2372 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1123.9 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 11.2372 | - | - | - | - | - | - | L413_L418_Pareora11.2371992293454 | SubTransmissionL413_L418_Pareora33196.6 | SubTransmissionL413_L418_Pareora33196.6 | 11.2372 | 196.6 | 196.6 | Pole 03575 | Pole 51637 | OH Line-Quail | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_Pareora3/1c 630mm² AL XLPE33- | SubTransmission | L413_L418_Pareora | Pole 51637 | Joint | 3 | GEMA\General Cable | 3/1c 630mm² AL XLPE | Cable | - | - | 33 | 664 | 37.9527 | 664 | 37.9527 | 664 | 37.9527 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 781.6 | 1.3 | 0.96 | 20 | 0.97 | 1.2 | 1 | 3 | 0.7 | 0.9 | 556.4851 | 31.8074 | 37.9527 | 37.9527 | 37.9527 | - | - | - | - | - | 31.8074 | L413_L418_Pareora31.8073965493701 | SubTransmissionL413_L418_Pareora33556.48512 | SubTransmissionL413_L418_Pareora33556.48512 | 31.8074 | 556.4851 | 556.4851 | Pole 51637 | Joint | Cable-3/1c 630mm² AL XLPE | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_Pareora3/1c 400mm² AL XLPE33- | SubTransmission | L413_L418_Pareora | Joint | Joint | 4 | GEMA\General Cable | 3/1c 400mm² AL XLPE | Cable | - | - | 33 | 537 | 30.6937 | 537 | 30.6937 | 537 | 30.6937 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 23.4 | 1.1 | 0.97 | 20 | 0.97 | 1.2 | 1 | 4 | 0.55 | 0.79 | 399.158 | 22.8149 | 30.6937 | 30.6937 | 30.6937 | - | - | - | - | - | 22.8149 | L413_L418_Pareora22.8149442962738 | SubTransmissionL413_L418_Pareora33399.158007 | SubTransmissionL413_L418_Pareora33399.158007 | 22.8149 | 399.158 | 399.158 | Joint | Joint | Cable-3/1c 400mm² AL XLPE | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_PareoraIODINE33- | SubTransmission | L413_L418_Pareora | Pole 22553 | Pole 25018 | 6 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2531.7 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | L413_L418_Pareora15.7404518297676 | SubTransmissionL413_L418_Pareora33275.386487911596 | SubTransmissionL413_L418_Pareora33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | Pole 22553 | Pole 25018 | OH Line-IODINE | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_Pareora70mm² Cu33- | SubTransmission | L413_L418_Pareora | Pole 25018 | Pole 51464 | 7 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 33 | 327.5152 | 18.72 | - | - | 246.7053 | 14.1011 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 385.8 | - | - | - | - | - | - | - | - | - | - | - | 18.72 | - | 14.1011 | - | - | - | - | - | - | L413_L418_Pareora14.1010992383369 | SubTransmissionL413_L418_Pareora33246.70525579162 | SubTransmissionL413_L418_Pareora33246.70525579162 | 14.1011 | 246.7053 | 246.7053 | Pole 25018 | Pole 51464 | OH Line-70mm² Cu | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_PareoraIODINE33- | SubTransmission | L413_L418_Pareora | Pole 51464 | ABS L690 | 8 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11040.9 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | L413_L418_Pareora15.7404518297676 | SubTransmissionL413_L418_Pareora33275.386487911596 | SubTransmissionL413_L418_Pareora33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | Pole 51464 | ABS L690 | OH Line-IODINE | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_Pareora3/1c 400mm² AL XLPE HDPE Screened33- | SubTransmission | L413_L418_Pareora | ABS L690 | CB 2332 | 9 | GEMA\AEL Drawing 12052 (Incomer) | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 33 | 537 | 30.6937 | 537 | 30.6937 | 537 | 30.6937 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 42.2 | 0.8 | 1 | 20 | 0.97 | 1.2 | 1 | 1 | 0 | 1 | 520.89 | 29.7729 | 30.6937 | 30.6937 | 30.6937 | - | - | - | - | - | 29.7729 | L413_L418_Pareora29.7728621901002 | SubTransmissionL413_L418_Pareora33520.89 | SubTransmissionL413_L418_Pareora33520.89 | 29.7729 | 520.89 | 520.89 | ABS L690 | CB 2332 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_Pareora233433- | SubTransmission | L413_L418_Pareora | CB 2332 | 2334 | 10 | GEMA | 2334 | Switch | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | L413_L418_Pareora | SubTransmissionL413_L418_Pareora33 | SubTransmissionL413_L418_Pareora33 |  |  |  | CB 2332 | 2334 | Switch-2334 | 33
SubTransmissionL413_L418_Pareora33T1 | SubTransmissionL413_L418_PareoraPAR-CB233233- | SubTransmission | L413_L418_Pareora | CB 2332 | 33 kV Bus | 11 | GEMA\AEL Transformer database | PAR-CB2332 | Circuit Breaker | - | - | 33 | - | - | - | - | - | - | - | - | - | - | 320 | 18.2905 | - | - | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.2905 | - | 22.8631 | - | L413_L418_Pareora18.2904565279273 | SubTransmissionL413_L418_Pareora33320 | SubTransmissionL413_L418_Pareora33320 | 18.2905 | 320 | 320 | CB 2332 | 33 kV Bus | Circuit Breaker-PAR-CB2332 | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraDOG33- | SubTransmission | L413_L418_Pareora | CB L418 | Pole 03576 | 1 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 31.7 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | L413_L418_Pareora14.6814364082846 | SubTransmissionL413_L418_Pareora33256.858523103439 | SubTransmissionL413_L418_Pareora33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | CB L418 | Pole 03576 | OH Line-DOG | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraMINK33- | SubTransmission | L413_L418_Pareora | Pole 03576 | Pole 51637 | 2 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1123.8 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | L413_L418_Pareora10.7814586230328 | SubTransmissionL413_L418_Pareora33188.626607220145 | SubTransmissionL413_L418_Pareora33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | Pole 03576 | Pole 51637 | OH Line-MINK | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora3/1c 630mm² AL XLPE33- | SubTransmission | L413_L418_Pareora | Pole 51637 | Joint | 3 | GEMA\General Cable | 3/1c 630mm² AL XLPE | Cable | - | - | 33 | 664 | 37.9527 | 664 | 37.9527 | 664 | 37.9527 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 349.2 | 1.3 | 0.96 | 20 | 0.97 | 1.2 | 1 | 3 | 0.7 | 0.9 | 556.4851 | 31.8074 | 37.9527 | 37.9527 | 37.9527 | - | - | - | - | - | 31.8074 | L413_L418_Pareora31.8073965493701 | SubTransmissionL413_L418_Pareora33556.48512 | SubTransmissionL413_L418_Pareora33556.48512 | 31.8074 | 556.4851 | 556.4851 | Pole 51637 | Joint | Cable-3/1c 630mm² AL XLPE | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora3/1c 630mm² AL XLPE33- | SubTransmission | L413_L418_Pareora | Joint | Joint | 4 | GEMA\General Cable | 3/1c 630mm² AL XLPE | Cable | - | - | 33 | 664 | 37.9527 | 664 | 37.9527 | 664 | 37.9527 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 432.2 | 1.3 | 0.96 | 20 | 0.97 | 1.2 | 1 | 3 | 0.7 | 0.9 | 556.4851 | 31.8074 | 37.9527 | 37.9527 | 37.9527 | - | - | - | - | - | 31.8074 | L413_L418_Pareora31.8073965493701 | SubTransmissionL413_L418_Pareora33556.48512 | SubTransmissionL413_L418_Pareora33556.48512 | 31.8074 | 556.4851 | 556.4851 | Joint | Joint | Cable-3/1c 630mm² AL XLPE | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora3/1c 400mm² AL XLPE33- | SubTransmission | L413_L418_Pareora | Joint | Joint (VIC LB210) | 5 | GEMA\General Cable | 3/1c 400mm² AL XLPE | Cable | - | - | 33 | 537 | 30.6937 | 537 | 30.6937 | 537 | 30.6937 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 23.4 | 1.1 | 0.97 | 20 | 0.97 | 1.2 | 1 | 4 | 0.55 | 0.79 | 399.158 | 22.8149 | 30.6937 | 30.6937 | 30.6937 | - | - | - | - | - | 22.8149 | L413_L418_Pareora22.8149442962738 | SubTransmissionL413_L418_Pareora33399.158007 | SubTransmissionL413_L418_Pareora33399.158007 | 22.8149 | 399.158 | 399.158 | Joint | Joint (VIC LB210) | Cable-3/1c 400mm² AL XLPE | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraQUAIL33- | SubTransmission | L413_L418_Pareora | Pole 01408 | Pole 01401 | 8 | GEMA/AEL OH Amp Calc. | QUAIL | OH Line | - | - | 33 | 260.8763 | 14.9111 | - | - | 196.2065 | 11.2147 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 634.2 | - | - | - | - | - | - | - | - | - | - | - | 14.9111 | - | 11.2147 | - | - | - | - | - | - | L413_L418_Pareora11.2147099801896 | SubTransmissionL413_L418_Pareora33196.206540180183 | SubTransmissionL413_L418_Pareora33196.206540180183 | 11.2147 | 196.2065 | 196.2065 | Pole 01408 | Pole 01401 | OH Line-QUAIL | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora70mm² Cu33- | SubTransmission | L413_L418_Pareora | Pole 01401 | Pole 01402 | 9 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 33 | 327.5152 | 18.72 | - | - | 246.7053 | 14.1011 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 59.8 | - | - | - | - | - | - | - | - | - | - | - | 18.72 | - | 14.1011 | - | - | - | - | - | - | L413_L418_Pareora14.1010992383369 | SubTransmissionL413_L418_Pareora33246.70525579162 | SubTransmissionL413_L418_Pareora33246.70525579162 | 14.1011 | 246.7053 | 246.7053 | Pole 01401 | Pole 01402 | OH Line-70mm² Cu | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraDOG33- | SubTransmission | L413_L418_Pareora | Pole 01402 | Pole 03523 | 10 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 201.7 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | L413_L418_Pareora14.6814364082846 | SubTransmissionL413_L418_Pareora33256.858523103439 | SubTransmissionL413_L418_Pareora33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | Pole 01402 | Pole 03523 | OH Line-DOG | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora70mm² Cu33- | SubTransmission | L413_L418_Pareora | Pole 03523 | Pole 03522 | 11 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 33 | 327.5152 | 18.72 | - | - | 246.7053 | 14.1011 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 62.5 | - | - | - | - | - | - | - | - | - | - | - | 18.72 | - | 14.1011 | - | - | - | - | - | - | L413_L418_Pareora14.1010992383369 | SubTransmissionL413_L418_Pareora33246.70525579162 | SubTransmissionL413_L418_Pareora33246.70525579162 | 14.1011 | 246.7053 | 246.7053 | Pole 03523 | Pole 03522 | OH Line-70mm² Cu | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraQUAIL33- | SubTransmission | L413_L418_Pareora | Pole 03522 | Pole 03558 | 12 | GEMA/AEL OH Amp Calc. | QUAIL | OH Line | - | - | 33 | 260.8763 | 14.9111 | - | - | 196.2065 | 11.2147 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 876.2 | - | - | - | - | - | - | - | - | - | - | - | 14.9111 | - | 11.2147 | - | - | - | - | - | - | L413_L418_Pareora11.2147099801896 | SubTransmissionL413_L418_Pareora33196.206540180183 | SubTransmissionL413_L418_Pareora33196.206540180183 | 11.2147 | 196.2065 | 196.2065 | Pole 03522 | Pole 03558 | OH Line-QUAIL | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraIODINE33- | SubTransmission | L413_L418_Pareora | Pole 03558 | Pole 50498 | 13 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 368.604 | 21.0685 | - | - | 275.3865 | 15.7405 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11769.8 | - | - | - | - | - | - | - | - | - | - | - | 21.0685 | - | 15.7405 | - | - | - | - | - | - | L413_L418_Pareora15.7404518297676 | SubTransmissionL413_L418_Pareora33275.386487911596 | SubTransmissionL413_L418_Pareora33275.386487911596 | 15.7405 | 275.3865 | 275.3865 | Pole 03558 | Pole 50498 | OH Line-IODINE | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora3/1c 400mm² AL XLPE HDPE Screened33- | SubTransmission | L413_L418_Pareora | ABS L691 | CB 2382 | 14 | GEMA\AEL Drawing 12052 (Incomer) | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 33 | 537 | 30.6937 | 537 | 30.6937 | 537 | 30.6937 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 36.6 | 0.6 | 1.02 | 20 | 0.97 | 1.2 | 1 | 3 | 0.3 | 0.8 | 425.0462 | 24.2947 | 30.6937 | 30.6937 | 30.6937 | - | - | - | - | - | 24.2947 | L413_L418_Pareora24.2946555471218 | SubTransmissionL413_L418_Pareora33425.04624 | SubTransmissionL413_L418_Pareora33425.04624 | 24.2947 | 425.0462 | 425.0462 | ABS L691 | CB 2382 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_Pareora238433- | SubTransmission | L413_L418_Pareora | CB 2382 | 2384 | 15 | GEMA | 2384 | Switch | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | L413_L418_Pareora | SubTransmissionL413_L418_Pareora33 | SubTransmissionL413_L418_Pareora33 |  |  |  | CB 2382 | 2384 | Switch-2384 | 33
SubTransmissionL413_L418_Pareora33T2 | SubTransmissionL413_L418_PareoraPAR-CB238233- | SubTransmission | L413_L418_Pareora | CB 2382 | 33 kV Bus | 16 | GEMA\AEL Transformer database | PAR-CB2382 | Circuit Breaker | - | - | 33 | - | - | - | - | - | - | - | - | - | - | 320 | 18.3 | - | - | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.3 | - | 22.8631 | - | L413_L418_Pareora18.3 | SubTransmissionL413_L418_Pareora33320.166967459702 | SubTransmissionL413_L418_Pareora33320 | 18.3 | 320.167 | 320 | CB 2382 | 33 kV Bus | Circuit Breaker-PAR-CB2382 | 33
ZoneSubstationPAR33T1 | ZoneSubstationPARPAR-CB234233- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 1 | GEMA\AEL Drawing 12052\AEL Transformer database | PAR-CB2342 | Circuit Breaker | - | - | 33 | - | - | - | - | - | - | - | - | - | - | 320 | 18.2905 | - | - | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.2905 | - | 22.8631 | - | PAR18.2904565279273 | ZoneSubstationPAR33320 | ZoneSubstationPAR33320 | 18.2905 | 320 | 320 | 33 kV Bus | 11 kV Bus | Circuit Breaker-PAR-CB2342 | 33
ZoneSubstationPAR33T1 | ZoneSubstationPAR3/1c 400mm² AL XLPE HDPE Screened33- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 2 | GEMA\AEL Drawing 12052\General Cable (Before TX) | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 33 | 507 | 28.9789 | 507 | 28.9789 | 507 | 28.9789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 20.6 | 1.14 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 491.79 | 28.1096 | 28.9789 | 28.9789 | 28.9789 | - | - | - | - | - | 28.1096 | PAR28.1095737995918 | ZoneSubstationPAR33491.79 | ZoneSubstationPAR33491.79 | 28.1096 | 491.79 | 491.79 | 33 kV Bus | 11 kV Bus | Cable-3/1c 400mm² AL XLPE HDPE Screened | 33
ZoneSubstationPAR33T1 | ZoneSubstationPARB712/T133HV Winding | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 3 | GEMA\AEL Drawing 12052 | B712/T1 | Transformer | - | HV Winding | 33 | 262.4319 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PAR | ZoneSubstationPAR33 | ZoneSubstationPAR33262.431940540739 |  |  | 262.4319 | 33 kV Bus | 11 kV Bus | Transformer-B712/T1-HV Winding | 33
ZoneSubstationPAR11.22T1 | ZoneSubstationPARB712/T111.22LV Winding | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 3 | GEMA\AEL Drawing 12052 | B712/T1 | Transformer | - | LV Winding | 11.22 | 771.8586 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PAR | ZoneSubstationPAR11.22 | ZoneSubstationPAR11.22771.858648649232 |  |  | 771.8586 | 33 kV Bus | 11 kV Bus | Transformer-B712/T1-LV Winding | 11.22
ZoneSubstationPAR11.22T1 | ZoneSubstationPARPAR-CB3511.22- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 4 | GEMA\AEL Drawing 12052\ 860RP1606\AEL Transformer database | PAR-CB35 | Circuit Breaker | - | - | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 950 | 18.4619 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 18.4619 | - | - | - | PAR18.4619295578767 | ZoneSubstationPAR11.22950 | ZoneSubstationPAR11.22950 | 18.4619 | 950 | 950 | 33 kV Bus | 11 kV Bus | Circuit Breaker-PAR-CB35 | 11.22
ZoneSubstationPAR11.22T1 | ZoneSubstationPAR2 x 3/1c 400mm² AL XLPE HDPE Screened11.22- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 5 | GEMA\AEL Drawing 12052\General Cable | 2 x 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11.22 | 1074 | 20.8717 | 1074 | 20.8717 | 1074 | 20.8717 | - | - | - | - | - | - | - | - | - | - | - | - | 6/1c | No | 28.3 | 1.05 | 0.97 | 15 | 1 | 1.2 | 1 | 2 | 0.2 | 0.83 | 864.6774 | 16.8038 | 20.8717 | 20.8717 | 20.8717 | - | - | - | - | - | 16.8038 | PAR16.8038034200926 | ZoneSubstationPAR11.22864.6774 | ZoneSubstationPAR11.22864.6774 | 16.8038 | 864.6774 | 864.6774 | 33 kV Bus | 11 kV Bus | Cable-2 x 3/1c 400mm² AL XLPE HDPE Screened | 11.22
ZoneSubstationPAR33T1 | ZoneSubstationPAR3/1c 400mm² AL XLPE HDPE Screened33- | ZoneSubstation | PAR | 33 kV Bus | 33 kV Bus | 6 | GEMA\AEL Drawing 12052\General Cable | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 33 | 507 | 28.9789 | 507 | 28.9789 | 507 | 28.9789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | No | 16 | 1.1 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 491.79 | 28.1096 | 28.9789 | 28.9789 | 28.9789 | - | - | - | - | - | 28.1096 | PAR28.1095737995918 | ZoneSubstationPAR33491.79 | ZoneSubstationPAR33491.79 | 28.1096 | 491.79 | 491.79 | 33 kV Bus | 33 kV Bus | Cable-3/1c 400mm² AL XLPE HDPE Screened | 33
ZoneSubstationPAR33T2 | ZoneSubstationPARPAR-CB237233- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 1 | AEL Transformer database | PAR-CB2372 | Circuit Breaker | - | - | 33 | - | - | - | - | - | - | - | - | - | - | 320 | 18.2905 | - | - | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 18.2905 | - | 22.8631 | - | PAR18.2904565279273 | ZoneSubstationPAR33320 | ZoneSubstationPAR33320 | 18.2905 | 320 | 320 | 33 kV Bus | 11 kV Bus | Circuit Breaker-PAR-CB2372 | 33
ZoneSubstationPAR33T2 | ZoneSubstationPAR3/1c 400mm² AL XLPE HDPE Screened33- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 2 | GEMA\AEL Drawing 12052\General Cable (Before TX) | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 33 | 507 | 28.9789 | 507 | 28.9789 | 507 | 28.9789 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | Yes | 19.4 | 1.1 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 491.79 | 28.1096 | 28.9789 | 28.9789 | 28.9789 | - | - | - | - | - | 28.1096 | PAR28.1095737995918 | ZoneSubstationPAR33491.79 | ZoneSubstationPAR33491.79 | 28.1096 | 491.79 | 491.79 | 33 kV Bus | 11 kV Bus | Cable-3/1c 400mm² AL XLPE HDPE Screened | 33
ZoneSubstationPAR33T2 | ZoneSubstationPARB712/T233HV Winding | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 3 | GEMA\AEL Drawing 12052\General Cable | B712/T2 | Transformer | - | HV Winding | 33 | 262.4319 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PAR | ZoneSubstationPAR33 | ZoneSubstationPAR33262.431940540739 |  |  | 262.4319 | 33 kV Bus | 11 kV Bus | Transformer-B712/T2-HV Winding | 33
ZoneSubstationPAR11.22T2 | ZoneSubstationPARB712/T211.22LV Winding | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 4 | GEMA\AEL Drawing 12052\General Cable | B712/T2 | Transformer | - | LV Winding | 11.22 | 771.8586 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PAR | ZoneSubstationPAR11.22 | ZoneSubstationPAR11.22771.858648649232 |  |  | 771.8586 | 33 kV Bus | 11 kV Bus | Transformer-B712/T2-LV Winding | 11.22
ZoneSubstationPAR11.22T2 | ZoneSubstationPARPAR-CB3611.22- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 5 | AEL Transformer database | PAR-CB36 | Circuit Breaker | - | - | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 950 | 18.4619 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 18.4619 | - | - | - | PAR18.4619295578767 | ZoneSubstationPAR11.22950 | ZoneSubstationPAR11.22950 | 18.4619 | 950 | 950 | 33 kV Bus | 11 kV Bus | Circuit Breaker-PAR-CB36 | 11.22
ZoneSubstationPAR11.22T2 | ZoneSubstationPAR2 x 3/1c 400mm² AL XLPE HDPE Screened11.22- | ZoneSubstation | PAR | 33 kV Bus | 11 kV Bus | 6 | GEMA\AEL Drawing 12052\General Cable | 2 x 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11.22 | 1074 | 20.8717 | 1074 | 20.8717 | 1074 | 20.8717 | - | - | - | - | - | - | - | - | - | - | - | - | 6/1c | No | 35.9 | 0.92 | 0.93 | 15 | 1 | 1.2 | 1 | 2 | 0.3 | 0.85 | 848.997 | 16.4991 | 20.8717 | 20.8717 | 20.8717 | - | - | - | - | - | 16.4991 | PAR16.4990766408933 | ZoneSubstationPAR11.22848.997 | ZoneSubstationPAR11.22848.997 | 16.4991 | 848.997 | 848.997 | 33 kV Bus | 11 kV Bus | Cable-2 x 3/1c 400mm² AL XLPE HDPE Screened | 11.22
DistributionFeederCB3_Works No. 111.22 | DistributionFeederCB3_Works No. 1PAR-CB311.22Protection | DistributionFeeder | CB3_Works No. 1 | 11 kV Bus | PAR3 | 1 | AEL Transformer database | PAR-CB3 | Circuit Breaker | Relay SEL351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 300 | 5.8301 | - | - | - | - | 300 | 5.8301 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 5.8301 | - | 5.8301 | - | CB3_Works No. 15.83008301827684 | DistributionFeederCB3_Works No. 111.22300 | DistributionFeederCB3_Works No. 111.22300 | 5.8301 | 300 | 300 | 11 kV Bus | PAR3 | Circuit Breaker-PAR-CB3-Protection | 11.22
DistributionFeederCB3_Works No. 111.22 | DistributionFeederCB3_Works No. 13c 240mm² AL PILC DSTA11.22- | DistributionFeeder | CB3_Works No. 1 | PAR3 | No.1 RMU | 2 | AEL Transformer database | 3c 240mm² AL PILC DSTA | Cable | - | - | 11.22 | 345 | 6.7046 | 345 | 6.7046 | 345 | 6.7046 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 334.6 | 0.82 | 1 | 20 | 0.95 | 1.2 | 1 | 2 | 0.65 | 0.92 | 301.53 | 5.8598 | 6.7046 | 6.7046 | 6.7046 | - | - | - | - | - | 5.8598 | CB3_Works No. 15.85981644167005 | DistributionFeederCB3_Works No. 111.22301.53 | DistributionFeederCB3_Works No. 111.22301.53 | 5.8598 | 301.53 | 301.53 | PAR3 | No.1 RMU | Cable-3c 240mm² AL PILC DSTA | 11.22
DistributionFeederCB4_St Andrews11.22 | DistributionFeederCB4_St AndrewsPAR-CB411.22Protection | DistributionFeeder | CB4_St Andrews | 11 kV Bus | PAR4 | 1 | AEL Transformer database | PAR-CB4 | Circuit Breaker | Relay SEL351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | - | - | 600 | 11.6602 | - | - | - | - | - | - | 0.95 | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | - | 11.6602 | - | CB4_St Andrews4.89726973535255 | DistributionFeederCB4_St Andrews11.22252 | DistributionFeederCB4_St Andrews11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PAR4 | Circuit Breaker-PAR-CB4-Protection | 11.22
DistributionFeederCB4_St Andrews11.22 | DistributionFeederCB4_St Andrews3c 300mm² AL XLPE CWS MDPE11.22- | DistributionFeeder | CB4_St Andrews | PAR4 | L572 Link | 2 | AEL Transformer database | 3c 300mm² AL XLPE CWS MDPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 129.9 | 0.4 | 1 | 20 | 0.97 | 1.2 | 1 | 3 | 0.4 | 0.82 | 378.6104 | 7.3578 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.3578 | CB4_St Andrews7.35776687861001 | DistributionFeederCB4_St Andrews11.22378.6104 | DistributionFeederCB4_St Andrews11.22378.6104 | 7.3578 | 378.6104 | 378.6104 | PAR4 | L572 Link | Cable-3c 300mm² AL XLPE CWS MDPE | 11.22
DistributionFeederCB4_St Andrews11.22 | DistributionFeederCB4_St AndrewsDOG11.22- | DistributionFeeder | CB4_St Andrews | L572 Link | L570 ABS | 3 | AEL Transformer database | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1232.8 | - | - | - | 0.95 | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB4_St Andrews4.99168837881677 | DistributionFeederCB4_St Andrews11.22256.858523103439 | DistributionFeederCB4_St Andrews11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | L572 Link | L570 ABS | OH Line-DOG | 11.22
DistributionFeederCB5_Works No. 211.22 | DistributionFeederCB5_Works No. 2PAR-CB511.22Protection | DistributionFeeder | CB5_Works No. 2 | 11 kV Bus | PAR5 | 1 | AEL Transformer database | PAR-CB5 | Circuit Breaker | Relay SEL351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 300 | 5.8301 | - | - | - | - | 300 | 5.8301 | - | - | - | - | - | - | 0.95 | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 5.8301 | - | 5.8301 | - | CB5_Works No. 25.83008301827684 | DistributionFeederCB5_Works No. 211.22300 | DistributionFeederCB5_Works No. 211.22300 | 5.8301 | 300 | 300 | 11 kV Bus | PAR5 | Circuit Breaker-PAR-CB5-Protection | 11.22
DistributionFeederCB5_Works No. 211.22 | DistributionFeederCB5_Works No. 23c 240mm² AL PILC DSTA11.22- | DistributionFeeder | CB5_Works No. 2 | PAR5 | No.2 RMU | 2 | AEL Transformer database | 3c 240mm² AL PILC DSTA | Cable | - | - | 11.22 | 345 | 6.7046 | 345 | 6.7046 | 345 | 6.7046 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 334.6 | 0.82 | 1 | 20 | 0.95 | 1.2 | 1 | 2 | 0.65 | 0.92 | 301.53 | 5.8598 | 6.7046 | 6.7046 | 6.7046 | - | - | - | - | - | 5.8598 | CB5_Works No. 25.85981644167005 | DistributionFeederCB5_Works No. 211.22301.53 | DistributionFeederCB5_Works No. 211.22301.53 | 5.8598 | 301.53 | 301.53 | PAR5 | No.2 RMU | Cable-3c 240mm² AL PILC DSTA | 11.22
DistributionFeederCB6_Normanby11.22 | DistributionFeederCB6_NormanbyPAR-CB611.22Protection | DistributionFeeder | CB6_Normanby | 11 kV Bus | PAR6 | 1 | AEL Transformer database | PAR-CB6 | Circuit Breaker | Relay SEL351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | - | - | 600 | 11.6602 | - | - | - | - | - | - | 0.95 | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | - | 11.6602 | - | CB6_Normanby4.89726973535255 | DistributionFeederCB6_Normanby11.22252 | DistributionFeederCB6_Normanby11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PAR6 | Circuit Breaker-PAR-CB6-Protection | 11.22
DistributionFeederCB6_Normanby11.22 | DistributionFeederCB6_Normanby3c 300mm² AL XLPE PVC11.22- | DistributionFeeder | CB6_Normanby | PAR6 | Joint | 2 | AEL Transformer database | 3c 300mm² AL XLPE PVC | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | - | 0.4 | 1 | 20 | 0.95 | 1.2 | 1 | 3 | 0.4 | 0.82 | 370.804 | 7.2061 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.2061 | CB6_Normanby7.20606034503042 | DistributionFeederCB6_Normanby11.22370.804 | DistributionFeederCB6_Normanby11.22370.804 | 7.2061 | 370.804 | 370.804 | PAR6 | Joint | Cable-3c 300mm² AL XLPE PVC | 11.22
DistributionFeederCB6_Normanby11.22 | DistributionFeederCB6_Normanby3c 240mm² AL PILC DSTA11.22- | DistributionFeeder | CB6_Normanby | Joint | Link L179 | 3 | AEL Transformer database | 3c 240mm² AL PILC DSTA | Cable | - | - | 11.22 | 345 | 6.7046 | 345 | 6.7046 | 345 | 6.7046 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | - | 0.45 | 1 | 20 | 0.95 | 1.2 | 1 | 1 | 1 | 1 | 327.75 | 6.3694 | 6.7046 | 6.7046 | 6.7046 | - | - | - | - | - | 6.3694 | CB6_Normanby6.36936569746745 | DistributionFeederCB6_Normanby11.22327.75 | DistributionFeederCB6_Normanby11.22327.75 | 6.3694 | 327.75 | 327.75 | Joint | Link L179 | Cable-3c 240mm² AL PILC DSTA | 11.22
DistributionFeederCB6_Normanby11.22 | DistributionFeederCB6_NormanbyRANGO11.22- | DistributionFeeder | CB6_Normanby | Link L179 | Pole 36354 | 4 | AEL Transformer database | RANGO | OH Line | - | - | 11.22 | 271.0582 | 5.2676 | - | - | 204.0399 | 3.9652 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.95 | - | - | - | - | - | - | - | 5.2676 | - | 3.9652 | - | - | - | - | - | - | CB6_Normanby3.96523107614148 | DistributionFeederCB6_Normanby11.22204.039860000834 | DistributionFeederCB6_Normanby11.22204.039860000834 | 3.9652 | 204.0399 | 204.0399 | Link L179 | Pole 36354 | OH Line-RANGO | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_HolmestationPAR-CB711.22Protection | DistributionFeeder | CB7_Holmestation | 11 kV Bus | PAR7 | 1 | AEL Transformer database | PAR-CB7 | Circuit Breaker | Relay SEL351S-6 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | - | - | 600 | 11.6602 | - | - | - | - | - | - | 0.95 | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | - | 11.6602 | - | CB7_Holmestation4.89726973535255 | DistributionFeederCB7_Holmestation11.22252 | DistributionFeederCB7_Holmestation11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PAR7 | Circuit Breaker-PAR-CB7-Protection | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_Holmestation3c 300mm² AL XLPE PVC11.22- | DistributionFeeder | CB7_Holmestation | PAR7 | Joint | 2 | GEMA\AEL Drawing 12052\General Cable | 3c 300mm² AL XLPE PVC | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 9.1 | 0.4 | 1 | 20 | 0.95 | 1.2 | 1 | 3 | 0.4 | 0.82 | 370.804 | 7.2061 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.2061 | CB7_Holmestation7.20606034503042 | DistributionFeederCB7_Holmestation11.22370.804 | DistributionFeederCB7_Holmestation11.22370.804 | 7.2061 | 370.804 | 370.804 | PAR7 | Joint | Cable-3c 300mm² AL XLPE PVC | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_Holmestation3c 240mm² AL PILC DSTA11.22- | DistributionFeeder | CB7_Holmestation | Joint | Link L174 | 3 | GEMA\AEL Drawing 12052\General Cable | 3c 240mm² AL PILC DSTA | Cable | - | - | 11.22 | 345 | 6.7046 | 345 | 6.7046 | 345 | 6.7046 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | - | 0.45 | 1 | 20 | 0.95 | 1.2 | 1 | 1 | 1 | 1 | 327.75 | 6.3694 | 6.7046 | 6.7046 | 6.7046 | - | - | - | - | - | 6.3694 | CB7_Holmestation6.36936569746745 | DistributionFeederCB7_Holmestation11.22327.75 | DistributionFeederCB7_Holmestation11.22327.75 | 6.3694 | 327.75 | 327.75 | Joint | Link L174 | Cable-3c 240mm² AL PILC DSTA | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_HolmestationWeke11.22- | DistributionFeeder | CB7_Holmestation | Link L174 | Pole 41703 | 4 | GEMA/AEL OH Amp Calc. | Weke | OH Line | - | - | 11.22 | 371.2951 | 7.2156 | - | - | 277.4806 | 5.3924 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 144.5 | - | - | - | - | - | - | - | - | - | - | - | 7.2156 | - | 5.3924 | - | - | - | - | - | - | CB7_Holmestation5.39244897989988 | DistributionFeederCB7_Holmestation11.22277.480558835697 | DistributionFeederCB7_Holmestation11.22277.480558835697 | 5.3924 | 277.4806 | 277.4806 | Link L174 | Pole 41703 | OH Line-Weke | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_HolmestationDOG11.22- | DistributionFeeder | CB7_Holmestation | Pole 41703 | L571 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1158.4 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB7_Holmestation4.99168837881677 | DistributionFeederCB7_Holmestation11.22256.858523103439 | DistributionFeederCB7_Holmestation11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | Pole 41703 | L571 | OH Line-DOG | 11.22
DistributionFeederCB7_Holmestation11.22 | DistributionFeederCB7_HolmestationMINK11.22- | DistributionFeeder | CB7_Holmestation | L571 | Pole 43326 | 6 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11.22 | 250.5823 | 4.8697 | - | - | 188.6266 | 3.6657 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 29.22 | - | - | - | - | - | - | - | - | - | - | - | 4.8697 | - | 3.6657 | - | - | - | - | - | - | CB7_Holmestation3.66569593183114 | DistributionFeederCB7_Holmestation11.22188.626607220145 | DistributionFeederCB7_Holmestation11.22188.626607220145 | 3.6657 | 188.6266 | 188.6266 | L571 | Pole 43326 | OH Line-MINK | 11.22
--- | ----- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | --- | --- |  |  |  | - | - | --- | -
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPointQUAIL33- | SubTransmission | L269_PleasantPoint | CB L269 | Pole 872745 | 1 | GEMA/AEL OH Amp Calc. | QUAIL | OH Line | - | - | 33 | 260.8763 | 14.9111 | 220 | 12.5747 | 196.2065 | 11.2147 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2061.7 | - | - | - | - | - | - | - | - | - | - | - | 14.9111 | 12.5747 | 11.2147 | - | - | - | - | - | - | L269_PleasantPoint11.2147099801896 | SubTransmissionL269_PleasantPoint33196.206540180183 | SubTransmissionL269_PleasantPoint33196.206540180183 | 11.2147 | 196.2065 | 196.2065 | CB L269 | Pole 872745 | OH Line-QUAIL | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPoint3c 95mm² AL XLPE PVC screened33- | SubTransmission | L269_PleasantPoint | Pole 872745 | Joint | 2 | GEMA/Nexans | 3c 95mm² AL XLPE PVC screened | Cable | - | - | 33 | 256 | 14.6324 | 256 | 14.6324 | 256 | 14.6324 | - | - | - | - | - | - | - | - | - | - | - | - | - | Yes | 800 | 1.4 | 0.91 | 20 | 0.97 | 1.2 | 1 | 2 | 0.6 | 0.91 | 205.6338 | 11.7535 | 14.6324 | 14.6324 | 14.6324 | - | - | - | - | - | 11.7535 | L269_PleasantPoint11.7535497914027 | SubTransmissionL269_PleasantPoint33205.633792 | SubTransmissionL269_PleasantPoint33205.633792 | 11.7535 | 205.6338 | 205.6338 | Pole 872745 | Joint | Cable - 3c 95mm² AL XLPE PVC screened | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPoint3/185mm2 Al XLPE PVC, 33 kV33- | SubTransmission | L269_PleasantPoint | Joint | Pole 873942 | 3 | GEMA/Nexans | 3/185mm2 Al XLPE PVC, 33 kV | Cable | - | - | 33 | 367 | 20.9769 | 367 | 20.9769 | 367 | 20.9769 | - | - | - | - | - | - | - | - | - | - | - | - | - | Yes | 1600 | 1.4 | 0.91 | 20 | 0.97 | 1.2 | 1 | 2 | 0.7 | 1 | 323.9509 | 18.5163 | 20.9769 | 20.9769 | 20.9769 | - | - | - | - | - | 18.5163 | L269_PleasantPoint18.5162807926029 | SubTransmissionL269_PleasantPoint33323.9509 | SubTransmissionL269_PleasantPoint33323.9509 | 18.5163 | 323.9509 | 323.9509 | Joint | Pole 873942 | Cable - 3/185mm2 Al XLPE PVC, 33 kV | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPointDOG33- | SubTransmission | L269_PleasantPoint | Pole 24384 | Pole 24351 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 772.8 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | L269_PleasantPoint14.6814364082846 | SubTransmissionL269_PleasantPoint33256.858523103439 | SubTransmissionL269_PleasantPoint33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | Pole 24384 | Pole 24351 | OH Line-DOG | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPoint19/14 Cu33- | SubTransmission | L269_PleasantPoint | Pole 24351 | Pole 24349 | 5 | GEMA/AEL OH Amp Calc. | 19/14 Cu | OH Line | - | - | 33 | 320.5975 | 18.3246 | - | - | 241.6125 | 13.81 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 48.7 | - | - | - | - | - | - | - | - | - | - | - | 18.3246 | - | 13.81 | - | - | - | - | - | - | L269_PleasantPoint13.8100068326806 | SubTransmissionL269_PleasantPoint33241.612459465415 | SubTransmissionL269_PleasantPoint33241.612459465415 | 13.81 | 241.6125 | 241.6125 | Pole 24351 | Pole 24349 | OH Line-19/14 Cu | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPointWeke33- | SubTransmission | L269_PleasantPoint | Pole 24349 | Pole 24318 | 6 | GEMA/AEL OH Amp Calc. | Weke | OH Line | - | - | 33 | 371.2951 | 21.2224 | - | - | 277.4806 | 15.8601 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 757.4 | - | - | - | - | - | - | - | - | - | - | - | 21.2224 | - | 15.8601 | - | - | - | - | - | - | L269_PleasantPoint15.8601440585291 | SubTransmissionL269_PleasantPoint33277.480558835697 | SubTransmissionL269_PleasantPoint33277.480558835697 | 15.8601 | 277.4806 | 277.4806 | Pole 24349 | Pole 24318 | OH Line-Weke | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPointDOG33- | SubTransmission | L269_PleasantPoint | Pole 24318 | L247 ABS | 7 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11823.5 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | L269_PleasantPoint14.6814364082846 | SubTransmissionL269_PleasantPoint33256.858523103439 | SubTransmissionL269_PleasantPoint33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | Pole 24318 | L247 ABS | OH Line-DOG | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPoint3/1c 95mm² AL XLPE PVC screened33- | SubTransmission | L269_PleasantPoint | L247 ABS | L994 ABS | 8 | GEMA\General Cable | 3/1c 95mm² AL XLPE PVC screened | Cable | - | - | 33 | 248 | 14.1751 | 248 | 14.1751 | 248 | 14.1751 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | 97.7 | 1.6 | 0.91 | 15 | 1 | 1 | 1.07 | 5 | 0.3 | 0.71 | 171.4491 | 9.7996 | 14.1751 | 14.1751 | 14.1751 | - | - | - | - | - | 9.7996 | L269_PleasantPoint9.79963199106388 | SubTransmissionL269_PleasantPoint33171.449096 | SubTransmissionL269_PleasantPoint33171.449096 | 9.7996 | 171.4491 | 171.4491 | L247 ABS | L994 ABS | Cable-3/1c 95mm² AL XLPE PVC screened | 33
SubTransmissionL269_PleasantPoint33 | SubTransmissionL269_PleasantPoint70mm² Cu33- | SubTransmission | L269_PleasantPoint | L994 ABS | CB L250 | 9 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 33 | 247 | 14.1179 | - | - | 246.7053 | 14.1011 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8.1 | - | - | - | - | - | - | - | - | - | - | - | 14.1179 | - | 14.1011 | - | - | - | - | - | - | L269_PleasantPoint14.1010992383369 | SubTransmissionL269_PleasantPoint33246.70525579162 | SubTransmissionL269_PleasantPoint33246.70525579162 | 14.1011 | 246.7053 | 246.7053 | L994 ABS | CB L250 | OH Line-70mm² Cu | 33
ZoneSubstationPLP33 | ZoneSubstationPLPPLP-L25033- | ZoneSubstation | PLP | CB L250 | 33 kV Bus | 1 | GEMA\AEL Drawing 7586-04\AEL Transformer database | PLP-L250 | Circuit Breaker | - | - | 33 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | 134 | 7.6591 | - | - | - | - | 200 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | - | 22.8631 | - | - | 7.6591 | - | 11.4315 | - | PLP7.65912867106957 | ZoneSubstationPLP33134 | ZoneSubstationPLP33134 | 7.6591 | 134 | 134 | CB L250 | 33 kV Bus | Circuit Breaker-PLP-L250 | 33
ZoneSubstationPLP33 | ZoneSubstationPLPB1212/T133HV Winding | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 2 | GEMA\AEL Drawing 7586-04 | B1212/T1 | Transformer | - | HV Winding | 33 | 109.3466 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLP | ZoneSubstationPLP33 | ZoneSubstationPLP33109.346641891975 |  |  | 109.3466 | 33 kV Bus | 11 kV Bus | Transformer-B1212/T1-HV Winding | 33
ZoneSubstationPLP11.22 | ZoneSubstationPLPB1212/T111.22LV Winding | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 4 | GEMA\AEL Drawing 7586-04 | B1212/T1 | Transformer | - | LV Winding | 11.22 | 321.6078 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLP | ZoneSubstationPLP11.22 | ZoneSubstationPLP11.22321.607770270513 |  |  | 321.6078 | 33 kV Bus | 11 kV Bus | Transformer-B1212/T1-LV Winding | 11.22
ZoneSubstationPLP11.22 | ZoneSubstationPLP70mm² Cu11.22- | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 5 | GEMA/AEL OH Amp Calc. | 70mm² Cu | OH Line | - | - | 11.22 | 417 | 8.1038 | - | - | 362 | 7.035 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.1 | - | - | - | - | - | - | - | - | - | - | - | 8.1038 | - | 7.035 | - | - | - | - | - | - | PLP7.03496684205405 | ZoneSubstationPLP11.22362 | ZoneSubstationPLP11.22362 | 7.035 | 362 | 362 | 33 kV Bus | 11 kV Bus | OH Line-70mm² Cu | 11.22
ZoneSubstationPLP11.22 | ZoneSubstationPLP-11.22- | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 6 | GEMA/AEL OH Amp Calc. | - | OH Line | - | - | 11.22 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.68 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PLP | ZoneSubstationPLP11.22 | ZoneSubstationPLP11.22 |  |  |  | 33 kV Bus | 11 kV Bus | OH Line-- | 11.22
ZoneSubstationPLP11.22 | ZoneSubstationPLP3c 300mm² AL XLPE MPDE11.22- | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 7 | GEMA\AEL Drawing 7586-04 | 3c 300mm² AL XLPE MPDE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 24.8 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 1 | 0 | 1 | 479.0155 | 9.309 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 9.309 | PLP9.25039838899925 | ZoneSubstationPLP11.22476 | ZoneSubstationPLP11.22476 | 9.2504 | 476 | 476 | 33 kV Bus | 11 kV Bus | Cable-3c 300mm² AL XLPE MPDE | 11.22
ZoneSubstationPLP11.22 | ZoneSubstationPLPPLP-CB311.22Protection | ZoneSubstation | PLP | 33 kV Bus | 11 kV Bus | 8 | GEMA\AEL Drawing 7586-04\AEL Transformer database | PLP-CB3 | Circuit Breaker | Relay SEL351S | Protection | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 348 | 6.7629 | - | - | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 6.7629 | 11.6602 | 11.6602 | - | PLP6.76289630120114 | ZoneSubstationPLP11.22348 | ZoneSubstationPLP11.22348 | 6.7629 | 348 | 348 | 33 kV Bus | 11 kV Bus | Circuit Breaker-PLP-CB3-Protection | 11.22
DistributionFeederCB1_Waitawa11.22 | DistributionFeederCB1_WaitawaPLP-CB111.22Protection | DistributionFeeder | CB1_Waitawa | 11 kV Bus | PLPTCB 1 | 1 | GEMA\AEL Drawing 11997\AEL Transformer database | PLP-CB1 | Circuit Breaker | Relay SEL351A | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | 7.7734 | 7.7734 | - | CB1_Waitawa4.89726973535255 | DistributionFeederCB1_Waitawa11.22252 | DistributionFeederCB1_Waitawa11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PLPTCB 1 | Circuit Breaker-PLP-CB1-Protection | 11.22
DistributionFeederCB1_Waitawa11.22 | DistributionFeederCB1_Waitawa3c 150mm² Al PILC STA11.22- | DistributionFeeder | CB1_Waitawa | PLPTCB 1 | Joint | 2 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3c 150mm² Al PILC STA | Cable | - | - | 11.22 | 265 | 5.1499 | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 90.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 200.0091 | 3.8869 | 5.1499 | 4.7612 | 4.7612 | - | - | - | - | - | 3.8869 | CB1_Waitawa3.88689849365593 | DistributionFeederCB1_Waitawa11.22200.00908125 | DistributionFeederCB1_Waitawa11.22200.00908125 | 3.8869 | 200.0091 | 200.0091 | PLPTCB 1 | Joint | Cable-3c 150mm² Al PILC STA | 11.22
DistributionFeederCB1_Waitawa11.22 | DistributionFeederCB1_Waitawa3x1c 185mm² Al XLPE11.22- | DistributionFeeder | CB1_Waitawa | Joint | Fuse L260 | 3 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3x1c 185mm² Al XLPE | Cable | - | - | 11.22 | 265 | 5.1499 | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 90.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 200.0091 | 3.8869 | 5.1499 | 4.7612 | 4.7612 | - | - | - | - | - | 3.8869 | CB1_Waitawa3.88689849365593 | DistributionFeederCB1_Waitawa11.22200.00908125 | DistributionFeederCB1_Waitawa11.22200.00908125 | 3.8869 | 200.0091 | 200.0091 | Joint | Fuse L260 | Cable-3x1c 185mm² Al XLPE | 11.22
DistributionFeederCB1_Waitawa11.22 | DistributionFeederCB1_WaitawaFerret11.22- | DistributionFeeder | CB1_Waitawa |  | Fuse L260 | 4 | GEMA | Ferret | OH Line | - | - | 11.22 | 148 | 2.8762 | 148 | 2.8762 | 148 | 2.8762 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 90.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | - | - | 2.8762 | 2.8762 | 2.8762 | - | - | - | - | - | - | CB1_Waitawa2.87617428901658 | DistributionFeederCB1_Waitawa11.22148 | DistributionFeederCB1_Waitawa11.22148 | 2.8762 | 148 | 148 | 0 | Fuse L260 | OH Line-Ferret | 11.22
DistributionFeederCB2_Sutherlands11.22 | DistributionFeederCB2_SutherlandsPLP-CB211.22Protection | DistributionFeeder | CB2_Sutherlands | 11 kV Bus | PLPTCB 2 | 1 | GEMA\AEL Drawing 11997\AEL Transformer database | PLP-CB2 | Circuit Breaker | Relay SEL351A | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | 7.7734 | 7.7734 | - | CB2_Sutherlands4.89726973535255 | DistributionFeederCB2_Sutherlands11.22252 | DistributionFeederCB2_Sutherlands11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PLPTCB 2 | Circuit Breaker-PLP-CB2-Protection | 11.22
DistributionFeederCB2_Sutherlands11.22 | DistributionFeederCB2_Sutherlands3c 150mm² Al PILC STA11.22- | DistributionFeeder | CB2_Sutherlands | PLPTCB 2 | Link L254 | 2 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3c 150mm² Al PILC STA | Cable | - | - | 11.22 | 265 | 5.1499 | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 108 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 200.0091 | 3.8869 | 5.1499 | 4.7612 | 4.7612 | - | - | - | - | - | 3.8869 | CB2_Sutherlands3.88689849365593 | DistributionFeederCB2_Sutherlands11.22200.00908125 | DistributionFeederCB2_Sutherlands11.22200.00908125 | 3.8869 | 200.0091 | 200.0091 | PLPTCB 2 | Link L254 | Cable-3c 150mm² Al PILC STA | 11.22
DistributionFeederCB2_Sutherlands11.22 | DistributionFeederCB2_Sutherlands7/10 Cu11.22- | DistributionFeeder | CB2_Sutherlands | Link L254 |  | 3 | GEMA | 7/10 Cu | OH Line | - | - | 11.22 | 215 | 4.1782 | 215 | 4.1782 | 215 | 4.1782 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 108 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | - | - | 4.1782 | 4.1782 | 4.1782 | - | - | - | - | - | - | CB2_Sutherlands4.1782261630984 | DistributionFeederCB2_Sutherlands11.22215 | DistributionFeederCB2_Sutherlands11.22215 | 4.1782 | 215 | 215 | Link L254 | 0 | OH Line-7/10 Cu | 11.22
DistributionFeederCB4_Totara Valley11.22 | DistributionFeederCB4_Totara ValleyPLP-CB411.22Protection | DistributionFeeder | CB4_Totara Valley | 11 kV Bus | PLPTCB 4 | 1 | GEMA\AEL Drawing 11997\AEL Transformer database | PLP-CB4 | Circuit Breaker | Relay SEL351A | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | 0.75 | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | 7.7734 | 7.7734 | - | CB4_Totara Valley4.89726973535255 | DistributionFeederCB4_Totara Valley11.22252 | DistributionFeederCB4_Totara Valley11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PLPTCB 4 | Circuit Breaker-PLP-CB4-Protection | 11.22
DistributionFeederCB4_Totara Valley11.22 | DistributionFeederCB4_Totara Valley3c 150mm² Al PILC STA11.22- | DistributionFeeder | CB4_Totara Valley | PLPTCB 4 | Link L262 | 2 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3c 150mm² Al PILC STA | Cable | - | - | 11.22 | 265 | 5.1499 | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 152.4 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 200.0091 | 3.8869 | 5.1499 | 4.7612 | 4.7612 | - | - | - | - | - | 3.8869 | CB4_Totara Valley3.88689849365593 | DistributionFeederCB4_Totara Valley11.22200.00908125 | DistributionFeederCB4_Totara Valley11.22200.00908125 | 3.8869 | 200.0091 | 200.0091 | PLPTCB 4 | Link L262 | Cable-3c 150mm² Al PILC STA | 11.22
DistributionFeederCB4_Totara Valley11.22 | DistributionFeederCB4_Totara ValleyMink 11.22- | DistributionFeeder | CB4_Totara Valley | Link L262 | B1088 | 3 | GEMA | Mink | OH Line | - | - | 11.22 | 189 | 3.673 | 189 | 3.673 | 189 | 3.673 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 152.4 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | - | - | 3.673 | 3.673 | 3.673 | - | - | - | - | - | - | CB4_Totara Valley3.67295230151441 | DistributionFeederCB4_Totara Valley11.22189 | DistributionFeederCB4_Totara Valley11.22189 | 3.673 | 189 | 189 | Link L262 | B1088 | OH Line-Mink | 11.22
DistributionFeederCB5_Pleasant Point Township11.22 | DistributionFeederCB5_Pleasant Point TownshipPLP-CB511.22Protection | DistributionFeeder | CB5_Pleasant Point Township | 11 kV Bus | PLPTCB 5 | 1 | GEMA\AEL Drawing 11997\AEL Transformer database | PLP-CB5 | Circuit Breaker | Relay SEL351A | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 252 | 4.8973 | - | - | 400 | 7.7734 | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | 0.75 | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 4.8973 | 7.7734 | 7.7734 | - | CB5_Pleasant Point Township4.89726973535255 | DistributionFeederCB5_Pleasant Point Township11.22252 | DistributionFeederCB5_Pleasant Point Township11.22252 | 4.8973 | 252 | 252 | 11 kV Bus | PLPTCB 5 | Circuit Breaker-PLP-CB5-Protection | 11.22
DistributionFeederCB5_Pleasant Point Township11.22 | DistributionFeederCB5_Pleasant Point Township3c 150mm² Al PILC STA11.22- | DistributionFeeder | CB5_Pleasant Point Township | PLPTCB 5 | Joint | 2 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3c 150mm² Al PILC STA | Cable | - | - | 11.22 | 265 | 5.1499 | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 40.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 200.0091 | 3.8869 | 5.1499 | 4.7612 | 4.7612 | - | - | - | - | - | 3.8869 | CB5_Pleasant Point Township3.88689849365593 | DistributionFeederCB5_Pleasant Point Township11.22200.00908125 | DistributionFeederCB5_Pleasant Point Township11.22200.00908125 | 3.8869 | 200.0091 | 200.0091 | PLPTCB 5 | Joint | Cable-3c 150mm² Al PILC STA | 11.22
DistributionFeederCB5_Pleasant Point Township11.22 | DistributionFeederCB5_Pleasant Point Township3 x 1c 185mm² Al XLPE11.22- | DistributionFeeder | CB5_Pleasant Point Township | Joint | Link L263 | 3 | GEMA\AEL Drawing 11997\General Cable Belted 11kV | 3 x 1c 185mm² Al XLPE | Cable | - | - | 11.22 |  | - | 245 | 4.7612 | 245 | 4.7612 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 40.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | 184.9141 | 3.5935 | - | 4.7612 | 4.7612 | - | - | - | - | - | 3.5935 | CB5_Pleasant Point Township3.59354766394604 | DistributionFeederCB5_Pleasant Point Township11.22184.91405625 | DistributionFeederCB5_Pleasant Point Township11.22184.91405625 | 3.5935 | 184.9141 | 184.9141 | Joint | Link L263 | Cable-3 x 1c 185mm² Al XLPE | 11.22
DistributionFeederCB5_Pleasant Point Township11.22 | DistributionFeederCB5_Pleasant Point Township7/14 Cu 11.22- | DistributionFeeder | CB5_Pleasant Point Township | Link L263 |  | 4 | GEMA | 7/14 Cu | OH line | - | - | 11.22 | 131 | 2.5458 | 131 | 2.5458 | 131 | 2.5458 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 40.7 | 0.9 | 0.99 | 20 | 0.95 | 1 | 1.07 | 4 | 0 | 0.75 | - | - | 2.5458 | 2.5458 | 2.5458 | - | - | - | - | - | - | CB5_Pleasant Point Township2.54580291798089 | DistributionFeederCB5_Pleasant Point Township11.22131 | DistributionFeederCB5_Pleasant Point Township11.22131 | 2.5458 | 131 | 131 | Link L263 | 0 | OH line-7/14 Cu | 11.22
--- | ----- | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | --- | --- |  |  |  | - | - | --- | -
Switching Station-11 | Switching Station-3/1c 1000mm² AL XLPE CWS MDPE Screened11- | Switching Station | - | CB2662 | Joint | - | Waipopo | 3/1c 1000mm² AL XLPE CWS MDPE Screened | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | -11.2626534480134 | Switching Station-11591.136 | Switching Station-11591.136 | 11.2627 | 591.136 | 591.136 | CB2662 | Joint | Cable-3/1c 1000mm² AL XLPE CWS MDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | Joint | L904 | - | Waipopo | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 567 | 10.8028 | 567 | 10.8028 | 567 | 10.8028 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20 | 1 | 1 | 20 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 414.7605 | 7.9022 | 10.8028 | 10.8028 | 10.8028 | - | - | - | - | - | 7.9022 | -7.90224884869938 | Switching Station-11414.7605 | Switching Station-11414.7605 | 7.9022 | 414.7605 | 414.7605 | Joint | L904 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 1000mm² AL XLPE CWS MDPE Screened11- | Switching Station | - | CB2672 | Joint | - | Washdyke | 3/1c 1000mm² AL XLPE CWS MDPE Screened | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | -11.2626534480134 | Switching Station-11591.136 | Switching Station-11591.136 | 11.2627 | 591.136 | 591.136 | CB2672 | Joint | Cable-3/1c 1000mm² AL XLPE CWS MDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | Joint | L910 | - | Washdyke | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20 | 1 | 1 | 20 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 392.8155 | 7.4841 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.4841 | -7.48414044400629 | Switching Station-11392.8155 | Switching Station-11392.8155 | 7.4841 | 392.8155 | 392.8155 | Joint | L910 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | CB2682 | Joint | - | Showgrounds | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 96.7 | 0.9 | 1.03 | 20 | 0.95 | 1.2 | 1 | 4 | 0.15 | 0.7 | 236.3077 | 4.5023 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 4.5023 | -4.50226732144513 | Switching Station-11236.30775 | Switching Station-11236.30775 | 4.5023 | 236.3077 | 236.3077 | CB2682 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
Switching Station-11 | Switching Station-3c 240mm² AL PILC 11- | Switching Station | - | Joint | L1080 | - | Showgrounds | 3c 240mm² AL PILC | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 3 | 0.91 | 1.03 | 20 | 0.95 | 1.2 | 1 | 4 | 0.15 | 0.7 | 367.8181 | 7.0079 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.0079 | -7.00787696120589 | Switching Station-11367.81815 | Switching Station-11367.81815 | 7.0079 | 367.8181 | 367.8181 | Joint | L1080 | Cable-3c 240mm² AL PILC | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | CB2992 | Joint | - | Goulds | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 111.6 | 0.9 | 1.03 | 20 | 0.95 | 1.2 | 1 | 4 | 0.15 | 0.7 | 236.3077 | 4.5023 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 4.5023 | -4.50226732144513 | Switching Station-11236.30775 | Switching Station-11236.30775 | 4.5023 | 236.3077 | 236.3077 | CB2992 | Joint | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
Switching Station-11 | Switching Station-3c 240mm² AL PILC 11- | Switching Station | - | Joint | L1078 | - | Goulds | 3c 240mm² AL PILC | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 7 | 0.9 | 1.03 | 20 | 0.95 | 1.2 | 1 | 4 | 0.15 | 0.7 | 367.8181 | 7.0079 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.0079 | -7.00787696120589 | Switching Station-11367.81815 | Switching Station-11367.81815 | 7.0079 | 367.8181 | 367.8181 | Joint | L1078 | Cable-3c 240mm² AL PILC | 11
Switching Station-11 | Switching Station-3/1c 1000mm² AL XLPE CWS MDPE Screened11- | Switching Station | - | CB3002 | Joint | - | Elginshire | 3/1c 1000mm² AL XLPE CWS MDPE Screened | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | -11.2626534480134 | Switching Station-11591.136 | Switching Station-11591.136 | 11.2627 | 591.136 | 591.136 | CB3002 | Joint | Cable-3/1c 1000mm² AL XLPE CWS MDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | Joint | L969 | - | Elginshire | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20 | 0.95 | 1 | 20 | 0.95 | 1.2 | 1 | 4 | 0.3 | 0.77 | 392.8155 | 7.4841 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.4841 | -7.48414044400629 | Switching Station-11392.8155 | Switching Station-11392.8155 | 7.4841 | 392.8155 | 392.8155 | Joint | L969 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 1000mm² AL XLPE CWS MDPE Screened11- | Switching Station | - | CB3012 | Joint | - | Arowhenua | 3/1c 1000mm² AL XLPE CWS MDPE Screened | Cable | - | - | 11 | 728 | 13.8703 | 728 | 13.8703 | 728 | 13.8703 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | yes | 3575 | 1 | 1 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.812 | 591.136 | 11.2627 | 13.8703 | 13.8703 | 13.8703 | - | - | - | - | - | 11.2627 | -11.2626534480134 | Switching Station-11591.136 | Switching Station-11591.136 | 11.2627 | 591.136 | 591.136 | CB3012 | Joint | Cable-3/1c 1000mm² AL XLPE CWS MDPE Screened | 11
Switching Station-11 | Switching Station-3/1c 400mm² AL XLPE HDPE Screened11- | Switching Station | - | Joint | L461 | - | Arowhenua | 3/1c 400mm² AL XLPE HDPE Screened | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 3/1c | - | 20 | 0.95 | 1 | 20 | 0.95 | 1.2 | 1 | 96.74 | 0.3 | 0.77 | 392.8155 | 7.4841 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.4841 | -7.48414044400629 | Switching Station-11392.8155 | Switching Station-11392.8155 | 7.4841 | 392.8155 | 392.8155 | Joint | L461 | Cable-3/1c 400mm² AL XLPE HDPE Screened | 11
[13 empty] | - | 2.5458 | - | 2.5458 | - | 2.5458 | - | 0 | - | 0 | - | 3.8105 | - | 6.9732 | - | 7.7734 | - | 5.8301 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - |  | - | - | - | -
Note on N2: Author: ONAN Transfomer ratings
Note on P2: Author: ONAF Transfomer ratings
Note on R2: Author: ODAN Transformer ratings
Note on AR16: Author: As per Transpower Branch reports 2018
Note on AR28: Author: As per Transpower Branch reports 2018
Note on AR38: Author: As per Transpower Branch reports 2018
Note on N40: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P40: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R40: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on N48: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P48: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R48: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on N62: Author: Derated to 50 degrees celsius operating temperature
Note on R62: Author: Derated to 50 degrees celsius operating temperature
Note on R66: Author: Derated to 50 degrees celsius operating temperature
Note on R67: Author: Derated to 50 degrees celsius operating temperature
Note on R68: Author: Derated to 50 degrees celsius operating temperature
Note on R69: Author: Derated to 50 degrees celsius operating temperature
Note on R70: Author: Derated to 50 degrees celsius operating temperature
Note on R71: Author: Derated to 50 degrees celsius operating temperature
Note on R72: Author: Derated to 50 degrees celsius operating temperature
Note on R73: Author: Derated to 50 degrees celsius operating temperature
Note on R74: Author: Derated to 50 degrees celsius operating temperature
Note on R75: Author: Derated to 50 degrees celsius operating temperature
Note on R76: Author: Derated to 50 degrees celsius operating temperature
Note on R77: Author: Derated to 50 degrees celsius operating temperature
Note on R78: Author: Derated to 50 degrees celsius operating temperature
Note on R79: Author: Derated to 50 degrees celsius operating temperature
Note on R80: Author: Derated to 50 degrees celsius operating temperature
Note on R81: Author: Derated to 50 degrees celsius operating temperature
Note on R82: Author: Derated to 50 degrees celsius operating temperature
Note on R83: Author: Derated to 50 degrees celsius operating temperature
Note on R84: Author: Derated to 50 degrees celsius operating temperature
Note on R85: Author: Derated to 50 degrees celsius operating temperature
Note on R86: Author: Derated to 50 degrees celsius operating temperature
Note on R87: Author: Derated to 50 degrees celsius operating temperature
Note on R88: Author: Derated to 50 degrees celsius operating temperature
Note on R89: Author: Derated to 50 degrees celsius operating temperature
Note on R90: Author: Derated to 50 degrees celsius operating temperature
Note on R91: Author: Derated to 50 degrees celsius operating temperature
Note on R92: Author: Derated to 50 degrees celsius operating temperature
Note on R93: Author: Derated to 50 degrees celsius operating temperature
Note on R94: Author: Derated to 50 degrees celsius operating temperature
Note on R95: Author: Derated to 50 degrees celsius operating temperature
Note on R96: Author: Derated to 50 degrees celsius operating temperature
Note on R97: Author: Derated to 50 degrees celsius operating temperature
Note on R98: Author: Derated to 50 degrees celsius operating temperature
Note on R99: Author: Derated to 50 degrees celsius operating temperature
Note on R100: Author: Derated to 50 degrees celsius operating temperature
Note on R101: Author: Derated to 50 degrees celsius operating temperature
Note on R102: Author: Derated to 50 degrees celsius operating temperature
Note on R103: Author: Derated to 50 degrees celsius operating temperature
Note on R104: Author: Derated to 50 degrees celsius operating temperature
Note on R105: Author: Derated to 50 degrees celsius operating temperature
Note on R106: Author: Derated to 50 degrees celsius operating temperature
Note on R107: Author: Derated to 50 degrees celsius operating temperature
Note on R108: Author: Derated to 50 degrees celsius operating temperature
Note on R109: Author: Derated to 50 degrees celsius operating temperature
Note on R110: Author: Derated to 50 degrees celsius operating temperature
Note on R111: Author: Derated to 50 degrees celsius operating temperature
Note on R112: Author: Derated to 50 degrees celsius operating temperature
Note on R113: Author: Derated to 50 degrees celsius operating temperature
Note on R114: Author: Derated to 50 degrees celsius operating temperature
Note on R115: Author: Derated to 50 degrees celsius operating temperature
Note on R116: Author: Derated to 50 degrees celsius operating temperature
Note on R117: Author: Derated to 50 degrees celsius operating temperature
Note on R118: Author: Derated to 50 degrees celsius operating temperature
Note on R119: Author: Derated to 50 degrees celsius operating temperature
Note on R120: Author: Derated to 50 degrees celsius operating temperature
Note on R121: Author: Derated to 50 degrees celsius operating temperature
Note on R122: Author: Derated to 50 degrees celsius operating temperature
Note on R123: Author: Derated to 50 degrees celsius operating temperature
Note on R124: Author: Derated to 50 degrees celsius operating temperature
Note on R125: Author: Derated to 50 degrees celsius operating temperature
Note on R126: Author: Derated to 50 degrees celsius operating temperature
Note on R127: Author: Derated to 50 degrees celsius operating temperature
Note on R128: Author: Derated to 50 degrees celsius operating temperature
Note on R131: Author: Derated to 50 degrees celsius operating temperature
Note on R132: Author: Derated to 50 degrees celsius operating temperature
Note on R133: Author: Derated to 50 degrees celsius operating temperature
Note on R134: Author: Derated to 50 degrees celsius operating temperature
Note on N136: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P136: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R136: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R144: Author: Derated to 50 degrees celsius operating temperature
Note on N146: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P146: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R146: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R153: Author: Derated to 50 degrees celsius operating temperature
Note on R154: Author: Derated to 50 degrees celsius operating temperature
Note on R155: Author: Derated to 50 degrees celsius operating temperature
Note on R156: Author: Derated to 50 degrees celsius operating temperature
Note on R157: Author: Derated to 50 degrees celsius operating temperature
Note on R158: Author: Derated to 50 degrees celsius operating temperature
Note on R159: Author: Derated to 50 degrees celsius operating temperature
Note on R162: Author: Derated to 50 degrees celsius operating temperature
Note on R163: Author: Derated to 50 degrees celsius operating temperature
Note on R164: Author: Derated to 50 degrees celsius operating temperature
Note on R165: Author: Derated to 50 degrees celsius operating temperature
Note on R166: Author: Derated to 50 degrees celsius operating temperature
Note on R167: Author: Derated to 50 degrees celsius operating temperature
Note on R168: Author: Derated to 50 degrees celsius operating temperature
Note on R169: Author: Derated to 50 degrees celsius operating temperature
Note on R170: Author: Derated to 50 degrees celsius operating temperature
Note on R171: Author: Derated to 50 degrees celsius operating temperature
Note on R176: Author: Derated to 50 degrees celsius operating temperature
Note on R177: Author: Derated to 50 degrees celsius operating temperature
Note on R178: Author: Derated to 50 degrees celsius operating temperature
Note on R179: Author: Derated to 50 degrees celsius operating temperature
Note on R180: Author: Derated to 50 degrees celsius operating temperature
Note on R181: Author: Derated to 50 degrees celsius operating temperature
Note on R182: Author: Derated to 50 degrees celsius operating temperature
Note on R183: Author: Derated to 50 degrees celsius operating temperature
Note on R186: Author: Derated to 50 degrees celsius operating temperature
Note on R187: Author: Derated to 50 degrees celsius operating temperature
Note on R192: Author: Derated to 50 degrees celsius operating temperature
Note on R193: Author: Derated to 50 degrees celsius operating temperature
Note on R194: Author: Derated to 50 degrees celsius operating temperature
Note on R195: Author: Derated to 50 degrees celsius operating temperature
Note on R196: Author: Derated to 50 degrees celsius operating temperature
Note on R197: Author: Derated to 50 degrees celsius operating temperature
Note on R198: Author: Derated to 50 degrees celsius operating temperature
Note on R199: Author: Derated to 50 degrees celsius operating temperature
Note on R200: Author: Derated to 50 degrees celsius operating temperature
Note on R201: Author: Derated to 50 degrees celsius operating temperature
Note on R202: Author: Derated to 50 degrees celsius operating temperature
Note on R203: Author: Derated to 50 degrees celsius operating temperature
Note on R204: Author: Derated to 50 degrees celsius operating temperature
Note on R205: Author: Derated to 50 degrees celsius operating temperature
Note on R206: Author: Derated to 50 degrees celsius operating temperature
Note on R211: Author: Derated to 50 degrees celsius operating temperature
Note on R212: Author: Derated to 50 degrees celsius operating temperature
Note on R213: Author: Derated to 50 degrees celsius operating temperature
Note on R214: Author: Derated to 50 degrees celsius operating temperature
Note on R215: Author: Derated to 50 degrees celsius operating temperature
Note on R216: Author: Derated to 50 degrees celsius operating temperature
Note on R217: Author: Derated to 50 degrees celsius operating temperature
Note on R218: Author: Derated to 50 degrees celsius operating temperature
Note on R219: Author: Derated to 50 degrees celsius operating temperature
Note on R220: Author: Derated to 50 degrees celsius operating temperature
Note on R221: Author: Derated to 50 degrees celsius operating temperature
Note on R246: Author: Derated to 50 degrees celsius operating temperature
Note on R247: Author: Derated to 50 degrees celsius operating temperature
Note on R250: Author: Derated to 50 degrees celsius operating temperature
Note on R251: Author: Derated to 50 degrees celsius operating temperature
Note on R252: Author: Derated to 50 degrees celsius operating temperature
Note on R253: Author: Derated to 50 degrees celsius operating temperature
Note on R254: Author: Derated to 50 degrees celsius operating temperature
Note on R258: Author: Derated to 50 degrees celsius operating temperature
Note on R259: Author: Derated to 50 degrees celsius operating temperature
Note on R260: Author: Derated to 50 degrees celsius operating temperature
Note on R261: Author: Derated to 50 degrees celsius operating temperature
Note on R262: Author: Derated to 50 degrees celsius operating temperature
Note on R264: Author: Derated to 50 degrees celsius operating temperature
Note on R265: Author: Derated to 50 degrees celsius operating temperature
Note on R266: Author: Derated to 50 degrees celsius operating temperature
Note on R267: Author: Derated to 50 degrees celsius operating temperature
Note on R268: Author: Derated to 50 degrees celsius operating temperature
Note on R269: Author: Derated to 50 degrees celsius operating temperature
Note on R270: Author: Derated to 50 degrees celsius operating temperature
Note on R271: Author: Derated to 50 degrees celsius operating temperature
Note on R272: Author: Derated to 50 degrees celsius operating temperature
Note on R273: Author: Derated to 50 degrees celsius operating temperature
Note on R274: Author: Derated to 50 degrees celsius operating temperature
Note on R275: Author: Derated to 50 degrees celsius operating temperature
Note on R276: Author: Derated to 50 degrees celsius operating temperature
Note on R277: Author: Derated to 50 degrees celsius operating temperature
Note on R278: Author: Derated to 50 degrees celsius operating temperature
Note on R279: Author: Derated to 50 degrees celsius operating temperature
Note on R280: Author: Derated to 50 degrees celsius operating temperature
Note on R281: Author: Derated to 50 degrees celsius operating temperature
Note on R282: Author: Derated to 50 degrees celsius operating temperature
Note on R283: Author: Derated to 50 degrees celsius operating temperature
Note on R284: Author: Derated to 50 degrees celsius operating temperature
Note on R286: Author: Derated to 50 degrees celsius operating temperature
Note on R287: Author: Derated to 50 degrees celsius operating temperature
Note on R288: Author: Derated to 50 degrees celsius operating temperature
Note on R289: Author: Derated to 50 degrees celsius operating temperature
Note on R290: Author: Derated to 50 degrees celsius operating temperature
Note on R291: Author: Derated to 50 degrees celsius operating temperature
Note on R292: Author: Derated to 50 degrees celsius operating temperature
Note on R293: Author: Derated to 50 degrees celsius operating temperature
Note on R294: Author: Derated to 50 degrees celsius operating temperature
Note on R295: Author: Derated to 50 degrees celsius operating temperature
Note on R296: Author: Derated to 50 degrees celsius operating temperature
Note on R297: Author: Derated to 50 degrees celsius operating temperature
Note on R298: Author: Derated to 50 degrees celsius operating temperature
Note on R299: Author: Derated to 50 degrees celsius operating temperature
Note on R300: Author: Derated to 50 degrees celsius operating temperature
Note on R301: Author: Derated to 50 degrees celsius operating temperature
Note on R302: Author: Derated to 50 degrees celsius operating temperature
Note on R303: Author: Derated to 50 degrees celsius operating temperature
Note on R304: Author: Derated to 50 degrees celsius operating temperature
Note on R305: Author: Derated to 50 degrees celsius operating temperature
Note on R306: Author: Derated to 50 degrees celsius operating temperature
Note on R307: Author: Derated to 50 degrees celsius operating temperature
Note on R308: Author: Derated to 50 degrees celsius operating temperature
Note on R309: Author: Derated to 50 degrees celsius operating temperature
Note on R310: Author: Derated to 50 degrees celsius operating temperature
Note on R311: Author: Derated to 50 degrees celsius operating temperature
Note on R312: Author: Derated to 50 degrees celsius operating temperature
Note on R313: Author: Derated to 50 degrees celsius operating temperature
Note on R315: Author: Derated to 50 degrees celsius operating temperature
Note on R316: Author: Derated to 50 degrees celsius operating temperature
Note on R317: Author: Derated to 50 degrees celsius operating temperature
Note on R318: Author: Derated to 50 degrees celsius operating temperature
Note on P385: Author: Using ratings from AEL Drawing 782
Note on N397: Author: Derated to 75 degrees celsius operating temperature
Note on R397: Author: Derated to 75 degrees celsius operating temperature
Note on N416: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P416: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R416: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on N418: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P418: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R418: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on N424: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P424: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R424: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on N426: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on P426: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details
Note on R426: Author: Based on General Cables technical specification at a depth of 2.5 m. See G:\Engineers\Assets\Substations Zone\Washdyke Switching Station\Projects & Jobs\2016-17 Original Project\Work\33 kV Cable Pricing\A - 213276 Timaru to Washdyke 33 kV Underground Cable Project - Cable Tech Details

## TKA_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of | ID | Type | ID | Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal R. |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [5 empty] | Data |  |  |  |  | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | - | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPTKA_GXP110 | GXPTKA_GXP19/2.34 Cu110- | GXP | TKA_GXP | CB42 | CB76 | 1 | TP Branch Report ABY.TKA.1 | 19/2.34 Cu | OH Line | - | - | 110 | 325 | 61.9208 | 297 | 56.5861 | 266 | 50.6798 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 61.9208 | 56.5861 | 50.6798 | - | - | - | - | - | - | TKA_GXP50.6798066294653 | GXPTKA_GXP110266 | GXPTKA_GXP110266 | 50.6798 | 266 | 266 | CB42 | CB76 | OH Line - 19/2.34 Cu | 110
GXPTKA_GXP110 | GXPTKA_GXP76-T6110- | GXP | TKA_GXP | CB76 | PTX T6 | 1 | TP Branch Report TKA.TF.T6 | 76-T6 | Busbar | TKA-BS-110-76-T6 | - | 110 | 410 | 78.1155 | 410 | 78.1155 | 410 | 78.1155 | 410 | 78.1155 | 410 | 78.1155 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.1155 | 78.1155 | 78.1155 | 78.1155 | 78.1155 | - | - | - | - | TKA_GXP78.1154914213564 | GXPTKA_GXP110410 | GXPTKA_GXP110410 | 78.1155 | 410 | 410 | CB76 | PTX T6 | Busbar - 76-T6 | 110
GXPTKA_GXP110 | GXPTKA_GXPTKA-CB72110Protection | GXP | TKA_GXP | CB72 | PTX T6 | 2 | TP Branch Report TKA.TF.T6 | TKA-CB72 | Circuit Breaker | Relay SEL 351S | Protection | 110 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | 3150 | 600.1556 | 260 | 49.5367 | - | - | 600 | 114.3154 | 400 | 76.2102 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600.1556 | 600.1556 | 600.1556 | 600.1556 | 600.1556 | 49.5367 | 114.3154 | 76.2102 | - | TKA_GXP49.5366530964699 | GXPTKA_GXP110260 | GXPTKA_GXP110260 | 49.5367 | 260 | 260 | CB72 | PTX T6 | Circuit Breaker - TKA-CB72 - Protection | 110
GXPTKA_GXP110 | GXPTKA_GXPT6110Tap Changer | GXP | TKA_GXP | CB72 | PTX T6 | 3 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6 | Tap Changer | 110 | 300 | 57.1577 | 300 | 57.1577 | 300 | 57.1577 | 360 | 68.5892 | 360 | 68.5892 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 57.1577 | 57.1577 | 57.1577 | 68.5892 | 68.5892 | - | - | - | - | TKA_GXP57.1576766497729 | GXPTKA_GXP110300 | GXPTKA_GXP110300 | 57.1577 | 300 | 300 | CB72 | PTX T6 | Transformer - T6 - Tap Changer | 110
GXPTKA_GXP110 | GXPTKA_GXPT6110Bushing | GXP | TKA_GXP | CB72 | PTX T6 | 4 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6 | Bushing | 110 | 1250 | 238.157 | 1250 | 238.157 | 1250 | 238.157 | 1500 | 285.7884 | 1500 | 285.7884 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 238.157 | 238.157 | 238.157 | 285.7884 | 285.7884 | - | - | - | - | TKA_GXP238.156986040721 | GXPTKA_GXP1101250 | GXPTKA_GXP1101250 | 238.157 | 1250 | 1250 | CB72 | PTX T6 | Transformer - T6 - Bushing | 110
GXPTKA_GXP110 | GXPTKA_GXPT6110Non Equipment | GXP | TKA_GXP | CB72 | PTX T6 | 4 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6-NEL-HV | Non Equipment | 110 | 184 | 35.0567 | 184 | 35.0567 | 184 | 35.0567 | 184 | 35.0567 | 184 | 35.0567 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 35.0567 | 35.0567 | 35.0567 | 35.0567 | 35.0567 | - | - | - | - | TKA_GXP35.0567083451941 | GXPTKA_GXP110184 | GXPTKA_GXP110184 | 35.0567 | 184 | 184 | CB72 | PTX T6 | Transformer - T6 - Non Equipment | 110
GXPTKA_GXP110 | GXPTKA_GXPT6110HV Winding | GXP | TKA_GXP | CB72 | PTX T6 | 5 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6 | HV Winding | 110 | 183.7024 | 35 | - | - | - | - | 237 | 45.1546 | 237 | 45.1546 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.1546 | 45.1546 | - | - | - | - | TKA_GXP45.1545645533206 | GXPTKA_GXP110237 | GXPTKA_GXP110183.702358378517 | 45.1546 | 237 | 183.7024 | CB72 | PTX T6 | Transformer - T6 - HV Winding | 110
GXPTKA_GXP11 | GXPTKA_GXPT611LV Winding | GXP | TKA_GXP | CB72 | PTX T6 | 6 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6 | LV Winding | 11 | 1837.0236 | 35 | - | - | - | - | 2367 | 45.0974 | 2367 | 45.0974 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.0974 | 45.0974 | - | - | - | - | TKA_GXP45.0974068766709 | GXPTKA_GXP112367 | GXPTKA_GXP111837.02358378517 | 45.0974 | 2367 | 1837.0236 | CB72 | PTX T6 | Transformer - T6 - LV Winding | 11
GXPTKA_GXP11 | GXPTKA_GXPT611Bushing | GXP | TKA_GXP | CB72 | PTX T6 | 7 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6 | Bushing | 11 | 3300 | 62.8734 | 3300 | 62.8734 | 3300 | 62.8734 | 3960 | 75.4481 | 3960 | 75.4481 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 62.8734 | 62.8734 | 62.8734 | 75.4481 | 75.4481 | - | - | - | - | TKA_GXP62.8734443147502 | GXPTKA_GXP113300 | GXPTKA_GXP113300 | 62.8734 | 3300 | 3300 | CB72 | PTX T6 | Transformer - T6 - Bushing | 11
GXPTKA_GXP11 | GXPTKA_GXPT611Non Equipment | GXP | TKA_GXP | CB72 | PTX T6 | 8 | TP Branch Report TKA.TF.T6 | T6 | Transformer | TKA-TF-T6-NEL-HV | Non Equipment | 11 | 1837 | 34.9996 | 1837 | 34.9996 | 1837 | 34.9996 | 1837 | 34.9996 | 1837 | 34.9996 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 34.9996 | 34.9996 | 34.9996 | 34.9996 | 34.9996 | - | - | - | - | TKA_GXP34.9995506685443 | GXPTKA_GXP111837 | GXPTKA_GXP111837 | 34.9996 | 1837 | 1837 | CB72 | PTX T6 | Transformer - T6 - Non Equipment | 11
GXPTKA_GXP11 | GXPTKA_GXP6-1c 630 mm² XLPE11- | GXP | TKA_GXP | PTX T6 | 11 kV Bus | 9 | TP Branch Report TKA.TF.T6 | 6-1c 630 mm² XLPE | Cable | TKA-CBL-37 | - | 11 | 2202 | 41.9537 | 2202 | 41.9537 | 2202 | 41.9537 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | - | 60 | - | - | - | - | - | - | - | - | - | - | - | 41.9537 | 41.9537 | 41.9537 | - | - | - | - | - | - | TKA_GXP41.9537346609333 | GXPTKA_GXP112202 | GXPTKA_GXP112202 | 41.9537 | 2202 | 2202 | PTX T6 | 11 kV Bus | Cable - 6-1c 630 mm² XLPE | 11
GXPTKA_GXP11 | GXPTKA_GXPTKA-CB3711Protection | GXP | TKA_GXP | PTX T6 | 11 kV Bus | 10 | TP Branch Report TKA.TF.T6 | TKA-CB37 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 2000 | 38.1051 | 2000 | 38.1051 | 2000 | 38.1051 | 2000 | 38.1051 | 2000 | 38.1051 | 2235 | 42.5825 | - | - | 4500 | 85.7365 | 3000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 38.1051 | 38.1051 | 38.1051 | 38.1051 | 38.1051 | 42.5825 | 85.7365 | 57.1577 | - | TKA_GXP38.1051177665153 | GXPTKA_GXP112000 | GXPTKA_GXP112000 | 38.1051 | 2000 | 2000 | PTX T6 | 11 kV Bus | Circuit Breaker - TKA-CB37 - Protection | 11
GXPTKA_GXP11 | GXPTKA_GXPTKA-CB3211Protection | GXP | TKA_GXP | CB32 | DS1046 | 1 | TP Branch Report TKA.TF.T1 | TKA-CB32 | Circuit Breaker | Relay SEL 451 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | 642 | 12.2317 | - | - | 1800 | 34.2946 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.0031 | 12.2317 | 34.2946 | - | - | TKA_GXP12.0031120964523 | GXPTKA_GXP11630 | GXPTKA_GXP11630 | 12.0031 | 630 | 630 | CB32 | DS1046 | Circuit Breaker-TKA-CB32-Protection | 11
GXPTKA_GXP11 | GXPTKA_GXP6-1c 185 mm² XLPE11- | GXP | TKA_GXP | CB32 | DS1046 | 2 | TP Branch Report TKA.TF.T1 | 6-1c 185 mm² XLPE | Cable | TKA-CBL-32 | - | 11 | 660 | 12.5747 | 660 | 12.5747 | 660 | 12.5747 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | - | 3.9 | - | 1 | - | 1 | - | 1 | - | - | 1 | 660 | 12.5747 | 12.5747 | 12.5747 | 12.5747 | - | - | - | - | - | 12.5747 | TKA_GXP12.57468886295 | GXPTKA_GXP11660 | GXPTKA_GXP11660 | 12.5747 | 660 | 660 | CB32 | DS1046 | Cable-6-1c 185 mm² XLPE | 11
GXPTKA_GXP11 | GXPTKA_GXPT111LV Winding | GXP | TKA_GXP | CB32 | DS1046 | 3 | TP Branch Report TKA.TF.T1 | T1 | Transformer | TKA-TF-T1 | LV Winding | 11 | 524.8639 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TKA_GXP | GXPTKA_GXP11 | GXPTKA_GXP11524.863881081478 |  |  | 524.8639 | CB32 | DS1046 | Transformer-T1-LV Winding | 11
GXPTKA_GXP33 | GXPTKA_GXPT133HV Winding | GXP | TKA_GXP | CB32 | DS1046 | 4 | TP Branch Report TKA.TF.T1 | T1 | Transformer | TKA-TF-T1 | HV Winding | 33 | 174.9546 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TKA_GXP | GXPTKA_GXP33 | GXPTKA_GXP33174.954627027159 |  |  | 174.9546 | CB32 | DS1046 | Transformer-T1-HV Winding | 33
GXPTKA_GXP33 | GXPTKA_GXPTKA-CB104233Protection | GXP | TKA_GXP | CB32 | DS1046 | 5 | TP Branch Report TKA.TF.T1 | TKA-CB1042 | Circuit Breaker | Relay SEL 451 | Protection | 33 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 183 | 10.4599 | - | - | 600 | 34.2946 | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4471 | 71.4471 | 71.4471 | 71.4471 | 71.4471 | 10.4599 | 34.2946 | 22.8631 | - | TKA_GXP10.4598548269084 | GXPTKA_GXP33183 | GXPTKA_GXP33183 | 10.4599 | 183 | 183 | CB32 | DS1046 | Circuit Breaker-TKA-CB1042-Protection | 33
GXPTKA_GXP33 | GXPTKA_GXP104633- | GXP | TKA_GXP | CB32 | DS1046 | 6 | TP Branch Report TKA.TF.T1 | 1046 | Disconnector | TKA-DS-1046 | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TKA_GXP | GXPTKA_GXP33 | GXPTKA_GXP33 |  |  |  | CB32 | DS1046 | Disconnector-1046 | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVTKA-CB104233Protection | SubTransmission | SBT_33kV | CB1042 | DS1046 | 1 | TP Branch Report TKA.TF.T1 | TKA-CB1042 | Circuit Breaker | Relay SEL 451 | Protection | 33 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 1250 | 71.4471 | 183 | 10.4599 | - | - | 600 | 34.2946 | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4471 | 71.4471 | 71.4471 | 71.4471 | 71.4471 | 10.4599 | 34.2946 | 22.8631 | - | SBT_33kV10.4598548269084 | SubTransmissionSBT_33kV33183 | SubTransmissionSBT_33kV33183 | 10.4599 | 183 | 183 | CB1042 | DS1046 | Circuit Breaker-TKA-CB1042-Protection | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kV104633- | SubTransmission | SBT_33kV | CB1042 | DS1046 | 2 | TP Branch Report TKA.TF.T1 | 1046 | Disconnector | TKA-DS-1046 | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | SBT_33kV | SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kV33 |  |  |  | CB1042 | DS1046 | Disconnector-1046 | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVIODINE33- | SubTransmission | SBT_33kV | DS1046 | M315 | 3 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 369 | 21.0912 | - | - | 275 | 15.7184 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 26.6 | - | - | - | - | - | - | - | - | - | - | - | 21.0912 | - | 15.7184 | - | - | - | - | - | - | SBT_33kV15.7183610786876 | SubTransmissionSBT_33kV33275 | SubTransmissionSBT_33kV33275 | 15.7184 | 275 | 275 | DS1046 | M315 | OH Line-IODINE | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVM31533- | SubTransmission | SBT_33kV | DS1046 | M315 | 4 | GEMA | M315 | Link | - | - | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | - | - | - | - | SBT_33kV36.009336289357 | SubTransmissionSBT_33kV33630 | SubTransmissionSBT_33kV33630 | 36.0093 | 630 | 630 | DS1046 | M315 | Link-M315 | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVDOG33- | SubTransmission | SBT_33kV | M315 | M55 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1470.2 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | SBT_33kV14.6814364082846 | SubTransmissionSBT_33kV33256.858523103439 | SubTransmissionSBT_33kV33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | M315 | M55 | OH Line-DOG | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVM5533- | SubTransmission | SBT_33kV | M315 | M55 | 6 | GEMA | M55 | Link | - | - | 33 | 300 | 17.1473 | 300 | 17.1473 | 300 | 17.1473 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 17.1473 | 17.1473 | 17.1473 | - | - | - | - | - | - | SBT_33kV17.1473029949319 | SubTransmissionSBT_33kV33300 | SubTransmissionSBT_33kV33300 | 17.1473 | 300 | 300 | M315 | M55 | Link-M55 | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kV19/14 Cu33- | SubTransmission | SBT_33kV | M55 | Pole 24021 | 7 | GEMA/AEL OH Amp Calc. | 19/14 Cu | OH Line | - | - | 33 | 320.5975 | 18.3246 | - | - | 242 | 13.8322 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 48.3 | - | - | - | - | - | - | - | - | - | - | - | 18.3246 | - | 13.8322 | - | - | - | - | - | - | SBT_33kV13.8321577492451 | SubTransmissionSBT_33kV33242 | SubTransmissionSBT_33kV33242 | 13.8322 | 242 | 242 | M55 | Pole 24021 | OH Line-19/14 Cu | 33
SubTransmissionSBT_33kV33 | SubTransmissionSBT_33kVDOG33- | SubTransmission | SBT_33kV | Pole 24021 | M11 T-off | 8 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1470.2 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | SBT_33kV14.6814364082846 | SubTransmissionSBT_33kV33256.858523103439 | SubTransmissionSBT_33kV33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | Pole 24021 | M11 T-off | OH Line-DOG | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11DOG33- | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 1 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8.8 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | TKA_M1114.6814364082846 | SubTransmissionTKA_M1133256.858523103439 | SubTransmissionTKA_M1133256.858523103439 | 14.6814 | 256.8585 | 256.8585 | M11 T-off | Pole 18992 | OH Line-DOG | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11M16533- | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 2 | GEMA | M165 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TKA_M11 | SubTransmissionTKA_M1133 | SubTransmissionTKA_M1133 |  |  |  | M11 T-off | Pole 18992 | ABS-M165 | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11TKA_M11-M1133Protection | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 3 | GEMA/AEL Protection Database | TKA_M11-M11 | Recloser | Relay ASEA-RX1D-2H | Protection | 33 | 560 | 32.0083 | 560 | 32.0083 | 560 | 32.0083 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.0083 | 32.0083 | 32.0083 | - | - | - | - | - | - | TKA_M1132.0082989238729 | SubTransmissionTKA_M1133560 | SubTransmissionTKA_M1133560 | 32.0083 | 560 | 560 | M11 T-off | Pole 18992 | Recloser-TKA_M11-M11-Protection | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11M1233- | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 4 | GEMA | M12 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TKA_M11 | SubTransmissionTKA_M1133 | SubTransmissionTKA_M1133 |  |  |  | M11 T-off | Pole 18992 | ABS-M12 | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M113-70mm2 Cu33- | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 5 | GEMA | 3-70mm2 Cu | OH Line | - | - | 33 | 247 | 14.1179 | 247 | 14.1179 | 247 | 14.1179 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8.4 | - | - | - | - | - | - | - | - | - | - | - | 14.1179 | 14.1179 | 14.1179 | - | - | - | - | - | - | TKA_M1114.1179461324939 | SubTransmissionTKA_M1133247 | SubTransmissionTKA_M1133247 | 14.1179 | 247 | 247 | M11 T-off | Pole 18992 | OH Line - 3-70mm2 Cu | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11TKA_M11-M34633Protection | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 3 | GEMA/AEL Protection Database | TKA_M11-M346 | Recloser | Relay SEL 751 | Protection | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | 150 | 8.5737 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | 8.5737 | - | - | - | TKA_M118.57365149746594 | SubTransmissionTKA_M1133150 | SubTransmissionTKA_M1133150 | 8.5737 | 150 | 150 | M11 T-off | Pole 18992 | Recloser - TKA_M11-M346 - Protection | 33
SubTransmissionTKA_M1133 | SubTransmissionTKA_M11DOG33- | SubTransmission | TKA_M11 | M11 T-off | Pole 18992 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6129.1 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | TKA_M1114.6814364082846 | SubTransmissionTKA_M1133256.858523103439 | SubTransmissionTKA_M1133256.858523103439 | 14.6814 | 256.8585 | 256.8585 | M11 T-off | Pole 18992 | OH Line-DOG | 33
SubTransmissionUHT33 | SubTransmissionUHTDOG33- | SubTransmission | UHT | Pole 18992 | M34 | 1 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10933.8 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | UHT14.6814364082846 | SubTransmissionUHT33256.858523103439 | SubTransmissionUHT33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | Pole 18992 | M34 | OH Line-DOG | 33
SubTransmissionUHT33 | SubTransmissionUHTM3433- | SubTransmission | UHT | M34 | M73 | 2 | GEMA | M34 | Link | - | - | 33 | 300 | 17.1473 | 300 | 17.1473 | 300 | 17.1473 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 17.1473 | 17.1473 | 17.1473 | - | - | - | - | - | - | UHT17.1473029949319 | SubTransmissionUHT33300 | SubTransmissionUHT33300 | 17.1473 | 300 | 300 | M34 | M73 | Link-M34 | 33
SubTransmissionUHT33 | SubTransmissionUHTM31833Protection | SubTransmission | UHT | M34 | M73 | 3 | GEMA/Setting File | M318 | Secionaliser | Relay SEL 351R | Protection | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | 120 | 6.8589 | 120 | 6.8589 | - | - | 1000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | 6.8589 | - | 57.1577 | - | UHT6.85892119797275 | SubTransmissionUHT33120 | SubTransmissionUHT33120 | 6.8589 | 120 | 120 | M34 | M73 | Secionaliser-M318-Protection | 33
SubTransmissionUHT33 | SubTransmissionUHTM3633- | SubTransmission | UHT | M34 | M73 | 4 | GEMA | M36 | Link | - | - | 33 | 300 | 17.1473 | 300 | 17.1473 | 300 | 17.1473 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 17.1473 | 17.1473 | 17.1473 | - | - | - | - | - | - | UHT17.1473029949319 | SubTransmissionUHT33300 | SubTransmissionUHT33300 | 17.1473 | 300 | 300 | M34 | M73 | Link-M36 | 33
SubTransmissionUHT33 | SubTransmissionUHTDOG33- | SubTransmission | UHT | M34 | M73 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33 | 343.6934 | 19.6447 | - | - | 256.8585 | 14.6814 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8736.4 | - | - | - | - | - | - | - | - | - | - | - | 19.6447 | - | 14.6814 | - | - | - | - | - | - | UHT14.6814364082846 | SubTransmissionUHT33256.858523103439 | SubTransmissionUHT33256.858523103439 | 14.6814 | 256.8585 | 256.8585 | M34 | M73 | OH Line-DOG | 33
SubTransmissionUHT33 | SubTransmissionUHTFLOUNDER33- | SubTransmission | UHT | M34 | M73 | 6 | GEMA/AEL OH Amp Calc. | FLOUNDER | OH Line | - | - | 33 | 128 | 7.3162 | - | - | 98 | 5.6015 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 217.5 | - | - | - | - | - | - | - | - | - | - | - | 7.3162 | - | 5.6015 | - | - | - | - | - | - | UHT5.60145231167775 | SubTransmissionUHT3398 | SubTransmissionUHT3398 | 5.6015 | 98 | 98 | M34 | M73 | OH Line-FLOUNDER | 33
SubTransmissionUHT33 | SubTransmissionUHTM7333- | SubTransmission | UHT | M73 | M61 | 7 | GEMA | M73 | ABS | - | - | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | - | - | - | - | - | UHT22.8630706599092 | SubTransmissionUHT33400 | SubTransmissionUHT33400 | 22.8631 | 400 | 400 | M73 | M61 | ABS-M73 | 33
SubTransmissionUHT33 | SubTransmissionUHTFLOUNDER33- | SubTransmission | UHT | M73 | M61 | 8 | GEMA/AEL OH Amp Calc. | FLOUNDER | OH Line | - | - | 33 | 128 | 7.3162 | - | - | 98 | 5.6015 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9683.3 | - | - | - | - | - | - | - | - | - | - | - | 7.3162 | - | 5.6015 | - | - | - | - | - | - | UHT5.60145231167775 | SubTransmissionUHT3398 | SubTransmissionUHT3398 | 5.6015 | 98 | 98 | M73 | M61 | OH Line-FLOUNDER | 33
SubTransmissionUHT33 | SubTransmissionUHTMINK33- | SubTransmission | UHT | M61 | M271 | 9 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | UHT10.7814586230328 | SubTransmissionUHT33188.626607220145 | SubTransmissionUHT33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | M61 | M271 | OH Line-MINK | 33
SubTransmissionUHT33 | SubTransmissionUHTM27133- | SubTransmission | UHT | M271 | M54 | 10 | GEMA | M271 | Link | - | - | 33 | 600 | 34.2946 | 600 | 34.2946 | 600 | 34.2946 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 34.2946 | 34.2946 | 34.2946 | - | - | - | - | - | - | UHT34.2946059898638 | SubTransmissionUHT33600 | SubTransmissionUHT33600 | 34.2946 | 600 | 600 | M271 | M54 | Link-M271 | 33
SubTransmissionUHT33 | SubTransmissionUHTM27233Protection | SubTransmission | UHT | M271 | M54 | 11 | GEMA/AEL Protection Database | M272 | Secionaliser | Relay SEL 351R | Protection | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | 80 | 4.5726 | 80 | 4.5726 | - | - | 1000 | 57.1577 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | 4.5726 | - | 57.1577 | - | UHT4.57261413198184 | SubTransmissionUHT3380 | SubTransmissionUHT3380 | 4.5726 | 80 | 80 | M271 | M54 | Secionaliser-M272-Protection | 33
SubTransmissionUHT33 | SubTransmissionUHTM27033- | SubTransmission | UHT | M271 | M54 | 12 | GEMA | M270 | Link | - | - | 33 | 600 | 34.2946 | 600 | 34.2946 | 600 | 34.2946 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 34.2946 | 34.2946 | 34.2946 | - | - | - | - | - | - | UHT34.2946059898638 | SubTransmissionUHT33600 | SubTransmissionUHT33600 | 34.2946 | 600 | 600 | M271 | M54 | Link-M270 | 33
SubTransmissionUHT33 | SubTransmissionUHTMINK33- | SubTransmission | UHT | M271 | M54 | 13 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2726.3 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | UHT10.7814586230328 | SubTransmissionUHT33188.626607220145 | SubTransmissionUHT33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | M271 | M54 | OH Line-MINK | 33
SubTransmissionUHT33 | SubTransmissionUHTM5433- | SubTransmission | UHT | M54 | M238 | 14 | GEMA | M54 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | UHT | SubTransmissionUHT33 | SubTransmissionUHT33 |  |  |  | M54 | M238 | ABS-M54 | 33
SubTransmissionUHT33 | SubTransmissionUHTPETREL33- | SubTransmission | UHT | M54 | M238 | 15 | GEMA/AEL OH Amp Calc. | PETREL | OH Line | - | - | 33 | 230 | 13.1463 | - | - | 172.8371 | 9.879 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 272.4 | - | - | - | - | - | - | - | - | - | - | - | 13.1463 | - | 9.879 | - | - | - | - | - | - | UHT9.87896668162793 | SubTransmissionUHT33172.837093119795 | SubTransmissionUHT33172.837093119795 | 9.879 | 172.8371 | 172.8371 | M54 | M238 | OH Line-PETREL | 33
SubTransmissionUHT33 | SubTransmissionUHT7/12 Cu33- | SubTransmission | UHT | M54 | M238 | 16 | GEMA/AEL OH Amp Calc. | 7/12 Cu | OH Line | - | - | 33 | 229 | 13.0891 | - | - | 174 | 9.9454 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 41 | - | - | - | - | - | - | - | - | - | - | - | 13.0891 | - | 9.9454 | - | - | - | - | - | - | UHT9.94543573706049 | SubTransmissionUHT33174 | SubTransmissionUHT33174 | 9.9454 | 174 | 174 | M54 | M238 | OH Line-7/12 Cu | 33
SubTransmissionUHT33 | SubTransmissionUHTMINK33- | SubTransmission | UHT | M54 | M238 | 17 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6827.3 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | UHT10.7814586230328 | SubTransmissionUHT33188.626607220145 | SubTransmissionUHT33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | M54 | M238 | OH Line-MINK | 33
SubTransmissionUHT33 | SubTransmissionUHTPETREL33- | SubTransmission | UHT | M54 | M238 | 18 | GEMA/AEL OH Amp Calc. | PETREL | OH Line | - | - | 33 | 230 | 13.1463 | - | - | 172.8371 | 9.879 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 267.8 | - | - | - | - | - | - | - | - | - | - | - | 13.1463 | - | 9.879 | - | - | - | - | - | - | UHT9.87896668162793 | SubTransmissionUHT33172.837093119795 | SubTransmissionUHT33172.837093119795 | 9.879 | 172.8371 | 172.8371 | M54 | M238 | OH Line-PETREL | 33
SubTransmissionUHT33 | SubTransmissionUHTMINK33- | SubTransmission | UHT | M54 | M238 | 19 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4686.8 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | UHT10.7814586230328 | SubTransmissionUHT33188.626607220145 | SubTransmissionUHT33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | M54 | M238 | OH Line-MINK | 33
SubTransmissionUHT33 | SubTransmissionUHTM23833- | SubTransmission | UHT | M238 | M303 | 20 | GEMA | M238 | ABS | - | - | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | - | - | - | - | - | UHT45.7261413198184 | SubTransmissionUHT33800 | SubTransmissionUHT33800 | 45.7261 | 800 | 800 | M238 | M303 | ABS-M238 | 33
SubTransmissionUHT33 | SubTransmissionUHTMINK33- | SubTransmission | UHT | M238 | M303 | 21 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 33 | 250.5823 | 14.3227 | - | - | 188.6266 | 10.7815 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.7 | - | - | - | - | - | - | - | - | - | - | - | 14.3227 | - | 10.7815 | - | - | - | - | - | - | UHT10.7814586230328 | SubTransmissionUHT33188.626607220145 | SubTransmissionUHT33188.626607220145 | 10.7815 | 188.6266 | 188.6266 | M238 | M303 | OH Line-MINK | 33
SubTransmissionUHT33 | SubTransmissionUHT3-1c 185 mm² AL XLPE33- | SubTransmission | UHT | M238 | M303 | 22 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 33 | 326 | 18.6334 | 326 | 18.6334 | 326 | 18.6334 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 3.5 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 1 | - | 1 | 319.48 | 18.2607 | 18.6334 | 18.6334 | 18.6334 | - | - | - | - | - | 18.2607 | UHT18.2607345360695 | SubTransmissionUHT33319.48 | SubTransmissionUHT33319.48 | 18.2607 | 319.48 | 319.48 | M238 | M303 | Cable-3-1c 185 mm² AL XLPE | 33
ZoneSubstationUHT33 | ZoneSubstationUHTM30333- | ZoneSubstation | UHT | M303 | M301 | 1 | GEMA | M303 | RMU Switch | - | - | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | - | - | - | - | UHT36.009336289357 | ZoneSubstationUHT33630 | ZoneSubstationUHT33630 | 36.0093 | 630 | 630 | M303 | M301 | RMU Switch-M303 | 33
ZoneSubstationUHT33 | ZoneSubstationUHTUHT-M30233Protection | ZoneSubstation | UHT | M303 | M301 | 2 | GEMA/AEL Protection Database | UHT-M302 | Circuit Breaker | Siemens 8DJH-36 | Protection | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | 50 | 2.8579 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | 2.8579 | - | - | - | UHT2.85788383248865 | ZoneSubstationUHT3350 | ZoneSubstationUHT3350 | 2.8579 | 50 | 50 | M303 | M301 | Circuit Breaker-UHT-M302-Protection | 33
ZoneSubstationUHT33 | ZoneSubstationUHTM36533- | ZoneSubstation | UHT | M303 | M301 | 3 | GEMA | M365 | RMU Switch | - | - | 33 | 630 | 36.0093 | 630 | 36.0093 | 630 | 36.0093 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.0093 | 36.0093 | 36.0093 | - | - | - | - | - | - | UHT36.009336289357 | ZoneSubstationUHT33630 | ZoneSubstationUHT33630 | 36.0093 | 630 | 630 | M303 | M301 | RMU Switch-M365 | 33
ZoneSubstationUHT33 | ZoneSubstationUHTE15233HV Winding | ZoneSubstation | UHT | M303 | M301 | 4 | AEL Transformers Database | E152 | Transformer | - | HV Winding | 33 | 26.2432 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | UHT | ZoneSubstationUHT33 | ZoneSubstationUHT3326.2431940540739 |  |  | 26.2432 | M303 | M301 | Transformer-E152-HV Winding | 33
ZoneSubstationUHT11 | ZoneSubstationUHTE15211LV Winding | ZoneSubstation | UHT | M303 | M301 | 5 | AEL Transformers Database | E152 | Transformer | - | LV Winding | 11 | 78.7296 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | UHT | ZoneSubstationUHT11 | ZoneSubstationUHT1178.7295821622217 |  |  | 78.7296 | M303 | M301 | Transformer-E152-LV Winding | 11
ZoneSubstationUHT11 | ZoneSubstationUHT3-1c 185 mm² AL XLPE11- | ZoneSubstation | UHT | M303 | M301 | 6 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11 | 326 | 6.2111 | 326 | 6.2111 | 326 | 6.2111 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 8.2 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 1 | - | 1 | 319.48 | 6.0869 | 6.2111 | 6.2111 | 6.2111 | - | - | - | - | - | 6.0869 | UHT6.08691151202315 | ZoneSubstationUHT11319.48 | ZoneSubstationUHT11319.48 | 6.0869 | 319.48 | 319.48 | M303 | M301 | Cable-3-1c 185 mm² AL XLPE | 11
ZoneSubstationUHT11 | ZoneSubstationUHTM30111- | ZoneSubstation | UHT | M303 | M301 | 7 | GEMA | M301 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | UHT12.0031120964523 | ZoneSubstationUHT11630 | ZoneSubstationUHT11630 | 12.0031 | 630 | 630 | M303 | M301 | RMU Switch-M301 | 11
DistributionFeederM158_Village11 | DistributionFeederM158_VillageUHT-M15811Protection | DistributionFeeder | M158_Village | M158 | M148 | 1 | GEMA/AEL Protection Database | UHT-M158 | Circuit Breaker | Siemens 8DJH | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 100 | 1.9053 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 1.9053 | - | - | - | M158_Village1.90525588832577 | DistributionFeederM158_Village11100 | DistributionFeederM158_Village11100 | 1.9053 | 100 | 100 | M158 | M148 | Circuit Breaker-UHT-M158-Protection | 11
DistributionFeederM158_Village11 | DistributionFeederM158_VillageM36411- | DistributionFeeder | M158_Village | M158 | M148 | 2 | GEMA | M364 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | M158_Village12.0031120964523 | DistributionFeederM158_Village11630 | DistributionFeederM158_Village11630 | 12.0031 | 630 | 630 | M158 | M148 | RMU Switch-M364 | 11
DistributionFeederM158_Village11 | DistributionFeederM158_Village3-1c 185 mm² AL XLPE11- | DistributionFeeder | M158_Village | M158 | M148 | 3 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11 | 326 | 6.2111 | 326 | 6.2111 | 326 | 6.2111 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 16.4 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 287.532 | 5.4782 | 6.2111 | 6.2111 | 6.2111 | - | - | - | - | - | 5.4782 | M158_Village5.47822036082084 | DistributionFeederM158_Village11287.532 | DistributionFeederM158_Village11287.532 | 5.4782 | 287.532 | 287.532 | M158 | M148 | Cable-3-1c 185 mm² AL XLPE | 11
DistributionFeederM158_Village11 | DistributionFeederM158_VillageM26811- | DistributionFeeder | M158_Village | M158 | M148 | 4 | GEMA | M268 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M158_Village | DistributionFeederM158_Village11 | DistributionFeederM158_Village11 |  |  |  | M158 | M148 | Link-M268 | 11
DistributionFeederM158_Village11 | DistributionFeederM158_Village3-1c 185 mm² AL XLPE11- | DistributionFeeder | M158_Village | M158 | M148 | 5 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11 | 326 | 6.2111 | 326 | 6.2111 | 326 | 6.2111 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 10.9 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 287.532 | 5.4782 | 6.2111 | 6.2111 | 6.2111 | - | - | - | - | - | 5.4782 | M158_Village5.47822036082084 | DistributionFeederM158_Village11287.532 | DistributionFeederM158_Village11287.532 | 5.4782 | 287.532 | 287.532 | M158 | M148 | Cable-3-1c 185 mm² AL XLPE | 11
DistributionFeederM158_Village11 | DistributionFeederM158_Village1-3c 150 mm² Al PILC11- | DistributionFeeder | M158_Village | M158 | M148 | 6 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 3586.8 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.92 | 1 | 259.7 | 4.9479 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 4.9479 | M158_Village4.94794954198201 | DistributionFeederM158_Village11259.7 | DistributionFeederM158_Village11259.7 | 4.9479 | 259.7 | 259.7 | M158 | M148 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederM159_Village11 | DistributionFeederM159_VillageUHT-M15911Protection | DistributionFeeder | M159_Village | M159 | M160 | 1 | GEMA/AEL Protection Database | UHT-M159 | Circuit Breaker | Siemens 8DJH | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 100 | 1.9053 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 1.9053 | - | - | - | M159_Village1.90525588832577 | DistributionFeederM159_Village11100 | DistributionFeederM159_Village11100 | 1.9053 | 100 | 100 | M159 | M160 | Circuit Breaker-UHT-M159-Protection | 11
DistributionFeederM159_Village11 | DistributionFeederM159_VillageM36311- | DistributionFeeder | M159_Village | M159 | M160 | 2 | GEMA | M363 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | M159_Village12.0031120964523 | DistributionFeederM159_Village11630 | DistributionFeederM159_Village11630 | 12.0031 | 630 | 630 | M159 | M160 | RMU Switch-M363 | 11
DistributionFeederM159_Village11 | DistributionFeederM159_Village3-1c 185 mm² AL XLPE11- | DistributionFeeder | M159_Village | M159 | M160 | 3 | GEMA/General Cables | 3-1c 185 mm² AL XLPE | Cable | - | - | 11 | 326 | 6.2111 | 326 | 6.2111 | 326 | 6.2111 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 19.5 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.6 | 0.9 | 287.532 | 5.4782 | 6.2111 | 6.2111 | 6.2111 | - | - | - | - | - | 5.4782 | M159_Village5.47822036082084 | DistributionFeederM159_Village11287.532 | DistributionFeederM159_Village11287.532 | 5.4782 | 287.532 | 287.532 | M159 | M160 | Cable-3-1c 185 mm² AL XLPE | 11
DistributionFeederM159_Village11 | DistributionFeederM159_Village1-3c 150 mm² Al PILC11- | DistributionFeeder | M159_Village | M159 | M160 | 4 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 3586.8 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 2 | 0.92 | 1 | 259.7 | 4.9479 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 4.9479 | M159_Village4.94794954198201 | DistributionFeederM159_Village11259.7 | DistributionFeederM159_Village11259.7 | 4.9479 | 259.7 | 259.7 | M159 | M160 | Cable-1-3c 150 mm² Al PILC | 11
ZoneSubstationTEK33 | ZoneSubstationTEKUnknown Line33- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 1 | GEMA/AEL OH Amp Calc. | Unknown Line | OH Line | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK33 | ZoneSubstationTEK33 |  |  |  | M11 T-off | 11 kV Bus | OH Line-Unknown Line | 33
ZoneSubstationTEK33 | ZoneSubstationTEKM16633- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 2 | GEMA | M166 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK33 | ZoneSubstationTEK33 |  |  |  | M11 T-off | 11 kV Bus | ABS-M166 | 33
ZoneSubstationTEK33 | ZoneSubstationTEKTEK-M16733Protection | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 3 | GEMA/AEL Protection Database | TEK-M167 | Circuit Breaker | Relay SEL 311C | Protection | 33 | 2000 | 114.3154 | 2000 | 114.3154 | 2000 | 114.3154 | - | - | - | - | 150 | 8.5737 | - | - | - | - | 200 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 114.3154 | 114.3154 | 114.3154 | - | - | 8.5737 | - | 11.4315 | - | TEK8.57365149746594 | ZoneSubstationTEK33150 | ZoneSubstationTEK33150 | 8.5737 | 150 | 150 | M11 T-off | 11 kV Bus | Circuit Breaker-TEK-M167-Protection | 33
ZoneSubstationTEK33 | ZoneSubstationTEKM16833- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 4 | GEMA | M168 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK33 | ZoneSubstationTEK33 |  |  |  | M11 T-off | 11 kV Bus | ABS-M168 | 33
ZoneSubstationTEK33 | ZoneSubstationTEKIODINE33- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 5 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33 | 471.546 | 26.9525 | - | - | 408.8746 | 23.3703 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.2 | - | - | - | - | - | - | - | - | - | - | - | 26.9525 | - | 23.3703 | - | - | - | - | - | - | TEK23.3703236603694 | ZoneSubstationTEK33408.874625950392 | ZoneSubstationTEK33408.874625950392 | 23.3703 | 408.8746 | 408.8746 | M11 T-off | 11 kV Bus | OH Line-IODINE | 33
ZoneSubstationTEK33 | ZoneSubstationTEKE19733HV Winding | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 6 | AEL Transformers Database | E197 | Transformer | - | HV Winding | 33 | 109.3466 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK33 | ZoneSubstationTEK33109.346641891975 |  |  | 109.3466 | M11 T-off | 11 kV Bus | Transformer-E197-HV Winding | 33
ZoneSubstationTEK11 | ZoneSubstationTEKE19711LV Winding | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 7 | AEL Transformers Database | E197 | Transformer | - | LV Winding | 11 | 328.0399 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK11 | ZoneSubstationTEK11328.039925675924 |  |  | 328.0399 | M11 T-off | 11 kV Bus | Transformer-E197-LV Winding | 11
ZoneSubstationTEK11 | ZoneSubstationTEKIODINE11- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 8 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 11 | 471.546 | 8.9842 | - | - | 408.8746 | 7.7901 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.1 | - | - | - | - | - | - | - | - | - | - | - | 8.9842 | - | 7.7901 | - | - | - | - | - | - | TEK7.79010788678979 | ZoneSubstationTEK11408.874625950392 | ZoneSubstationTEK11408.874625950392 | 7.7901 | 408.8746 | 408.8746 | M11 T-off | 11 kV Bus | OH Line-IODINE | 11
ZoneSubstationTEK11 | ZoneSubstationTEKM17011- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 9 | GEMA | M170 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TEK | ZoneSubstationTEK11 | ZoneSubstationTEK11 |  |  |  | M11 T-off | 11 kV Bus | Link-M170 | 11
ZoneSubstationTEK11 | ZoneSubstationTEK3-1c 400 mm² Al XLPE11- | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 10 | GEMA/General Cables | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 74.8 | 1 | 0.97 | 15 | 1 | 0.9 | 1.12 | 4 | 0.3 | 0.96 | 560.0609 | 10.6706 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 10.6706 | TEK10.2312241203094 | ZoneSubstationTEK11537 | ZoneSubstationTEK11537 | 10.2312 | 537 | 537 | M11 T-off | 11 kV Bus | Cable-3-1c 400 mm² Al XLPE | 11
ZoneSubstationTEK11 | ZoneSubstationTEKTEK-M20211Protection | ZoneSubstation | TEK | M11 T-off | 11 kV Bus | 11 | GEMA/AEL Protection Database | TEK-M202 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 400 | 7.621 | - | - | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 7.621 | - | 7.621 | - | TEK7.62102355330306 | ZoneSubstationTEK11400 | ZoneSubstationTEK11400 | 7.621 | 400 | 400 | M11 T-off | 11 kV Bus | Circuit Breaker-TEK-M202-Protection | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_LilybankTEK-M20011Protection | DistributionFeeder | M200_Haldon_Lilybank | 11 kV Bus | M194 | 1 | GEMA/AEL Protection Database | TEK-M200 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 276 | 5.2585 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 5.2585 | - | - | - | M200_Haldon_Lilybank5.25850625177911 | DistributionFeederM200_Haldon_Lilybank11276 | DistributionFeederM200_Haldon_Lilybank11276 | 5.2585 | 276 | 276 | 11 kV Bus | M194 | Circuit Breaker-TEK-M200-Protection | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_Lilybank1-3c 150 mm² Al PILC11- | DistributionFeeder | M200_Haldon_Lilybank | 11 kV Bus | M194 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 75.9 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | M200_Haldon_Lilybank3.55555614944344 | DistributionFeederM200_Haldon_Lilybank11186.6183 | DistributionFeederM200_Haldon_Lilybank11186.6183 | 3.5556 | 186.6183 | 186.6183 | 11 kV Bus | M194 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_LilybankM19411- | DistributionFeeder | M200_Haldon_Lilybank | 11 kV Bus | M194 | 3 | GEMA | M194 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M200_Haldon_Lilybank | DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_Lilybank11 |  |  |  | 11 kV Bus | M194 | Link-M194 | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_LilybankUnknown Line11- | DistributionFeeder | M200_Haldon_Lilybank | M194 | Pole 14140 | 4 | GEMA/AEL OH Amp Calc. | Unknown Line | OH Line | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M200_Haldon_Lilybank | DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_Lilybank11 |  |  |  | M194 | Pole 14140 | OH Line-Unknown Line | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_LilybankMINK11- | DistributionFeeder | M200_Haldon_Lilybank | M194 | Pole 14140 | 5 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11 | 250.5823 | 4.7742 | - | - | 188.6266 | 3.5938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 252.2 | - | - | - | - | - | - | - | - | - | - | - | 4.7742 | - | 3.5938 | - | - | - | - | - | - | M200_Haldon_Lilybank3.59381954101092 | DistributionFeederM200_Haldon_Lilybank11188.626607220145 | DistributionFeederM200_Haldon_Lilybank11188.626607220145 | 3.5938 | 188.6266 | 188.6266 | M194 | Pole 14140 | OH Line-MINK | 11
DistributionFeederM200_Haldon_Lilybank11 | DistributionFeederM200_Haldon_LilybankDOG11- | DistributionFeeder | M200_Haldon_Lilybank | M194 | Pole 14140 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 343.6934 | 6.5482 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 822.3 | - | - | - | - | - | - | - | - | - | - | - | 6.5482 | - | 4.8938 | - | - | - | - | - | - | M200_Haldon_Lilybank4.89381213609487 | DistributionFeederM200_Haldon_Lilybank11256.858523103439 | DistributionFeederM200_Haldon_Lilybank11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | M194 | Pole 14140 | OH Line-DOG | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_SimonsTEK-M20111Protection | DistributionFeeder | M201_Simons | 11 kV Bus | M175 | 1 | GEMA/AEL Protection Database | TEK-M201 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 250 | 4.7631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 4.7631 | - | - | - | M201_Simons4.76313972081441 | DistributionFeederM201_Simons11250 | DistributionFeederM201_Simons11250 | 4.7631 | 250 | 250 | 11 kV Bus | M175 | Circuit Breaker-TEK-M201-Protection | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_Simons1-3c 150 mm² Al PILC11- | DistributionFeeder | M201_Simons | 11 kV Bus | M175 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 70.7 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | M201_Simons3.55555614944344 | DistributionFeederM201_Simons11186.6183 | DistributionFeederM201_Simons11186.6183 | 3.5556 | 186.6183 | 186.6183 | 11 kV Bus | M175 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_SimonsM17511 | DistributionFeeder | M201_Simons | M175 | Pole 25260 | 3 | GEMA | M175 | Link |  |  | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M201_Simons | DistributionFeederM201_Simons11 | DistributionFeederM201_Simons11 |  |  |  | M175 | Pole 25260 | Link-M175- | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_SimonsHERRING11- | DistributionFeeder | M201_Simons | M175 | Pole 25260 | 4 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.5 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | M201_Simons1.40435251412357 | DistributionFeederM201_Simons1173.7093910969426 | DistributionFeederM201_Simons1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M175 | Pole 25260 | OH Line-HERRING | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_SimonsM29711 | DistributionFeeder | M201_Simons | M175 | Pole 25260 | 5 | GEMA | M297 | Link |  |  | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | M201_Simons5.7157676649773 | DistributionFeederM201_Simons11300 | DistributionFeederM201_Simons11300 | 5.7158 | 300 | 300 | M175 | Pole 25260 | Link-M297- | 11
DistributionFeederM201_Simons11 | DistributionFeederM201_SimonsHERRING11- | DistributionFeeder | M201_Simons | M175 | Pole 25260 | 6 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1169.5 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | M201_Simons1.40435251412357 | DistributionFeederM201_Simons1173.7093910969426 | DistributionFeederM201_Simons1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M175 | Pole 25260 | OH Line-HERRING | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyTEK-M20511Protection | DistributionFeeder | M205_Godley | 11 kV Bus | M184 | 1 | GEMA/AEL Protection Database | TEK-M205 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 200 | 3.8105 | - | - | - | - | 100 | 1.9053 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 3.8105 | - | 1.9053 | - | M205_Godley1.90525588832577 | DistributionFeederM205_Godley11100 | DistributionFeederM205_Godley11100 | 1.9053 | 100 | 100 | 11 kV Bus | M184 | Circuit Breaker-TEK-M205-Protection | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_Godley1-3c 150 mm² Al PILC11- | DistributionFeeder | M205_Godley | 11 kV Bus | M184 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 70.7 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | M205_Godley3.55555614944344 | DistributionFeederM205_Godley11186.6183 | DistributionFeederM205_Godley11186.6183 | 3.5556 | 186.6183 | 186.6183 | 11 kV Bus | M184 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyM18411- | DistributionFeeder | M205_Godley | 11 kV Bus | M184 | 3 | GEMA | M184 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M205_Godley | DistributionFeederM205_Godley11 | DistributionFeederM205_Godley11 |  |  |  | 11 kV Bus | M184 | Link-M184 | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyUnknown Line11- | DistributionFeeder | M205_Godley | M184 | M186 | 4 | GEMA/AEL OH Amp Calc. | Unknown Line | OH Line | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M205_Godley | DistributionFeederM205_Godley11 | DistributionFeederM205_Godley11 |  |  |  | M184 | M186 | OH Line-Unknown Line | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyM18611- | DistributionFeeder | M205_Godley | M186 | M296 | 5 | GEMA | M186 | ABS | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M205_Godley | DistributionFeederM205_Godley11 | DistributionFeederM205_Godley11 |  |  |  | M186 | M296 | ABS-M186 | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyHERRING11- | DistributionFeeder | M205_Godley | M186 | M296 | 6 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.4 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | M205_Godley1.40435251412357 | DistributionFeederM205_Godley1173.7093910969426 | DistributionFeederM205_Godley1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M186 | M296 | OH Line-HERRING | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyHERRING11- | DistributionFeeder | M205_Godley | M296 | Pole 14106 | 8 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1176.2 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | M205_Godley1.40435251412357 | DistributionFeederM205_Godley1173.7093910969426 | DistributionFeederM205_Godley1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M296 | Pole 14106 | OH Line-HERRING | 11
DistributionFeederM205_Godley11 | DistributionFeederM205_GodleyM29611- | DistributionFeeder | M205_Godley | M186 | M296 | 7 | GEMA | M296 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | M205_Godley5.7157676649773 | DistributionFeederM205_Godley11300 | DistributionFeederM205_Godley11300 | 5.7158 | 300 | 300 | M186 | M296 | Link-M296 | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo TownshipTEK-M20611Protection | DistributionFeeder | M206_Tekapo Township | 11 kV Bus | M180 | 1 | GEMA/AEL Protection Database | TEK-M206 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 276 | 5.2585 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 5.2585 | - | - | - | M206_Tekapo Township5.25850625177911 | DistributionFeederM206_Tekapo Township11276 | DistributionFeederM206_Tekapo Township11276 | 5.2585 | 276 | 276 | 11 kV Bus | M180 | Circuit Breaker-TEK-M206-Protection | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo Township1-3c 150 mm² Al PILC11- | DistributionFeeder | M206_Tekapo Township | 11 kV Bus | M180 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 68 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | M206_Tekapo Township3.55555614944344 | DistributionFeederM206_Tekapo Township11186.6183 | DistributionFeederM206_Tekapo Township11186.6183 | 3.5556 | 186.6183 | 186.6183 | 11 kV Bus | M180 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo Township3-1c 185 mm² Al XLPE11- | DistributionFeeder | M206_Tekapo Township | 11 kV Bus | M180 | 3 | GEMA/General Cables | 3-1c 185 mm² Al XLPE | Cable | - | - | 11 | 362 | 6.897 | 362 | 6.897 | 362 | 6.897 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 3.5 | 1 | 0.98 | 15 | 1 | 0.9 | 1.12 | 1 | 0 | 1 | 397.3312 | 7.5702 | 6.897 | 6.897 | 6.897 | - | - | - | - | - | 7.5702 | M206_Tekapo Township6.89702631573927 | DistributionFeederM206_Tekapo Township11362 | DistributionFeederM206_Tekapo Township11362 | 6.897 | 362 | 362 | 11 kV Bus | M180 | Cable-3-1c 185 mm² Al XLPE | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo TownshipM18011- | DistributionFeeder | M206_Tekapo Township | 11 kV Bus | M180 | 4 | GEMA | M180 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M206_Tekapo Township | DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo Township11 |  |  |  | 11 kV Bus | M180 | Link-M180 | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo TownshipMINK11- | DistributionFeeder | M206_Tekapo Township | M180 | Pole 14122 | 5 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11 | 250.5823 | 4.7742 | - | - | 188.6266 | 3.5938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 254.9 | - | - | - | - | - | - | - | - | - | - | - | 4.7742 | - | 3.5938 | - | - | - | - | - | - | M206_Tekapo Township3.59381954101092 | DistributionFeederM206_Tekapo Township11188.626607220145 | DistributionFeederM206_Tekapo Township11188.626607220145 | 3.5938 | 188.6266 | 188.6266 | M180 | Pole 14122 | OH Line-MINK | 11
DistributionFeederM206_Tekapo Township11 | DistributionFeederM206_Tekapo TownshipDOG11- | DistributionFeeder | M206_Tekapo Township | M181 | Pole 14123 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 343.6934 | 6.5482 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 222.5 | - | - | - | - | - | - | - | - | - | - | - | 6.5482 | - | 4.8938 | - | - | - | - | - | - | M206_Tekapo Township4.89381213609487 | DistributionFeederM206_Tekapo Township11256.858523103439 | DistributionFeederM206_Tekapo Township11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | M181 | Pole 14123 | OH Line-DOG | 11
SecondarySubstationHLB11 | SecondarySubstationHLBTEK-M20011Protection | SecondarySubstation | HLB | M200 | M194 | 1 | GEMA/AEL Protection Database | TEK-M200 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | 276 | 5.2585 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | 5.2585 | - | - | - | HLB5.25850625177911 | SecondarySubstationHLB11276 | SecondarySubstationHLB11276 | 5.2585 | 276 | 276 | M200 | M194 | Circuit Breaker-TEK-M200-Protection | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 150 mm² Al PILC11- | SecondarySubstation | HLB | M200 | M194 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 75.9 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | HLB3.55555614944344 | SecondarySubstationHLB11186.6183 | SecondarySubstationHLB11186.6183 | 3.5556 | 186.6183 | 186.6183 | M200 | M194 | Cable-1-3c 150 mm² Al PILC | 11
SecondarySubstationHLB11 | SecondarySubstationHLBM19411- | SecondarySubstation | HLB | M200 | M194 | 3 | GEMA | M194 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HLB | SecondarySubstationHLB11 | SecondarySubstationHLB11 |  |  |  | M200 | M194 | Link-M194 | 11
SecondarySubstationHLB11 | SecondarySubstationHLBUnknown Line11- | SecondarySubstation | HLB | M194 | Pole 14140 | 4 | GEMA/AEL OH Amp Calc. | Unknown Line | OH Line | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HLB | SecondarySubstationHLB11 | SecondarySubstationHLB11 |  |  |  | M194 | Pole 14140 | OH Line-Unknown Line | 11
SecondarySubstationHLB11 | SecondarySubstationHLBMINK11- | SecondarySubstation | HLB | M194 | Pole 14140 | 5 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11 | 250.5823 | 4.7742 | - | - | 188.6266 | 3.5938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 252.2 | - | - | - | - | - | - | - | - | - | - | - | 4.7742 | - | 3.5938 | - | - | - | - | - | - | HLB3.59381954101092 | SecondarySubstationHLB11188.626607220145 | SecondarySubstationHLB11188.626607220145 | 3.5938 | 188.6266 | 188.6266 | M194 | Pole 14140 | OH Line-MINK | 11
SecondarySubstationHLB11 | SecondarySubstationHLBDOG11- | SecondarySubstation | HLB | M194 | Pole 14140 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 343.6934 | 6.5482 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 822.3 | - | - | - | - | - | - | - | - | - | - | - | 6.5482 | - | 4.8938 | - | - | - | - | - | - | HLB4.89381213609487 | SecondarySubstationHLB11256.858523103439 | SecondarySubstationHLB11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | M194 | Pole 14140 | OH Line-DOG | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 300 mm² Al XLPE11- | SecondarySubstation | HLB | Pole 14140 | M242 | 7 | GEMA/General Cables | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 528.5 | 1.3 | 0.959 | 15 | 1 | 0.9 | 1.11 | 3 | 0.6 | 0.85 | 430.6927 | 8.2058 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 8.2058 | HLB8.20579715092152 | SecondarySubstationHLB11430.692654 | SecondarySubstationHLB11430.692654 | 8.2058 | 430.6927 | 430.6927 | Pole 14140 | M242 | Cable-1-3c 300 mm² Al XLPE | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 95 mm² Al PILC11- | SecondarySubstation | HLB | M244 | M193 | 8 | GEMA/General Cables | 1-3c 95 mm² Al PILC | Cable | - | - | 11 | 205 | 3.9058 | 205 | 3.9058 | 205 | 3.9058 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 438.8 | 1 | 0.98 | 15 | 1 | 0.9 | 1.1 | 3 | 0.6 | 0.86 | 190.0514 | 3.621 | 3.9058 | 3.9058 | 3.9058 | - | - | - | - | - | 3.621 | HLB3.62096548934555 | SecondarySubstationHLB11190.0514 | SecondarySubstationHLB11190.0514 | 3.621 | 190.0514 | 190.0514 | M244 | M193 | Cable-1-3c 95 mm² Al PILC | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 95 mm² Al XLPE11- | SecondarySubstation | HLB | M244 | M193 | 9 | GEMA/General Cables | 1-3c 95 mm² Al XLPE | Cable | - | - | 11 | 253 | 4.8203 | 253 | 4.8203 | 253 | 4.8203 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 4.7 | 1 | 0.98 | 15 | 1 | 0.9 | 1.1 | 3 | 0.6 | 0.86 | 234.5512 | 4.4688 | 4.8203 | 4.8203 | 4.8203 | - | - | - | - | - | 4.4688 | HLB4.4688013112411 | SecondarySubstationHLB11234.55124 | SecondarySubstationHLB11234.55124 | 4.4688 | 234.5512 | 234.5512 | M244 | M193 | Cable-1-3c 95 mm² Al XLPE | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 95 mm² Al PILC11- | SecondarySubstation | HLB | M244 | M193 | 10 | GEMA/General Cables | 1-3c 95 mm² Al PILC | Cable | - | - | 11 | 205 | 3.9058 | 205 | 3.9058 | 205 | 3.9058 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 416.9 | 1 | 0.98 | 15 | 1 | 0.9 | 1.1 | 1 | 0 | 1 | 220.99 | 4.2104 | 3.9058 | 3.9058 | 3.9058 | - | - | - | - | - | 4.2104 | HLB3.90577457106782 | SecondarySubstationHLB11205 | SecondarySubstationHLB11205 | 3.9058 | 205 | 205 | M244 | M193 | Cable-1-3c 95 mm² Al PILC | 11
SecondarySubstationHLB11 | SecondarySubstationHLBM19311- | SecondarySubstation | HLB | M244 | M193 | 11 | GEMA | M193 | ABS | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HLB | SecondarySubstationHLB11 | SecondarySubstationHLB11 |  |  |  | M244 | M193 | ABS-M193 | 11
SecondarySubstationHLB11 | SecondarySubstationHLBHERRING11- | SecondarySubstation | HLB | M193 | Pole 14149 | 12 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 427.7 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | HLB1.40435251412357 | SecondarySubstationHLB1173.7093910969426 | SecondarySubstationHLB1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M193 | Pole 14149 | OH Line-HERRING | 11
SecondarySubstationHLB11 | SecondarySubstationHLB1-3c 95 mm² Al XLPE11- | SecondarySubstation | HLB | Pole 14149 | Pole 14150 | 13 | GEMA/General Cables | 1-3c 95 mm² Al XLPE | Cable | - | - | 11 | 253 | 4.8203 | 253 | 4.8203 | 253 | 4.8203 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 533.7 | 1 | 0.98 | 15 | 1 | 0.9 | 1.1 | 1 | 0 | 1 | 272.734 | 5.1963 | 4.8203 | 4.8203 | 4.8203 | - | - | - | - | - | 5.1963 | HLB4.82029739746419 | SecondarySubstationHLB11253 | SecondarySubstationHLB11253 | 4.8203 | 253 | 253 | Pole 14149 | Pole 14150 | Cable-1-3c 95 mm² Al XLPE | 11
SecondarySubstationHLB11 | SecondarySubstationHLBHERRING11- | SecondarySubstation | HLB | Pole 14150 | TX E117 | 14 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 347.7 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | HLB1.40435251412357 | SecondarySubstationHLB1173.7093910969426 | SecondarySubstationHLB1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | Pole 14150 | TX E117 | OH Line-HERRING | 11
SecondarySubstationHLB11 | SecondarySubstationHLBM8111- | SecondarySubstation | HLB | Pole 14150 | TX E117 | 1 | GEMA | M81 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | HLB5.7157676649773 | SecondarySubstationHLB11300 | SecondarySubstationHLB11300 | 5.7158 | 300 | 300 | Pole 14150 | TX E117 | Link-M81 | 11
SecondarySubstationHLB11 | SecondarySubstationHLBM8211Protection | SecondarySubstation | HLB | Pole 14150 | TX E117 | 2 | GEMA | M82 | Recloser | Relay SEL 351R | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 60 | 1.1432 | 60 | 1.1432 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 1.1432 | - | - | - | HLB1.14315353299546 | SecondarySubstationHLB1160 | SecondarySubstationHLB1160 | 1.1432 | 60 | 60 | Pole 14150 | TX E117 | Recloser-M82-Protection | 11
SecondarySubstationHLB11 | SecondarySubstationHLBM8311- | SecondarySubstation | HLB | Pole 14150 | TX E117 | 3 | GEMA | M83 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | HLB5.7157676649773 | SecondarySubstationHLB11300 | SecondarySubstationHLB11300 | 5.7158 | 300 | 300 | Pole 14150 | TX E117 | Link-M83 | 11
SecondarySubstationHLB11 | SecondarySubstationHLBE11711LV Winding | SecondarySubstation | HLB | Pole 14150 | TX E117 | 4 | AEL Transformers Database | E117 | Transformer | - | LV Winding | 11 | 52.4864 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HLB | SecondarySubstationHLB11 | SecondarySubstationHLB1152.4863881081478 |  |  | 52.4864 | Pole 14150 | TX E117 | Transformer-E117-LV Winding | 11
SecondarySubstationHLB22 | SecondarySubstationHLBE11722HV Winding | SecondarySubstation | HLB | Pole 14150 | TX E117 | 5 | AEL Transformers Database | E117 | Transformer | - | HV Winding | 22 | 26.2432 | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HLB | SecondarySubstationHLB22 | SecondarySubstationHLB2226.2431940540739 |  |  | 26.2432 | Pole 14150 | TX E117 | Transformer-E117-HV Winding | 22
SecondarySubstationHLB22 | SecondarySubstationHLBM8522- | SecondarySubstation | HLB | TX E117 | Pole 51596 | 6 | GEMA | M85 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | HLB11.4315353299546 | SecondarySubstationHLB22300 | SecondarySubstationHLB22300 | 11.4315 | 300 | 300 | TX E117 | Pole 51596 | Link-M85 | 22
SecondarySubstationHLB22 | SecondarySubstationHLBM8622Protection | SecondarySubstation | HLB | TX E117 | Pole 51596 | 7 | GEMA | M86 | Recloser | Relay SEL 351R | Protection | 22 | - | - | - | - | - | - | - | - | - | - | 30 | 1.1432 | 30 | 1.1432 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1.1432 | - | - | - | HLB1.14315353299546 | SecondarySubstationHLB2230 | SecondarySubstationHLB2230 | 1.1432 | 30 | 30 | TX E117 | Pole 51596 | Recloser-M86-Protection | 22
SecondarySubstationHLB22 | SecondarySubstationHLBM8722- | SecondarySubstation | HLB | TX E117 | Pole 51596 | 8 | GEMA | M87 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | HLB11.4315353299546 | SecondarySubstationHLB22300 | SecondarySubstationHLB22300 | 11.4315 | 300 | 300 | TX E117 | Pole 51596 | Link-M87 | 22
SecondarySubstationHLB22 | SecondarySubstationHLBMINK22- | SecondarySubstation | HLB | TX E117 | Pole 51596 | 9 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 22 | 250.5823 | 9.5485 | - | - | 188.6266 | 7.1876 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.8 | - | - | - | - | - | - | - | - | - | - | - | 9.5485 | - | 7.1876 | - | - | - | - | - | - | HLB7.18763908202184 | SecondarySubstationHLB22188.626607220145 | SecondarySubstationHLB22188.626607220145 | 7.1876 | 188.6266 | 188.6266 | TX E117 | Pole 51596 | OH Line-MINK | 22
DistributionFeederM32_Lilybank22 | DistributionFeederM32_LilybankMINK22- | DistributionFeeder | M32_Lilybank | Pole 51596 | M32 | 1 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 22 | 250.5823 | 9.5485 | - | - | 188.6266 | 7.1876 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1.1 | - | - | - | - | - | - | - | - | - | - | - | 9.5485 | - | 7.1876 | - | - | - | - | - | - | M32_Lilybank7.18763908202184 | DistributionFeederM32_Lilybank22188.626607220145 | DistributionFeederM32_Lilybank22188.626607220145 | 7.1876 | 188.6266 | 188.6266 | Pole 51596 | M32 | OH Line-MINK | 22
DistributionFeederM32_Lilybank22 | DistributionFeederM32_LilybankHERRING22- | DistributionFeeder | M32_Lilybank | M32 | TX E58 | 2 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 22 | 96.3773 | 3.6725 | - | - | 73.7094 | 2.8087 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1592.3 | - | - | - | - | - | - | - | - | - | - | - | 3.6725 | - | 2.8087 | - | - | - | - | - | - | M32_Lilybank2.80870502824713 | DistributionFeederM32_Lilybank2273.7093910969426 | DistributionFeederM32_Lilybank2273.7093910969426 | 2.8087 | 73.7094 | 73.7094 | M32 | TX E58 | OH Line-HERRING | 22
DistributionFeederM33_Haldon22 | DistributionFeederM33_HaldonMINK22- | DistributionFeeder | M33_Haldon | Pole 51596 | M33 | 1 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 22 | 250.5823 | 9.5485 | - | - | 188.6266 | 7.1876 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.8 | - | - | - | - | - | - | - | - | - | - | - | 9.5485 | - | 7.1876 | - | - | - | - | - | - | M33_Haldon7.18763908202184 | DistributionFeederM33_Haldon22188.626607220145 | DistributionFeederM33_Haldon22188.626607220145 | 7.1876 | 188.6266 | 188.6266 | Pole 51596 | M33 | OH Line-MINK | 22
DistributionFeederM33_Haldon22 | DistributionFeederM33_HaldonHERRING22- | DistributionFeeder | M33_Haldon | M33 | Pole 24654 | 2 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 22 | 96.3773 | 3.6725 | - | - | 73.7094 | 2.8087 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6004.6 | - | - | - | - | - | - | - | - | - | - | - | 3.6725 | - | 2.8087 | - | - | - | - | - | - | M33_Haldon2.80870502824713 | DistributionFeederM33_Haldon2273.7093910969426 | DistributionFeederM33_Haldon2273.7093910969426 | 2.8087 | 73.7094 | 73.7094 | M33 | Pole 24654 | OH Line-HERRING | 22
SecondarySubstationOMR11 | SecondarySubstationOMROMR-M20111Protection | SecondarySubstation | OMR | 11 kV Bus | M175 | 1 | GEMA/AEL Protection Database | OMR-M201 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | OMR11.4315353299546 | SecondarySubstationOMR11600 | SecondarySubstationOMR11600 | 11.4315 | 600 | 600 | 11 kV Bus | M175 | Circuit Breaker-OMR-M201-Protection | 11
SecondarySubstationOMR11 | SecondarySubstationOMR1-3c 150 mm² Al PILC11- | SecondarySubstation | OMR | 11 kV Bus | M175 | 2 | GEMA/General Cables | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 70.7 | 1.1 | 0.97 | 15 | 1 | 0.9 | 1.1 | 5 | 0.15 | 0.66 | 186.6183 | 3.5556 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.5556 | OMR3.55555614944344 | SecondarySubstationOMR11186.6183 | SecondarySubstationOMR11186.6183 | 3.5556 | 186.6183 | 186.6183 | 11 kV Bus | M175 | Cable-1-3c 150 mm² Al PILC | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM17511 | SecondarySubstation | OMR | M175 | Pole 25260 | 3 | GEMA | M175 | Link |  |  | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OMR | SecondarySubstationOMR11 | SecondarySubstationOMR11 |  |  |  | M175 | Pole 25260 | Link-M175- | 11
SecondarySubstationOMR11 | SecondarySubstationOMRHERRING11- | SecondarySubstation | OMR | M175 | Pole 25260 | 4 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.5 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | OMR1.40435251412357 | SecondarySubstationOMR1173.7093910969426 | SecondarySubstationOMR1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M175 | Pole 25260 | OH Line-HERRING | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM29711 | SecondarySubstation | OMR | M175 | Pole 25260 | 5 | GEMA | M297 | Link |  |  | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | OMR5.7157676649773 | SecondarySubstationOMR11300 | SecondarySubstationOMR11300 | 5.7158 | 300 | 300 | M175 | Pole 25260 | Link-M297- | 11
SecondarySubstationOMR11 | SecondarySubstationOMRHERRING11- | SecondarySubstation | OMR | M175 | Pole 25260 | 6 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1169.5 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | OMR1.40435251412357 | SecondarySubstationOMR1173.7093910969426 | SecondarySubstationOMR1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M175 | Pole 25260 | OH Line-HERRING | 11
SecondarySubstationOMR11 | SecondarySubstationOMRHERRING11- | SecondarySubstation | OMR | Pole 25260 | M306 | 7 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2090.9 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | OMR1.40435251412357 | SecondarySubstationOMR1173.7093910969426 | SecondarySubstationOMR1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | Pole 25260 | M306 | OH Line-HERRING | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM30511- | SecondarySubstation | OMR | Pole 25260 | M306 | 8 | GEMA | M305 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | OMR5.7157676649773 | SecondarySubstationOMR11300 | SecondarySubstationOMR11300 | 5.7158 | 300 | 300 | Pole 25260 | M306 | Link-M305 | 11
SecondarySubstationOMR11 | SecondarySubstationOMRE34311Controller | SecondarySubstation | OMR | Pole 25260 | M306 | 9 | GEMA/Equipment Name plate | E343 | Regulator | CL-7 | Controller | 11 | 200 | 3.8105 | 200 | 3.8105 | 200 | 3.8105 | - | - | - | - | 200 | 3.8105 | 200 | 3.8105 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.8105 | 3.8105 | 3.8105 | - | - | 3.8105 | - | - | - | OMR3.81051177665153 | SecondarySubstationOMR11200 | SecondarySubstationOMR11200 | 3.8105 | 200 | 200 | Pole 25260 | M306 | Regulator-E343-Controller | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM30611- | SecondarySubstation | OMR | Pole 25260 | M306 | 10 | GEMA | M306 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | OMR5.7157676649773 | SecondarySubstationOMR11300 | SecondarySubstationOMR11300 | 5.7158 | 300 | 300 | Pole 25260 | M306 | Link-M306 | 11
SecondarySubstationOMR11 | SecondarySubstationOMRHERRING11- | SecondarySubstation | OMR | M306 | M213 | 11 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1465 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | OMR1.40435251412357 | SecondarySubstationOMR1173.7093910969426 | SecondarySubstationOMR1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M306 | M213 | OH Line-HERRING | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM21311- | SecondarySubstation | OMR | M213 | M329 | 12 | GEMA | M213 | ABS | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OMR | SecondarySubstationOMR11 | SecondarySubstationOMR11 |  |  |  | M213 | M329 | ABS-M213 | 11
SecondarySubstationOMR11 | SecondarySubstationOMRHERRING11- | SecondarySubstation | OMR | M213 | M329 | 13 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 11 | 96.3773 | 1.8362 | - | - | 73.7094 | 1.4044 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 500 | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | - | 1.4044 | - | - | - | - | - | - | OMR1.40435251412357 | SecondarySubstationOMR1173.7093910969426 | SecondarySubstationOMR1173.7093910969426 | 1.4044 | 73.7094 | 73.7094 | M213 | M329 | OH Line-HERRING | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM32911- | SecondarySubstation | OMR | M329 | M339 | 1 | GEMA | M329 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | OMR5.7157676649773 | SecondarySubstationOMR11300 | SecondarySubstationOMR11300 | 5.7158 | 300 | 300 | M329 | M339 | Link-M329 | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM33111Protection | SecondarySubstation | OMR | M329 | M339 | 2 | GEMA/AEL Protection Database | M331 | Recloser | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 120 | 2.2863 | 120 | 2.2863 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 2.2863 | - | - | - | OMR2.28630706599092 | SecondarySubstationOMR11120 | SecondarySubstationOMR11120 | 2.2863 | 120 | 120 | M329 | M339 | Recloser-M331-Protection | 11
SecondarySubstationOMR11 | SecondarySubstationOMRM33211- | SecondarySubstation | OMR | M329 | M339 | 3 | GEMA | M332 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | OMR5.7157676649773 | SecondarySubstationOMR11300 | SecondarySubstationOMR11300 | 5.7158 | 300 | 300 | M329 | M339 | Link-M332 | 11
SecondarySubstationOMR11 | SecondarySubstationOMRIODINE11- | SecondarySubstation | OMR | M329 | M339 | 4 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 11 | 471.546 | 8.9842 | - | - | 408.8746 | 7.7901 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.2 | - | - | - | - | - | - | - | - | - | - | - | 8.9842 | - | 7.7901 | - | - | - | - | - | - | OMR7.79010788678979 | SecondarySubstationOMR11408.874625950392 | SecondarySubstationOMR11408.874625950392 | 7.7901 | 408.8746 | 408.8746 | M329 | M339 | OH Line-IODINE | 11
SecondarySubstationOMR11 | SecondarySubstationOMR3-1c 95 mm² Al XLPE11- | SecondarySubstation | OMR | M329 | M339 | 5 | GEMA/General Cables | 3-1c 95 mm² Al XLPE | Cable | - | - | 11 | 243 | 4.6298 | 243 | 4.6298 | 243 | 4.6298 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 3.8 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | - | 1 | 235.71 | 4.4909 | 4.6298 | 4.6298 | 4.6298 | - | - | - | - | - | 4.4909 | OMR4.49087865437266 | SecondarySubstationOMR11235.71 | SecondarySubstationOMR11235.71 | 4.4909 | 235.71 | 235.71 | M329 | M339 | Cable-3-1c 95 mm² Al XLPE | 11
SecondarySubstationOMR11 | SecondarySubstationOMRE35211LV Winding | SecondarySubstation | OMR | M329 | M339 | 6 | AEL Transformers Database | E352 | Transformer | - | LV Winding | 11 | 78.7296 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OMR | SecondarySubstationOMR11 | SecondarySubstationOMR1178.7295821622217 |  |  | 78.7296 | M329 | M339 | Transformer-E352-LV Winding | 11
SecondarySubstationOMR22 | SecondarySubstationOMRE35222HV Winding | SecondarySubstation | OMR | M329 | M339 | 7 | AEL Transformers Database | E352 | Transformer | - | HV Winding | 22 | 39.3648 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | OMR | SecondarySubstationOMR22 | SecondarySubstationOMR2239.3647910811109 |  |  | 39.3648 | M329 | M339 | Transformer-E352-HV Winding | 22
SecondarySubstationOMR22 | SecondarySubstationOMR3-1c 95 mm² Al XLPE22- | SecondarySubstation | OMR | M329 | M339 | 8 | GEMA/General Cables | 3-1c 95 mm² Al XLPE | Cable | - | - | 22 | 243 | 9.2595 | 243 | 9.2595 | 243 | 9.2595 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 4.2 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | - | 1 | 235.71 | 8.9818 | 9.2595 | 9.2595 | 9.2595 | - | - | - | - | - | 8.9818 | OMR8.98175730874532 | SecondarySubstationOMR22235.71 | SecondarySubstationOMR22235.71 | 8.9818 | 235.71 | 235.71 | M329 | M339 | Cable-3-1c 95 mm² Al XLPE | 22
SecondarySubstationOMR22 | SecondarySubstationOMRIODINE22- | SecondarySubstation | OMR | M329 | M339 | 9 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 22 | 471.546 | 17.9683 | - | - | 408.8746 | 15.5802 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.3 | - | - | - | - | - | - | - | - | - | - | - | 17.9683 | - | 15.5802 | - | - | - | - | - | - | OMR15.5802157735796 | SecondarySubstationOMR22408.874625950392 | SecondarySubstationOMR22408.874625950392 | 15.5802 | 408.8746 | 408.8746 | M329 | M339 | OH Line-IODINE | 22
SecondarySubstationOMR22 | SecondarySubstationOMRM33322- | SecondarySubstation | OMR | M329 | M339 | 10 | GEMA | M333 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | OMR11.4315353299546 | SecondarySubstationOMR22300 | SecondarySubstationOMR22300 | 11.4315 | 300 | 300 | M329 | M339 | Link-M333 | 22
SecondarySubstationOMR22 | SecondarySubstationOMRE35322Controller | SecondarySubstation | OMR | M329 | M339 | 11 | GEMA/Equipment Name plate | E353 | Regulator | CL-7 | Controller | 22 | 100 | 3.8105 | 200 | 7.621 | 200 | 7.621 | - | - | - | - | 200 | 7.621 | 200 | 7.621 | - | - | 200 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.8105 | 7.621 | 7.621 | - | - | 7.621 | - | 7.621 | - | OMR3.81051177665153 | SecondarySubstationOMR22100 | SecondarySubstationOMR22100 | 3.8105 | 100 | 100 | M329 | M339 | Regulator-E353-Controller | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeE35222HV Winding | DistributionFeeder | M338_Old Man Range | M329 | M339 | 1 | AEL Transformers Database | E352 | Transformer | - | HV Winding | 22 | 39.3648 | 1.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | M338_Old Man Range | DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man Range2239.3647910811109 |  |  | 39.3648 | M329 | M339 | Transformer-E352-HV Winding | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man Range3-1c 95 mm² Al XLPE22- | DistributionFeeder | M338_Old Man Range | M329 | M339 | 2 | GEMA/General Cables | 3-1c 95 mm² Al XLPE | Cable | - | - | 22 | 243 | 9.2595 | 243 | 9.2595 | 243 | 9.2595 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 4.2 | 1 | 0.97 | 15 | 1 | 1.2 | 1 | 1 | - | 1 | 235.71 | 8.9818 | 9.2595 | 9.2595 | 9.2595 | - | - | - | - | - | 8.9818 | M338_Old Man Range8.98175730874532 | DistributionFeederM338_Old Man Range22235.71 | DistributionFeederM338_Old Man Range22235.71 | 8.9818 | 235.71 | 235.71 | M329 | M339 | Cable-3-1c 95 mm² Al XLPE | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeIODINE22- | DistributionFeeder | M338_Old Man Range | M329 | M339 | 3 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 22 | 471.546 | 17.9683 | - | - | 408.8746 | 15.5802 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.3 | - | - | - | - | - | - | - | - | - | - | - | 17.9683 | - | 15.5802 | - | - | - | - | - | - | M338_Old Man Range15.5802157735796 | DistributionFeederM338_Old Man Range22408.874625950392 | DistributionFeederM338_Old Man Range22408.874625950392 | 15.5802 | 408.8746 | 408.8746 | M329 | M339 | OH Line-IODINE | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeM33322- | DistributionFeeder | M338_Old Man Range | M329 | M339 | 4 | GEMA | M333 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | M338_Old Man Range11.4315353299546 | DistributionFeederM338_Old Man Range22300 | DistributionFeederM338_Old Man Range22300 | 11.4315 | 300 | 300 | M329 | M339 | Link-M333 | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeE35322Controller | DistributionFeeder | M338_Old Man Range | M329 | M339 | 5 | GEMA/Equipment Name plate | E353 | Regulator | CL-7 | Controller | 22 | 100 | 3.8105 | 200 | 7.621 | 200 | 7.621 | - | - | - | - | 200 | 7.621 | 200 | 7.621 | - | - | 200 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.8105 | 7.621 | 7.621 | - | - | 7.621 | - | 7.621 | - | M338_Old Man Range3.81051177665153 | DistributionFeederM338_Old Man Range22100 | DistributionFeederM338_Old Man Range22100 | 3.8105 | 100 | 100 | M329 | M339 | Regulator-E353-Controller | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeM33522- | DistributionFeeder | M338_Old Man Range | M329 | M335 | 6 | GEMA | M335 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | M338_Old Man Range11.4315353299546 | DistributionFeederM338_Old Man Range22300 | DistributionFeederM338_Old Man Range22300 | 11.4315 | 300 | 300 | M329 | M335 | Link-M335 | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeIODINE22- | DistributionFeeder | M338_Old Man Range | M335 | Pole 51625 | 7 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 22 | 471.546 | 17.9683 | - | - | 408.8746 | 15.5802 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.2 | - | - | - | - | - | - | - | - | - | - | - | 17.9683 | - | 15.5802 | - | - | - | - | - | - | M338_Old Man Range15.5802157735796 | DistributionFeederM338_Old Man Range22408.874625950392 | DistributionFeederM338_Old Man Range22408.874625950392 | 15.5802 | 408.8746 | 408.8746 | M335 | Pole 51625 | OH Line-IODINE | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeM33622- | DistributionFeeder | M338_Old Man Range | M335 | Pole 51625 | 8 | GEMA | M336 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | M338_Old Man Range11.4315353299546 | DistributionFeederM338_Old Man Range22300 | DistributionFeederM338_Old Man Range22300 | 11.4315 | 300 | 300 | M335 | Pole 51625 | Link-M336 | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeOMR-M33822Protection | DistributionFeeder | M338_Old Man Range | M335 | Pole 51625 | 9 | GEMA/AEL Protection Database | OMR-M338 | Recloser | Relay SEL 751A | Protection | 22 | 630 | 24.0062 | 630 | 24.0062 | 630 | 24.0062 | - | - | - | - | 60 | 2.2863 | 60 | 2.2863 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.0062 | 24.0062 | 24.0062 | - | - | 2.2863 | - | - | - | M338_Old Man Range2.28630706599092 | DistributionFeederM338_Old Man Range2260 | DistributionFeederM338_Old Man Range2260 | 2.2863 | 60 | 60 | M335 | Pole 51625 | Recloser-OMR-M338-Protection | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeM33922- | DistributionFeeder | M338_Old Man Range | M335 | Pole 51625 | 10 | GEMA | M339 | Link | - | - | 22 | 300 | 11.4315 | 300 | 11.4315 | 300 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | M338_Old Man Range11.4315353299546 | DistributionFeederM338_Old Man Range22300 | DistributionFeederM338_Old Man Range22300 | 11.4315 | 300 | 300 | M335 | Pole 51625 | Link-M339 | 22
DistributionFeederM338_Old Man Range22 | DistributionFeederM338_Old Man RangeHERRING22- | DistributionFeeder | M338_Old Man Range | M335 | Pole 51625 | 11 | GEMA/AEL OH Amp Calc. | HERRING | OH Line | - | - | 22 | 96.3773 | 3.6725 | - | - | 73.7094 | 2.8087 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1800.9 | - | - | - | - | - | - | - | - | - | - | - | 3.6725 | - | 2.8087 | - | - | - | - | - | - | M338_Old Man Range2.80870502824713 | DistributionFeederM338_Old Man Range2273.7093910969426 | DistributionFeederM338_Old Man Range2273.7093910969426 | 2.8087 | 73.7094 | 73.7094 | M335 | Pole 51625 | OH Line-HERRING | 22
[13 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1.8362 | 3.8105 | 1.4044 | 12.0031 | 12.0031 | 1.1432 | 34.2946 | 1.9053 | 3.5556 | - | - |  | 1.1432 | - |  | - | - | - | -
Note on I52: Author: Rating obtained by using rating from drawijng 782 of 200 A and scaling it similar to DOG
Note on I55: Author: Rating obtained by using rating from drawijng 782 of 200 A and scaling it similar to DOG
Note on N112: Author: Based on 50°C design
Note on R112: Author: Based on 50°C design
Note on N113: Author: Based on 50°C design
Note on R113: Author: Based on 50°C design

## TMK_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of | ID | Type | ID | Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal R. |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [5 empty] | Data |  |  |  |  | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | - | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPTMK_GXP110T1 | GXPTMK_GXPDOG110- | GXP | TMK_GXP | DS134 | 33 kV Bus | 1 | TP Branch Report TIM.TMK.1 | DOG | OH Line | - | - | 110 | 413 | 78.6871 | 394 | 75.0671 | 375 | 71.4471 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16000 | - | - | - | - | - | - | - | - | - | - | - | 78.6871 | 75.0671 | 71.4471 | - | - | - | - | - | - | TMK_GXP71.4470958122162 | GXPTMK_GXP110375 | GXPTMK_GXP110375 | 71.4471 | 375 | 375 | DS134 | 33 kV Bus | OH Line-DOG | 110
GXPTMK_GXP110T1 | GXPTMK_GXPWOLF110- | GXP | TMK_GXP | DS134 | 33 kV Bus | 2 | TP Branch Report TIM.TMK.1 | WOLF | OH Line | - | - | 110 | 531 | 101.1691 | 507 | 96.5965 | 482 | 91.8333 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2000 | - | - | - | - | - | - | - | - | - | - | - | 101.1691 | 96.5965 | 91.8333 | - | - | - | - | - | - | TMK_GXP91.8333338173019 | GXPTMK_GXP110482 | GXPTMK_GXP110482 | 91.8333 | 482 | 482 | DS134 | 33 kV Bus | OH Line-WOLF | 110
GXPTMK_GXP110T1 | GXPTMK_GXPTMK-BS-110-134-T1110- | GXP | TMK_GXP | DS134 | 33 kV Bus | 3 | TP Branch Report TMK.TF.T1 | TMK-BS-110-134-T1 | Bus | - | - | 110 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 171.473 | 171.473 | 171.473 | 171.473 | 171.473 | - | - | - | - | TMK_GXP171.473029949319 | GXPTMK_GXP110900 | GXPTMK_GXP110900 | 171.473 | 900 | 900 | DS134 | 33 kV Bus | Bus-TMK-BS-110-134-T1 | 110
GXPTMK_GXP110T1 | GXPTMK_GXPTMK-CB132110Protection | GXP | TMK_GXP | DS134 | 33 kV Bus | 4 | TP Branch Report TMK.TF.T1 | TMK-CB132 | Circuit Breaker | Relay SR760 | Protection | 110 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 359 | 68.3987 | - | - | 900 | 171.473 | 600 | 114.3154 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 476.314 | 476.314 | 476.314 | 476.314 | 476.314 | 68.3987 | 171.473 | 114.3154 | - | TMK_GXP68.398686390895 | GXPTMK_GXP110359 | GXPTMK_GXP110359 | 68.3987 | 359 | 359 | DS134 | 33 kV Bus | Circuit Breaker-TMK-CB132-Protection | 110
GXPTMK_GXP110T1 | GXPTMK_GXPTMK-TF-T1110Bushings | GXP | TMK_GXP | DS134 | 33 kV Bus | 5 | TP Branch Report TMK.TF.T1 | TMK-TF-T1 | Transformer | TMK-TF-T1 | Bushings | 110 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | 960 | 182.9046 | 960 | 182.9046 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 152.4205 | 152.4205 | 152.4205 | 182.9046 | 182.9046 | - | - | - | - | TMK_GXP152.420471066061 | GXPTMK_GXP110800 | GXPTMK_GXP110800 | 152.4205 | 800 | 800 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-Bushings | 110
GXPTMK_GXP110T1 | GXPTMK_GXPTMK-TF-T1110TapChanger | GXP | TMK_GXP | DS134 | 33 kV Bus | 6 | TP Branch Report TMK.TF.T1 | TMK-TF-T1 | Transformer | - | TapChanger | 110 | 300 | 57.1577 | 300 | 57.1577 | 300 | 57.1577 | 360 | 68.5892 | 360 | 68.5892 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 57.1577 | 57.1577 | 57.1577 | 68.5892 | 68.5892 | - | - | - | - | TMK_GXP57.1576766497729 | GXPTMK_GXP110300 | GXPTMK_GXP110300 | 57.1577 | 300 | 300 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-TapChanger | 110
GXPTMK_GXP110T1 | GXPTMK_GXPTMK-TF-T1110HV Winding | GXP | TMK_GXP | DS134 | 33 kV Bus | 7 | TP Branch Report TMK.TF.T1 | TMK-TF-T1 | Transformer | - | HV Winding | 110 | 283.4265 | 54 | - | - | - | - | 332 | 63.2545 | 319 | 60.7777 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK_GXP | GXPTMK_GXP110 | GXPTMK_GXP110283.426495783998 |  |  | 283.4265 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-HV Winding | 110
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-TF-T133.594LV Winding | GXP | TMK_GXP | DS134 | 33 kV Bus | 8 | TP Branch Report TMK.TF.T1 | TMK-TF-T1 | Transformer | - | LV Winding | 33.594 | 928.0501 | 54 | - | - | - | - | 1107 | 64.4125 | 1062 | 61.7941 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK_GXP | GXPTMK_GXP33.594 | GXPTMK_GXP33.594928.050084426975 |  |  | 928.0501 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-LV Winding | 33.594
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-TF-T133.594Bushings | GXP | TMK_GXP | DS134 | 33 kV Bus | 9 | TP Branch Report TMK.TF.T1 | TMK-TF-T1 | Transformer | TMK-TF-T1 | Bushings | 33.594 | 1200 | 69.8238 | 1200 | 69.8238 | 1200 | 69.8238 | 1440 | 83.7886 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 69.8238 | 69.8238 | 69.8238 | 83.7886 | 83.7886 | - | - | - | - | TMK_GXP69.8238177953626 | GXPTMK_GXP33.5941200 | GXPTMK_GXP33.5941200 | 69.8238 | 1200 | 1200 | DS134 | 33 kV Bus | Transformer-TMK-TF-T1-Bushings | 33.594
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-CBL-T133.594- | GXP | TMK_GXP | DS134 | 33 kV Bus | 10 | TP Branch Report TMK.TF.T1 | TMK-CBL-T1 | Cable | - | - | 33.594 | 1200 | 69.8238 | 1200 | 69.8238 | 1200 | 69.8238 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 69.8238 | 69.8238 | 69.8238 | - | - | - | - | - | - | TMK_GXP69.8238177953626 | GXPTMK_GXP33.5941200 | GXPTMK_GXP33.5941200 | 69.8238 | 1200 | 1200 | DS134 | 33 kV Bus | Cable-TMK-CBL-T1 | 33.594
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-CB125233.594Protection | GXP | TMK_GXP | DS134 | 33 kV Bus | 11 | TP Branch Report TMK.TF.T1 | TMK-CB1252 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 496 | 28.8605 | 1136 | 66.0999 | 3600 | 209.4715 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 72.7331 | 72.7331 | 72.7331 | 72.7331 | 72.7331 | 28.8605 | 209.4715 | 83.7886 | - | TMK_GXP28.8605113554166 | GXPTMK_GXP33.594496 | GXPTMK_GXP33.594496 | 28.8605 | 496 | 496 | DS134 | 33 kV Bus | Circuit Breaker-TMK-CB1252-Protection | 33.594
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-CB-1252-OEL33.594- | GXP | TMK_GXP | DS134 | 33 kV Bus | 12 | TP Branch Report TMK.TF.T1 | TMK-CB-1252-OEL | Other Equipment | - | - | 33.594 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.7886 | 83.7886 | 83.7886 | 83.7886 | 83.7886 | - | - | - | - | TMK_GXP83.7885813544352 | GXPTMK_GXP33.5941440 | GXPTMK_GXP33.5941440 | 83.7886 | 1440 | 1440 | DS134 | 33 kV Bus | Other Equipment-TMK-CB-1252-OEL | 33.594
GXPTMK_GXP33.594T1 | GXPTMK_GXPTMK-BS-033-1252-T133.594- | GXP | TMK_GXP | DS134 | 33 kV Bus | 13 | TP Branch Report TMK.TF.T1 | TMK-BS-033-1252-T1 | Bus | - | - | 33.594 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 72.7331 | 72.7331 | 72.7331 | - | - | - | - | - | - | TMK_GXP72.7331435368361 | GXPTMK_GXP33.5941250 | GXPTMK_GXP33.5941250 | 72.7331 | 1250 | 1250 | DS134 | 33 kV Bus | Bus-TMK-BS-033-1252-T1 | 33.594
GXPTMK_GXP110T2 | GXPTMK_GXPHYENA110- | GXP | TMK_GXP | DS114 | 33 kV Bus | 1 | TP Branch Report TIM.TMK.2 | HYENA | OH Line | - | - | 110 | 422 | 80.4018 | 403 | 76.7818 | 383 | 72.9713 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16000 | - | - | - | - | - | - | - | - | - | - | - | 80.4018 | 76.7818 | 72.9713 | - | - | - | - | - | - | TMK_GXP72.9713005228768 | GXPTMK_GXP110383 | GXPTMK_GXP110383 | 72.9713 | 383 | 383 | DS114 | 33 kV Bus | OH Line-HYENA | 110
GXPTMK_GXP110T2 | GXPTMK_GXPWOLF110- | GXP | TMK_GXP | DS114 | 33 kV Bus | 2 | TP Branch Report TIM.TMK.2 | WOLF | OH Line | - | - | 110 | 531 | 101.1691 | 507 | 96.5965 | 482 | 91.8333 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2000 | - | - | - | - | - | - | - | - | - | - | - | 101.1691 | 96.5965 | 91.8333 | - | - | - | - | - | - | TMK_GXP91.8333338173019 | GXPTMK_GXP110482 | GXPTMK_GXP110482 | 91.8333 | 482 | 482 | DS114 | 33 kV Bus | OH Line-WOLF | 110
GXPTMK_GXP110T2 | GXPTMK_GXPTMK-BS-110-114-T2110- | GXP | TMK_GXP | DS114 | 33 kV Bus | 3 | TP Branch Report TMK.TF.T2 | TMK-BS-110-114-T2 | Bus | - | - | 110 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | 900 | 171.473 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 171.473 | 171.473 | 171.473 | 171.473 | 171.473 | - | - | - | - | TMK_GXP171.473029949319 | GXPTMK_GXP110900 | GXPTMK_GXP110900 | 171.473 | 900 | 900 | DS114 | 33 kV Bus | Bus-TMK-BS-110-114-T2 | 110
GXPTMK_GXP110T2 | GXPTMK_GXPTMK-CB112110Protection | GXP | TMK_GXP | DS114 | 33 kV Bus | 4 | TP Branch Report TMK.TF.T2 | TMK-CB112 | Circuit Breaker | Relay SR760 | Protection | 110 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 2500 | 476.314 | 358 | 68.2082 | - | - | 1200 | 228.6307 | 800 | 152.4205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 476.314 | 476.314 | 476.314 | 476.314 | 476.314 | 68.2082 | 228.6307 | 152.4205 | - | TMK_GXP68.2081608020624 | GXPTMK_GXP110358 | GXPTMK_GXP110358 | 68.2082 | 358 | 358 | DS114 | 33 kV Bus | Circuit Breaker-TMK-CB112-Protection | 110
GXPTMK_GXP110T2 | GXPTMK_GXPTMK-TF-T2110Bushings | GXP | TMK_GXP | DS114 | 33 kV Bus | 5 | TP Branch Report TMK.TF.T2 | TMK-TF-T2 | Transformer | TMK-TF-T2 | Bushings | 110 | 800 | 152.4205 | 800 | 152.4205 | 800 | 152.4205 | 960 | 182.9046 | 960 | 182.9046 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 152.4205 | 152.4205 | 152.4205 | 182.9046 | 182.9046 | - | - | - | - | TMK_GXP152.420471066061 | GXPTMK_GXP110800 | GXPTMK_GXP110800 | 152.4205 | 800 | 800 | DS114 | 33 kV Bus | Transformer-TMK-TF-T2-Bushings | 110
GXPTMK_GXP110T2 | GXPTMK_GXPTMK-TF-T2110TapChanger | GXP | TMK_GXP | DS114 | 33 kV Bus | 6 | TP Branch Report TMK.TF.T2 | TMK-TF-T2 | Transformer | - | TapChanger | 110 | 300 | 57.1577 | 300 | 57.1577 | 300 | 57.1577 | 360 | 68.5892 | 360 | 68.5892 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 57.1577 | 57.1577 | 57.1577 | 68.5892 | 68.5892 | - | - | - | - | TMK_GXP57.1576766497729 | GXPTMK_GXP110300 | GXPTMK_GXP110300 | 57.1577 | 300 | 300 | DS114 | 33 kV Bus | Transformer-TMK-TF-T2-TapChanger | 110
GXPTMK_GXP110T2 | GXPTMK_GXPTMK-TF-T2110HV Winding | GXP | TMK_GXP | DS114 | 33 kV Bus | 7 | TP Branch Report TMK.TF.T2 | TMK-TF-T2 | Transformer | - | HV Winding | 110 | 283.4265 | 54 | - | - | - | - | 332 | 63.2545 | 319 | 60.7777 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK_GXP | GXPTMK_GXP110 | GXPTMK_GXP110283.426495783998 |  |  | 283.4265 | DS114 | 33 kV Bus | Transformer-TMK-TF-T2-HV Winding | 110
GXPTMK_GXP33.594T2 | GXPTMK_GXPTMK-TF-T233.594LV Winding | GXP | TMK_GXP | DS114 | 33 kV Bus | 8 | TP Branch Report TMK.TF.T2 | TMK-TF-T2 | Transformer | - | LV Winding | 33.594 | 928.0501 | 54 | - | - | - | - | 1107 | 64.4125 | 1062 | 61.7941 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK_GXP | GXPTMK_GXP33.594 | GXPTMK_GXP33.594928.050084426975 |  |  | 928.0501 | DS114 | 33 kV Bus | Transformer-TMK-TF-T2-LV Winding | 33.594
GXPTMK_GXP33.594T2 | GXPTMK_GXPTMK-TF-T233.594Bushings | GXP | TMK_GXP | DS114 | 33 kV Bus | 9 | TP Branch Report TMK.TF.T2 | TMK-TF-T2 | Transformer | TMK-TF-T2 | Bushings | 33.594 | 1200 | 69.8238 | 1200 | 69.8238 | 1200 | 69.8238 | 1440 | 83.7886 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 69.8238 | 69.8238 | 69.8238 | 83.7886 | 83.7886 | - | - | - | - | TMK_GXP69.8238177953626 | GXPTMK_GXP33.5941200 | GXPTMK_GXP33.5941200 | 69.8238 | 1200 | 1200 | DS114 | 33 kV Bus | Transformer-TMK-TF-T2-Bushings | 33.594
GXPTMK_GXP33.594T2 | GXPTMK_GXPTMK-CBL-T133.594- | GXP | TMK_GXP | DS114 | 33 kV Bus | 10 | TP Branch Report TMK.TF.T2 | TMK-CBL-T1 | Cable | - | - | 33.594 | 1200 | 69.8238 | 1200 | 69.8238 | 1200 | 69.8238 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 69.8238 | 69.8238 | 69.8238 | - | - | - | - | - | - | TMK_GXP69.8238177953626 | GXPTMK_GXP33.5941200 | GXPTMK_GXP33.5941200 | 69.8238 | 1200 | 1200 | DS114 | 33 kV Bus | Cable-TMK-CBL-T1 | 33.594
GXPTMK_GXP33.594T2 | GXPTMK_GXPTMK-CB123233.594Protection | GXP | TMK_GXP | DS114 | 33 kV Bus | 11 | TP Branch Report TMK.TF.T2 | TMK-CB1232 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 1250 | 72.7331 | 496 | 28.8605 | 1136 | 66.0999 | 3600 | 209.4715 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 72.7331 | 72.7331 | 72.7331 | 72.7331 | 72.7331 | 28.8605 | 209.4715 | 83.7886 | - | TMK_GXP28.8605113554166 | GXPTMK_GXP33.594496 | GXPTMK_GXP33.594496 | 28.8605 | 496 | 496 | DS114 | 33 kV Bus | Circuit Breaker-TMK-CB1232-Protection | 33.594
GXPTMK_GXP33.594T2 | GXPTMK_GXPTMK-CB-1232-OEL33.594- | GXP | TMK_GXP | DS114 | 33 kV Bus | 12 | TP Branch Report TMK.TF.T2 | TMK-CB-1232-OEL | Other Equipment | - | - | 33.594 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | 1440 | 83.7886 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.7886 | 83.7886 | 83.7886 | 83.7886 | 83.7886 | - | - | - | - | TMK_GXP83.7885813544352 | GXPTMK_GXP33.5941440 | GXPTMK_GXP33.5941440 | 83.7886 | 1440 | 1440 | DS114 | 33 kV Bus | Other Equipment-TMK-CB-1232-OEL | 33.594
SubTransmissionCB1192_Clandeboye No.133.594 | SubTransmissionCB1192_Clandeboye No.1TMK-CB119233.594Protection | SubTransmission | CB1192_Clandeboye No.1 | 33 kV Bus | CD1-D1246-T1 | 1 | TP Branch Report TMK.FDR.1192/AEL Protection Database | TMK-CB1192 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 34.9119 | - | CB1192_Clandeboye No.129.6751225630291 | SubTransmissionCB1192_Clandeboye No.133.594510 | SubTransmissionCB1192_Clandeboye No.133.594510 | 29.6751 | 510 | 510 | 33 kV Bus | CD1-D1246-T1 | Circuit Breaker-TMK-CB1192-Protection | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataTMK-CB120233.594Protection | SubTransmission | CB1202_Rangitata | 33 kV Bus | RGA-D1479-T2 | 1 | TP Branch Report TMK.FDR.1202/AEL Protection Database | TMK-CB1202 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 72.7331 | - | CB1202_Rangitata26.8821698512146 | SubTransmissionCB1202_Rangitata33.594462 | SubTransmissionCB1202_Rangitata33.594462 | 26.8822 | 462 | 462 | 33 kV Bus | RGA-D1479-T2 | Circuit Breaker-TMK-CB1202-Protection | 33.594
SubTransmissionCB1212_Temuka No.133.594 | SubTransmissionCB1212_Temuka No.1TMK-CB121233.594Protection | SubTransmission | CB1212_Temuka No.1 | 33 kV Bus | TMK-D816-T1 | 1 | TP Branch Report TMK.FDR.1212/AEL Protection Database | TMK-CB1212 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | CB1212_Temuka No.133.8645516307509 | SubTransmissionCB1212_Temuka No.133.594582 | SubTransmissionCB1212_Temuka No.133.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T1 | Circuit Breaker-TMK-CB1212-Protection | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.3TMK-CB122233.594Protection | SubTransmission | CB1222_Clandeboye No.3 | 33 kV Bus | CD2-D1462-T3 | 1 | TP Branch Report TMK.FDR.1222/AEL Protection Database | TMK-CB1222 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 540 | 31.4207 | 540 | 31.4207 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 31.4207 | 104.7357 | 72.7331 | - | CB1222_Clandeboye No.331.4207180079132 | SubTransmissionCB1222_Clandeboye No.333.594540 | SubTransmissionCB1222_Clandeboye No.333.594540 | 31.4207 | 540 | 540 | 33 kV Bus | CD2-D1462-T3 | Circuit Breaker-TMK-CB1222-Protection | 33.594
SubTransmissionCB1262_Temuka No.233.594 | SubTransmissionCB1262_Temuka No.2TMK-CB126233.594Protection | SubTransmission | CB1262_Temuka No.2 | 33 kV Bus | TMK-D816-T2 | 1 | TP Branch Report TMK.FDR.1262/AEL Protection Database | TMK-CB1262 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | CB1262_Temuka No.233.8645516307509 | SubTransmissionCB1262_Temuka No.233.594582 | SubTransmissionCB1262_Temuka No.233.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T2 | Circuit Breaker-TMK-CB1262-Protection | 33.594
SubTransmissionCB1272_Clandeboye No.233.594 | SubTransmissionCB1272_Clandeboye No.2TMK-CB127233.594Protection | SubTransmission | CB1272_Clandeboye No.2 | 33 kV Bus | CD1-D1246-T2 | 1 | TP Branch Report TMK.FDR.1272/AEL Protection Database | TMK-CB1272 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 72.7331 | - | CB1272_Clandeboye No.229.6751225630291 | SubTransmissionCB1272_Clandeboye No.233.594510 | SubTransmissionCB1272_Clandeboye No.233.594510 | 29.6751 | 510 | 510 | 33 kV Bus | CD1-D1246-T2 | Circuit Breaker-TMK-CB1272-Protection | 33.594
SubTransmissionCB1282_Clandeboye No.433.594 | SubTransmissionCB1282_Clandeboye No.4TMK-CB128233.594Protection | SubTransmission | CB1282_Clandeboye No.4 | 33 kV Bus | CD2-D1462-T4 | 1 | TP Branch Report TMK.FDR.1282/AEL Protection Database | TMK-CB1282 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 660 | 38.4031 | 660 | 38.4031 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 38.4031 | 104.7357 | 34.9119 | - | CB1282_Clandeboye No.434.9119088976813 | SubTransmissionCB1282_Clandeboye No.433.594600 | SubTransmissionCB1282_Clandeboye No.433.594600 | 34.9119 | 600 | 600 | 33 kV Bus | CD2-D1462-T4 | Circuit Breaker-TMK-CB1282-Protection | 33.594
SubTransmissionCB1292_Geraldine33.594 | SubTransmissionCB1292_GeraldineTMK-CB129233.594Protection | SubTransmission | CB1292_Geraldine | 33 kV Bus | GLD-D823-T2 | 1 | TP Branch Report TMK.FDR.1292/AEL Protection Database | TMK-CB1292 | Circuit Breaker | Relay SEL 351S | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 34.9119 | - | CB1292_Geraldine26.8821698512146 | SubTransmissionCB1292_Geraldine33.594462 | SubTransmissionCB1292_Geraldine33.594462 | 26.8822 | 462 | 462 | 33 kV Bus | GLD-D823-T2 | Circuit Breaker-TMK-CB1292-Protection | 33.594
SubTransmissionCB1212_Temuka No.133.594 | SubTransmissionCB1212_Temuka No.1TMK-CB121233.594Protection | SubTransmission | CB1212_Temuka No.1 | 33 kV Bus | TMK-D816-T1 | 1 | TP Branch Report TMK.FDR.1212/AEL Protection Database | TMK-CB1212 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | CB1212_Temuka No.133.8645516307509 | SubTransmissionCB1212_Temuka No.133.594582 | SubTransmissionCB1212_Temuka No.133.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T1 | Circuit Breaker-TMK-CB1212-Protection | 33.594
SubTransmissionCB1212_Temuka No.133.594 | SubTransmissionCB1212_Temuka No.13-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1212_Temuka No.1 | 33 kV Bus | TMK-D816-T1 | 2 | GEMA/Drawing 10407/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 465 | 27.0567 | 465 | 27.0567 | 465 | 27.0567 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 33 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.05 | 2 | 0.6 | 0.9 | 426.3301 | 24.8067 | 27.0567 | 27.0567 | 27.0567 | - | - | - | - | - | 24.8067 | CB1212_Temuka No.124.806664722427 | SubTransmissionCB1212_Temuka No.133.594426.330135 | SubTransmissionCB1212_Temuka No.133.594426.330135 | 24.8067 | 426.3301 | 426.3301 | 33 kV Bus | TMK-D816-T1 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCB1262_Temuka No.233.594 | SubTransmissionCB1262_Temuka No.2TMK-CB126233.594Protection | SubTransmission | CB1262_Temuka No.2 | 33 kV Bus | TMK-D816-T2 | 1 | TP Branch Report TMK.FDR.1262/AEL Protection Database | TMK-CB1262 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | CB1262_Temuka No.233.8645516307509 | SubTransmissionCB1262_Temuka No.233.594582 | SubTransmissionCB1262_Temuka No.233.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T2 | Circuit Breaker-TMK-CB1262-Protection | 33.594
SubTransmissionCB1262_Temuka No.233.594 | SubTransmissionCB1262_Temuka No.23-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1262_Temuka No.2 | 33 kV Bus | TMK-D816-T2 | 2 | GEMA/Drawing 10407/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 465 | 27.0567 | 465 | 27.0567 | 465 | 27.0567 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 35.1 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.05 | 2 | 0.6 | 0.9 | 426.3301 | 24.8067 | 27.0567 | 27.0567 | 27.0567 | - | - | - | - | - | 24.8067 | CB1262_Temuka No.224.806664722427 | SubTransmissionCB1262_Temuka No.233.594426.330135 | SubTransmissionCB1262_Temuka No.233.594426.330135 | 24.8067 | 426.3301 | 426.3301 | 33 kV Bus | TMK-D816-T2 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionTMK33.594 | SubTransmissionTMKTMK-CB121233.594Protection | SubTransmission | TMK | 33 kV Bus | TMK-D816-T1 | 1 | TP Branch Report TMK.FDR.1212/AEL Protection Database | TMK-CB1212 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | TMK33.8645516307509 | SubTransmissionTMK33.594582 | SubTransmissionTMK33.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T1 | Circuit Breaker-TMK-CB1212-Protection | 33.594
SubTransmissionTMK33.594 | SubTransmissionTMK3-1c 400 mm² Al XLPE33.594- | SubTransmission | TMK | 33 kV Bus | TMK-D816-T1 | 2 | GEMA/Drawing 10407/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 465 | 27.0567 | 465 | 27.0567 | 465 | 27.0567 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 33 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.05 | 2 | 0.6 | 0.9 | 426.3301 | 24.8067 | 27.0567 | 27.0567 | 27.0567 | - | - | - | - | - | 24.8067 | TMK24.806664722427 | SubTransmissionTMK33.594426.330135 | SubTransmissionTMK33.594426.330135 | 24.8067 | 426.3301 | 426.3301 | 33 kV Bus | TMK-D816-T1 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionTMK33.594 | SubTransmissionTMKTMK-CB126233.594Protection | SubTransmission | TMK | 33 kV Bus | TMK-D816-T2 | 1 | TP Branch Report TMK.FDR.1262/AEL Protection Database | TMK-CB1262 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 582 | 33.8646 | 582 | 33.8646 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 33.8646 | 104.7357 | 72.7331 | - | TMK33.8645516307509 | SubTransmissionTMK33.594582 | SubTransmissionTMK33.594582 | 33.8646 | 582 | 582 | 33 kV Bus | TMK-D816-T2 | Circuit Breaker-TMK-CB1262-Protection | 33.594
SubTransmissionTMK33.594 | SubTransmissionTMK3-1c 400 mm² Al XLPE33.594- | SubTransmission | TMK | 33 kV Bus | TMK-D816-T2 | 2 | GEMA/Drawing 10407/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 465 | 27.0567 | 465 | 27.0567 | 465 | 27.0567 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 35.1 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.05 | 2 | 0.6 | 0.9 | 426.3301 | 24.8067 | 27.0567 | 27.0567 | 27.0567 | - | - | - | - | - | 24.8067 | TMK24.806664722427 | SubTransmissionTMK33.594426.330135 | SubTransmissionTMK33.594426.330135 | 24.8067 | 426.3301 | 426.3301 | 33 kV Bus | TMK-D816-T2 | Cable-3-1c 400 mm² Al XLPE | 33.594
ZoneSubstationTMK33.594 | ZoneSubstationTMKD816-T133.594HV Winding | ZoneSubstation | TMK | TMK-D816-T1 | 11 kV Bus | 1 | AEL Transformers Database | D816-T1 | Transformer | - | HV Winding | 33.594 | 429.6528 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK | ZoneSubstationTMK33.594 | ZoneSubstationTMK33.594429.65281686434 |  |  | 429.6528 | TMK-D816-T1 | 11 kV Bus | Transformer-D816-T1-HV Winding | 33.594
ZoneSubstationTMK11 | ZoneSubstationTMKD816-T111LV Winding | ZoneSubstation | TMK | TMK-D816-T1 | 11 kV Bus | 2 | AEL Transformers Database | D816-T1 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK | ZoneSubstationTMK11 | ZoneSubstationTMK111312.1597027037 |  |  | 1312.1597 | TMK-D816-T1 | 11 kV Bus | Transformer-D816-T1-LV Winding | 11
ZoneSubstationTMK11 | ZoneSubstationTMK6-1c 500 mm² Cu XLPE11- | ZoneSubstation | TMK | TMK-D816-T1 | 11 kV Bus | 3 | GEMA/Drawing 10407 | 6-1c 500 mm² Cu XLPE | Cable | - | - | 11 | 1192 | 22.7107 | 1192 | 22.7107 | 1192 | 22.7107 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 41.7 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.06 | 2 | 0 | 0.85 | 1041.987 | 19.8525 | 22.7107 | 22.7107 | 22.7107 | - | - | - | - | - | 19.8525 | TMK19.8525194047073 | ZoneSubstationTMK111041.9870384 | ZoneSubstationTMK111041.9870384 | 19.8525 | 1041.987 | 1041.987 | TMK-D816-T1 | 11 kV Bus | Cable-6-1c 500 mm² Cu XLPE | 11
ZoneSubstationTMK11 | ZoneSubstationTMKTMK-CB411Protection | ZoneSubstation | TMK | TMK-D816-T1 | 11 kV Bus | 4 | GEMA/AEL Protection Database | TMK-CB4 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1080 | 20.5768 | 1080 | 20.5768 | - | - | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.5768 | - | 22.8631 | - | TMK20.5767635939183 | ZoneSubstationTMK111080 | ZoneSubstationTMK111080 | 20.5768 | 1080 | 1080 | TMK-D816-T1 | 11 kV Bus | Circuit Breaker-TMK-CB4-Protection | 11
ZoneSubstationTMK33.594 | ZoneSubstationTMKD816-T233.594HV Winding | ZoneSubstation | TMK | TMK-D816-T2 | 11 kV Bus | 1 | AEL Transformers Database | D816-T2 | Transformer | - | HV Winding | 33.594 | 429.6528 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK | ZoneSubstationTMK33.594 | ZoneSubstationTMK33.594429.65281686434 |  |  | 429.6528 | TMK-D816-T2 | 11 kV Bus | Transformer-D816-T2-HV Winding | 33.594
ZoneSubstationTMK11 | ZoneSubstationTMKD816-T211LV Winding | ZoneSubstation | TMK | TMK-D816-T2 | 11 kV Bus | 2 | AEL Transformers Database | D816-T2 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TMK | ZoneSubstationTMK11 | ZoneSubstationTMK111312.1597027037 |  |  | 1312.1597 | TMK-D816-T2 | 11 kV Bus | Transformer-D816-T2-LV Winding | 11
ZoneSubstationTMK11 | ZoneSubstationTMK6-1c 500 mm² Cu XLPE11- | ZoneSubstation | TMK | TMK-D816-T2 | 11 kV Bus | 3 | GEMA/Drawing 10407 | 6-1c 500 mm² Cu XLPE | Cable | - | - | 11 | 1192 | 22.7107 | 1192 | 22.7107 | 1192 | 22.7107 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 46.5 | 0.9 | 0.99 | 18 | 0.98 | 1.2 | 1.06 | 2 | 0 | 0.85 | 1041.987 | 19.8525 | 22.7107 | 22.7107 | 22.7107 | - | - | - | - | - | 19.8525 | TMK19.8525194047073 | ZoneSubstationTMK111041.9870384 | ZoneSubstationTMK111041.9870384 | 19.8525 | 1041.987 | 1041.987 | TMK-D816-T2 | 11 kV Bus | Cable-6-1c 500 mm² Cu XLPE | 11
ZoneSubstationTMK11 | ZoneSubstationTMKTMK-CB611Protection | ZoneSubstation | TMK | TMK-D816-T2 | 11 kV Bus | 4 | GEMA/AEL Protection Database | TMK-CB6 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1080 | 20.5768 | 1080 | 20.5768 | - | - | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 20.5768 | - | 22.8631 | - | TMK20.5767635939183 | ZoneSubstationTMK111080 | ZoneSubstationTMK111080 | 20.5768 | 1080 | 1080 | TMK-D816-T2 | 11 kV Bus | Circuit Breaker-TMK-CB6-Protection | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestTMK-CB111Protection | DistributionFeeder | CB1_Temuka West | 11 kV Bus | T200 | 1 | GEMA/AEL Protection Database | TMK-CB1 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB1_Temuka West7.65912867106957 | DistributionFeederCB1_Temuka West11402 | DistributionFeederCB1_Temuka West11402 | 7.6591 | 402 | 402 | 11 kV Bus | T200 | Circuit Breaker-TMK-CB1-Protection | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka West1-3c 300 mm² Al XLPE HD11- | DistributionFeeder | CB1_Temuka West | 11 kV Bus | T200 | 2 | GEMA/Drawing 13902-02 | 1-3c 300 mm² Al XLPE HD | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 13.5 | 1 | 0.9817 | 18 | 0.9672 | 1.2 | 1.0066 | 5 | 0 | 0.57 | 259.3186 | 4.9407 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 4.9407 | CB1_Temuka West4.94068256500933 | DistributionFeederCB1_Temuka West11259.318582626239 | DistributionFeederCB1_Temuka West11259.318582626239 | 4.9407 | 259.3186 | 259.3186 | 11 kV Bus | T200 | Cable-1-3c 300 mm² Al XLPE HD | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka West2-3c 150 mm² Al PILC11- | DistributionFeeder | CB1_Temuka West | 11 kV Bus | T200 | 3 | GEMA/Drawing 3952-02 & 8831-02 | 2-3c 150 mm² Al PILC | Cable | - | - | 11 | 530 | 10.0979 | 530 | 10.0979 | 530 | 10.0979 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 36.9 | 1 | 0.9817 | 18 | 0.9672 | 1.2 | 1.0066 | 2 | 0.45 | 0.90741 | 459.6521 | 8.7575 | 10.0979 | 10.0979 | 10.0979 | - | - | - | - | - | 8.7575 | CB1_Temuka West8.75754827237039 | DistributionFeederCB1_Temuka West11459.652077499472 | DistributionFeederCB1_Temuka West11459.652077499472 | 8.7575 | 459.6521 | 459.6521 | 11 kV Bus | T200 | Cable-2-3c 150 mm² Al PILC | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestT20011- | DistributionFeeder | CB1_Temuka West | 12 kV Bus | T201 | 4 | GEMA | T200 | ABS | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | CB1_Temuka West11.4315353299546 | DistributionFeederCB1_Temuka West11600 | DistributionFeederCB1_Temuka West11600 | 11.4315 | 600 | 600 | 12 kV Bus | T201 | ABS-T200 | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestCHAFER11- | DistributionFeeder | CB1_Temuka West | T200 | T201 | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.4 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB1_Temuka West7.3943903990836 | DistributionFeederCB1_Temuka West11388.104844309464 | DistributionFeederCB1_Temuka West11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | T200 | T201 | OH Line-CHAFER | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestT20111- | DistributionFeeder | CB1_Temuka West | T200 | T201 | 6 | GEMA | T201 | ABS | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | CB1_Temuka West11.4315353299546 | DistributionFeederCB1_Temuka West11600 | DistributionFeederCB1_Temuka West11600 | 11.4315 | 600 | 600 | T200 | T201 | ABS-T201 | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestCHAFER11- | DistributionFeeder | CB1_Temuka West | T201 | T208 | 7 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1695.9 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB1_Temuka West7.3943903990836 | DistributionFeederCB1_Temuka West11388.104844309464 | DistributionFeederCB1_Temuka West11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | T201 | T208 | OH Line-CHAFER | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestT20811- | DistributionFeeder | CB1_Temuka West | T201 | T208 | 8 | GEMA | T208 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB1_Temuka West7.62102355330306 | DistributionFeederCB1_Temuka West11400 | DistributionFeederCB1_Temuka West11400 | 7.621 | 400 | 400 | T201 | T208 | ABS-T208 | 11
DistributionFeederCB1_Temuka West11 | DistributionFeederCB1_Temuka WestCHAFER11- | DistributionFeeder | CB1_Temuka West | 11 kV Bus | Pole 27077 | 9 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 604.3 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB1_Temuka West7.3943903990836 | DistributionFeederCB1_Temuka West11388.104844309464 | DistributionFeederCB1_Temuka West11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | 11 kV Bus | Pole 27077 | OH Line-CHAFER | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordTMK-CB211Protection | DistributionFeeder | CB2_Milford | 11 kV Bus | T500 | 1 | GEMA/AEL Protection Database | TMK-CB2 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB2_Milford7.65912867106957 | DistributionFeederCB2_Milford11402 | DistributionFeederCB2_Milford11402 | 7.6591 | 402 | 402 | 11 kV Bus | T500 | Circuit Breaker-TMK-CB2-Protection | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_Milford1-3c 300 mm² Al XLPE HD11- | DistributionFeeder | CB2_Milford | 11 kV Bus | T500 | 2 | GEMA/Drawing 13903-02 | 1-3c 300 mm² Al XLPE HD | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 7.9 | 1 | 0.9817 | 18 | 0.9672 | 1.2 | 1.0066 | 5 | 0 | 0.57 | 259.3186 | 4.9407 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 4.9407 | CB2_Milford4.94068256500933 | DistributionFeederCB2_Milford11259.318582626239 | DistributionFeederCB2_Milford11259.318582626239 | 4.9407 | 259.3186 | 259.3186 | 11 kV Bus | T500 | Cable-1-3c 300 mm² Al XLPE HD | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_Milford1-3c 150 mm² Al PILC11- | DistributionFeeder | CB2_Milford | 11 kV Bus | T500 | 3 | GEMA/Drawing 1109-02 | 1-3c 150 mm² Al PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 198.7 | 0.95 | 0.9817 | 18 | 0.9672 | 1.2 | 1.0061 | 4 | 0 | 0.6297 | 159.408 | 3.0371 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 3.0371 | CB2_Milford3.03713056262812 | DistributionFeederCB2_Milford11159.408013445217 | DistributionFeederCB2_Milford11159.408013445217 | 3.0371 | 159.408 | 159.408 | 11 kV Bus | T500 | Cable-1-3c 150 mm² Al PILC | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_Milford3-1c 185 mm² Al XLPE11- | DistributionFeeder | CB2_Milford | 11 kV Bus | T500 | 4 | GEMA/Drawing 10449 | 3-1c 185 mm² Al XLPE | Cable | - | - | 11 | 326 | 6.2111 | 326 | 6.2111 | 326 | 6.2111 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 8.7 | 1 | 0.9776 | 18 | 0.9788 | 1.2 | 0.99854 | 1 | 0 | 1 | 311.4853 | 5.9346 | 6.2111 | 6.2111 | 6.2111 | - | - | - | - | - | 5.9346 | CB2_Milford5.93459133321985 | DistributionFeederCB2_Milford11311.485263978628 | DistributionFeederCB2_Milford11311.485263978628 | 5.9346 | 311.4853 | 311.4853 | 11 kV Bus | T500 | Cable-3-1c 185 mm² Al XLPE | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordT50011- | DistributionFeeder | CB2_Milford | T500 | T500 | 5 | GEMA | T500 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB2_Milford7.62102355330306 | DistributionFeederCB2_Milford11400 | DistributionFeederCB2_Milford11400 | 7.621 | 400 | 400 | T500 | T500 | ABS-T500 | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordCHAFER11- | DistributionFeeder | CB2_Milford | T500 | T120 | 6 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 388.1 | 7.3943 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5 | - | - | - | - | - | - | - | - | - | - | - | 7.3943 | - | 7.3944 | - | - | - | - | - | - | CB2_Milford7.39429810259229 | DistributionFeederCB2_Milford11388.1 | DistributionFeederCB2_Milford11388.1 | 7.3943 | 388.1 | 388.1 | T500 | T120 | OH Line-CHAFER | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordDOG11- | DistributionFeeder | CB2_Milford | T500 | T120 | 7 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 257 | 4.8965 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 59.7 | - | - | - | - | - | - | - | - | - | - | - | 4.8965 | - | 4.8938 | - | - | - | - | - | - | CB2_Milford4.89381213609487 | DistributionFeederCB2_Milford11256.858523103439 | DistributionFeederCB2_Milford11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | T500 | T120 | OH Line-DOG | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordT12011- | DistributionFeeder | CB2_Milford | T500 | T120 | 8 | GEMA | T120 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB2_Milford7.62102355330306 | DistributionFeederCB2_Milford11400 | DistributionFeederCB2_Milford11400 | 7.621 | 400 | 400 | T500 | T120 | ABS-T120 | 11
DistributionFeederCB2_Milford11 | DistributionFeederCB2_MilfordDOG11- | DistributionFeeder | CB2_Milford | T500 | Pole 04185 | 9 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11 | 257 | 4.8965 | - | - | 256.8585 | 4.8938 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1028.9 | - | - | - | - | - | - | - | - | - | - | - | 4.8965 | - | 4.8938 | - | - | - | - | - | - | CB2_Milford4.89381213609487 | DistributionFeederCB2_Milford11256.858523103439 | DistributionFeederCB2_Milford11256.858523103439 | 4.8938 | 256.8585 | 256.8585 | T500 | Pole 04185 | OH Line-DOG | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterTMK-CB311Protection | DistributionFeeder | CB3_Winchester | 11 kV Bus | G100 | 1 | GEMA/AEL Protection Database | TMK-CB3 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB3_Winchester7.65912867106957 | DistributionFeederCB3_Winchester11402 | DistributionFeederCB3_Winchester11402 | 7.6591 | 402 | 402 | 11 kV Bus | G100 | Circuit Breaker-TMK-CB3-Protection | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_Winchester1-3c 300 mm² Al XLPE11- | DistributionFeeder | CB3_Winchester | 11 kV Bus | G100 | 2 | GEMA/Drawing 10449 | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 118.2 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.8 | 0.95 | 434.2929 | 8.2744 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 8.2744 | CB3_Winchester8.27439066877955 | DistributionFeederCB3_Winchester11434.29288 | DistributionFeederCB3_Winchester11434.29288 | 8.2744 | 434.2929 | 434.2929 | 11 kV Bus | G100 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterG10011- | DistributionFeeder | CB3_Winchester | 11 kV Bus | G100 | 3 | GEMA | G100 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB3_Winchester7.62102355330306 | DistributionFeederCB3_Winchester11400 | DistributionFeederCB3_Winchester11400 | 7.621 | 400 | 400 | 11 kV Bus | G100 | ABS-G100 | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterCHAFER11- | DistributionFeeder | CB3_Winchester | G100 | Pole 47049 | 4 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 33.4 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB3_Winchester7.3943903990836 | DistributionFeederCB3_Winchester11388.104844309464 | DistributionFeederCB3_Winchester11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | G100 | Pole 47049 | OH Line-CHAFER | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterJAGUAR11- | DistributionFeeder | CB3_Winchester | Pole 47049 | T548 | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11 | 523.1348 | 9.9671 | - | - | 386.9283 | 7.372 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 577.1 | - | - | - | - | - | - | - | - | - | - | - | 9.9671 | - | 7.372 | - | - | - | - | - | - | CB3_Winchester7.37197367771845 | DistributionFeederCB3_Winchester11386.92827157178 | DistributionFeederCB3_Winchester11386.92827157178 | 7.372 | 386.9283 | 386.9283 | Pole 47049 | T548 | OH Line-JAGUAR | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterT54611- | DistributionFeeder | CB3_Winchester | Pole 47049 | T548 | 6 | GEMA | T546 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | CB3_Winchester5.7157676649773 | DistributionFeederCB3_Winchester11300 | DistributionFeederCB3_Winchester11300 | 5.7158 | 300 | 300 | Pole 47049 | T548 | Link-T546 | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_Winchester1-3c 300 mm² Al XLPE11- | DistributionFeeder | CB3_Winchester | Pole 47049 | T548 | 7 | GEMA/General Cables | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 391.5 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.8 | 0.95 | 434.2929 | 8.2744 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 8.2744 | CB3_Winchester8.27439066877955 | DistributionFeederCB3_Winchester11434.29288 | DistributionFeederCB3_Winchester11434.29288 | 8.2744 | 434.2929 | 434.2929 | Pole 47049 | T548 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederCB3_Winchester11 | DistributionFeederCB3_WinchesterT54811- | DistributionFeeder | CB3_Winchester | Pole 47049 | T548 | 8 | GEMA | T548 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | CB3_Winchester5.7157676649773 | DistributionFeederCB3_Winchester11300 | DistributionFeederCB3_Winchester11300 | 5.7158 | 300 | 300 | Pole 47049 | T548 | Link-T548 | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataTMK-CB711Protection | DistributionFeeder | CB7_Rangitata | 11 kV Bus | T400 | 1 | GEMA/AEL Protection Database | TMK-CB7 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB7_Rangitata7.65912867106957 | DistributionFeederCB7_Rangitata11402 | DistributionFeederCB7_Rangitata11402 | 7.6591 | 402 | 402 | 11 kV Bus | T400 | Circuit Breaker-TMK-CB7-Protection | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_Rangitata1-3c 300 mm² Al XLPE11- | DistributionFeeder | CB7_Rangitata | 11 kV Bus | T400 | 2 | GEMA/Drawing 10449 | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 118.2 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.8 | 0.95 | 434.2929 | 8.2744 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 8.2744 | CB7_Rangitata8.27439066877955 | DistributionFeederCB7_Rangitata11434.29288 | DistributionFeederCB7_Rangitata11434.29288 | 8.2744 | 434.2929 | 434.2929 | 11 kV Bus | T400 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataT40011- | DistributionFeeder | CB7_Rangitata | 11 kV Bus | T400 | 3 | GEMA | T400 | ABS | - | - | 11 | 400 | 7.621 | 400 | 7.621 | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.621 | 7.621 | 7.621 | - | - | - | - | - | - | CB7_Rangitata7.62102355330306 | DistributionFeederCB7_Rangitata11400 | DistributionFeederCB7_Rangitata11400 | 7.621 | 400 | 400 | 11 kV Bus | T400 | ABS-T400 | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataCHAFER11- | DistributionFeeder | CB7_Rangitata | T400 | Pole 47048 | 4 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 35.8 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB7_Rangitata7.3943903990836 | DistributionFeederCB7_Rangitata11388.104844309464 | DistributionFeederCB7_Rangitata11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | T400 | Pole 47048 | OH Line-CHAFER | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataJAGUAR11- | DistributionFeeder | CB7_Rangitata | Pole 47048 | T549 | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 11 | 523.1348 | 9.9671 | - | - | 386.9283 | 7.372 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 778.3 | - | - | - | - | - | - | - | - | - | - | - | 9.9671 | - | 7.372 | - | - | - | - | - | - | CB7_Rangitata7.37197367771845 | DistributionFeederCB7_Rangitata11386.92827157178 | DistributionFeederCB7_Rangitata11386.92827157178 | 7.372 | 386.9283 | 386.9283 | Pole 47048 | T549 | OH Line-JAGUAR | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataT54711- | DistributionFeeder | CB7_Rangitata | Pole 47048 | T549 | 6 | GEMA | T547 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | CB7_Rangitata5.7157676649773 | DistributionFeederCB7_Rangitata11300 | DistributionFeederCB7_Rangitata11300 | 5.7158 | 300 | 300 | Pole 47048 | T549 | Link-T547 | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_Rangitata1-3c 300 mm² Al XLPE11- | DistributionFeeder | CB7_Rangitata | Pole 47048 | T549 | 7 | GEMA/General Cables | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 390.8 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.8 | 0.95 | 434.2929 | 8.2744 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 8.2744 | CB7_Rangitata8.27439066877955 | DistributionFeederCB7_Rangitata11434.29288 | DistributionFeederCB7_Rangitata11434.29288 | 8.2744 | 434.2929 | 434.2929 | Pole 47048 | T549 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederCB7_Rangitata11 | DistributionFeederCB7_RangitataT54911- | DistributionFeeder | CB7_Rangitata | Pole 47048 | T549 | 8 | GEMA | T549 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | CB7_Rangitata5.7157676649773 | DistributionFeederCB7_Rangitata11300 | DistributionFeederCB7_Rangitata11300 | 5.7158 | 300 | 300 | Pole 47048 | T549 | Link-T549 | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka EastTMK-CB811Protection | DistributionFeeder | CB8_Temuka East | 11 kV Bus | T101 | 1 | GEMA/AEL Protection Database | TMK-CB8 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB8_Temuka East7.65912867106957 | DistributionFeederCB8_Temuka East11402 | DistributionFeederCB8_Temuka East11402 | 7.6591 | 402 | 402 | 11 kV Bus | T101 | Circuit Breaker-TMK-CB8-Protection | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka East1-3c 300 mm² Al PILC11- | DistributionFeeder | CB8_Temuka East | 11 kV Bus | T101 | 2 | GEMA/Drawing 10449 | 1-3c 300 mm² Al PILC | Cable | - | - | 11 | 390 | 7.4305 | 390 | 7.4305 | 390 | 7.4305 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 149.9 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 3 | 0.6 | 0.86 | 322.1182 | 6.1372 | 7.4305 | 7.4305 | 7.4305 | - | - | - | - | - | 6.1372 | CB8_Temuka East6.13717521076661 | DistributionFeederCB8_Temuka East11322.11816 | DistributionFeederCB8_Temuka East11322.11816 | 6.1372 | 322.1182 | 322.1182 | 11 kV Bus | T101 | Cable-1-3c 300 mm² Al PILC | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka EastT10111- | DistributionFeeder | CB8_Temuka East | 11 kV Bus | T101 | 3 | GEMA | T101 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CB8_Temuka East | DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka East11 |  |  |  | 11 kV Bus | T101 | Link-T101 | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka East37/14 Cu11- | DistributionFeeder | CB8_Temuka East | T101 | T102 | 4 | GEMA/AEL OH Amp Calc. | 37/14 Cu | OH Line | - | - | 11 | 486 | 9.2595 | 399.5 | 7.6115 | 363 | 6.9161 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 31.6 | - | - | - | - | - | - | - | - | - | - | - | 9.2595 | 7.6115 | 6.9161 | - | - | - | - | - | - | CB8_Temuka East6.91607887462253 | DistributionFeederCB8_Temuka East11363 | DistributionFeederCB8_Temuka East11363 | 6.9161 | 363 | 363 | T101 | T102 | OH Line-37/14 Cu | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka EastT10211- | DistributionFeeder | CB8_Temuka East | T101 | T102 | 5 | GEMA | T102 | ABS | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | CB8_Temuka East11.4315353299546 | DistributionFeederCB8_Temuka East11600 | DistributionFeederCB8_Temuka East11600 | 11.4315 | 600 | 600 | T101 | T102 | ABS-T102 | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka East37/14 Cu11- | DistributionFeeder | CB8_Temuka East | T102 | Pole 36752 | 6 | GEMA/AEL OH Amp Calc. | 37/14 Cu | OH Line | - | - | 11 | 486 | 9.2595 | 399.5 | 7.6115 | 363 | 6.9161 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.2 | - | - | - | - | - | - | - | - | - | - | - | 9.2595 | 7.6115 | 6.9161 | - | - | - | - | - | - | CB8_Temuka East6.91607887462253 | DistributionFeederCB8_Temuka East11363 | DistributionFeederCB8_Temuka East11363 | 6.9161 | 363 | 363 | T102 | Pole 36752 | OH Line-37/14 Cu | 11
DistributionFeederCB8_Temuka East11 | DistributionFeederCB8_Temuka East7/0.136 Cu11- | DistributionFeeder | CB8_Temuka East | T102 | Pole 36752 | 7 | GEMA/AEL OH Amp Calc. | 7/0.136 Cu | OH Line | - | - | 11 | 320 | 6.0968 | 263.5 | 5.0203 | 241 | 4.5917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 399 | - | - | - | - | - | - | - | - | - | - | - | 6.0968 | 5.0203 | 4.5917 | - | - | - | - | - | - | CB8_Temuka East4.59166669086509 | DistributionFeederCB8_Temuka East11241 | DistributionFeederCB8_Temuka East11241 | 4.5917 | 241 | 241 | T102 | Pole 36752 | OH Line-7/0.136 Cu | 11
DistributionFeederCB9_Waitohi11 | DistributionFeederCB9_WaitohiTMK-CB911Protection | DistributionFeeder | CB9_Waitohi | 11 kV Bus | T300 | 1 | GEMA/AEL Protection Database | TMK-CB9 | Circuit Breaker | Relay SEL 351S | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 402 | 7.6591 | 402 | 7.6591 | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 7.6591 | - | 11.4315 | - | CB9_Waitohi7.65912867106957 | DistributionFeederCB9_Waitohi11402 | DistributionFeederCB9_Waitohi11402 | 7.6591 | 402 | 402 | 11 kV Bus | T300 | Circuit Breaker-TMK-CB9-Protection | 11
DistributionFeederCB9_Waitohi11 | DistributionFeederCB9_Waitohi1-3c 240 mm² Al PILC11- | DistributionFeeder | CB9_Waitohi | 11 kV Bus | T300 | 2 | GEMA/Drawing 10449 | 1-3c 240 mm² Al PILC | Cable | - | - | 11 | 345 | 6.5731 | 345 | 6.5731 | 345 | 6.5731 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 57.4 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.45 | 0.9 | 298.2042 | 5.6816 | 6.5731 | 6.5731 | 6.5731 | - | - | - | - | - | 5.6816 | CB9_Waitohi5.68155307973474 | DistributionFeederCB9_Waitohi11298.2042 | DistributionFeederCB9_Waitohi11298.2042 | 5.6816 | 298.2042 | 298.2042 | 11 kV Bus | T300 | Cable-1-3c 240 mm² Al PILC | 11
DistributionFeederCB9_Waitohi11 | DistributionFeederCB9_WaitohiT30011- | DistributionFeeder | CB9_Waitohi | 11 kV Bus | T300 | 3 | GEMA | T300 | ABS | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | CB9_Waitohi11.4315353299546 | DistributionFeederCB9_Waitohi11600 | DistributionFeederCB9_Waitohi11600 | 11.4315 | 600 | 600 | 11 kV Bus | T300 | ABS-T300 | 11
DistributionFeederCB9_Waitohi11 | DistributionFeederCB9_Waitohi19/16 Cu11- | DistributionFeeder | CB9_Waitohi | T300 | Pole 36779 | 4 | GEMA/AEL OH Amp Calc. | 19/16 Cu | OH Line | - | - | 11 | 233 | 4.4392 | 195.5 | 3.7248 | 176 | 3.3533 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.3 | - | - | - | - | - | - | - | - | - | - | - | 4.4392 | 3.7248 | 3.3533 | - | - | - | - | - | - | CB9_Waitohi3.35325036345335 | DistributionFeederCB9_Waitohi11176 | DistributionFeederCB9_Waitohi11176 | 3.3533 | 176 | 176 | T300 | Pole 36779 | OH Line-19/16 Cu | 11
DistributionFeederCB9_Waitohi11 | DistributionFeederCB9_WaitohiCHAFER11- | DistributionFeeder | CB9_Waitohi | Pole 36779 | Pole 36784 | 5 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 375.3 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | CB9_Waitohi7.3943903990836 | DistributionFeederCB9_Waitohi11388.104844309464 | DistributionFeederCB9_Waitohi11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | Pole 36779 | Pole 36784 | OH Line-CHAFER | 11
SubTransmissionCB1292_Geraldine33.594 | SubTransmissionCB1292_GeraldineTMK-CB129233.594Protection | SubTransmission | CB1292_Geraldine | 33 kV Bus | G217 | 1 | TP Branch Report TMK.FDR.1292/AEL Protection Database | TMK-CB1292 | Circuit Breaker | Relay SEL 351S | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 34.9119 | - | CB1292_Geraldine26.8821698512146 | SubTransmissionCB1292_Geraldine33.594462 | SubTransmissionCB1292_Geraldine33.594462 | 26.8822 | 462 | 462 | 33 kV Bus | G217 | Circuit Breaker-TMK-CB1292-Protection | 33.594
SubTransmissionCB1292_Geraldine33.594 | SubTransmissionCB1292_Geraldine3-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1292_Geraldine | 33 kV Bus | G217 | 2 | GEMA/Drawing 12189/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 521 | 30.3152 | 521 | 30.3152 | 521 | 30.3152 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 43.8 | 1.2 | 0.95 | 18 | 0.98 | 1.2 | 1 | 4 | 0.3 | 0.72 | 349.2367 | 20.3209 | 30.3152 | 30.3152 | 30.3152 | - | - | - | - | - | 20.3209 | CB1292_Geraldine20.3208675872751 | SubTransmissionCB1292_Geraldine33.594349.23672 | SubTransmissionCB1292_Geraldine33.594349.23672 | 20.3209 | 349.2367 | 349.2367 | 33 kV Bus | G217 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCB1292_Geraldine33.594 | SubTransmissionCB1292_GeraldineT55933.594- | SubTransmission | CB1292_Geraldine | 33 kV Bus | G217 | 3 | GEMA | T559 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | CB1292_Geraldine46.5492118635751 | SubTransmissionCB1292_Geraldine33.594800 | SubTransmissionCB1292_Geraldine33.594800 | 46.5492 | 800 | 800 | 33 kV Bus | G217 | ABS-T559 | 33.594
SubTransmissionCB1292_Geraldine33.594 | SubTransmissionCB1292_GeraldineDOG33.594- | SubTransmission | CB1292_Geraldine | 33 kV Bus | G217 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16513.2 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1292_Geraldine14.9457022636337 | SubTransmissionCB1292_Geraldine33.594256.858523103439 | SubTransmissionCB1292_Geraldine33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | 33 kV Bus | G217 | OH Line-DOG | 33.594
SubTransmissionGLD33.594 | SubTransmissionGLDTMK-CB129233.594Protection | SubTransmission | GLD | 33 kV Bus | G217 | 1 | TP Branch Report TMK.FDR.1292/AEL Protection Database | TMK-CB1292 | Circuit Breaker | Relay SEL 351S | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 34.9119 | - | GLD26.8821698512146 | SubTransmissionGLD33.594462 | SubTransmissionGLD33.594462 | 26.8822 | 462 | 462 | 33 kV Bus | G217 | Circuit Breaker-TMK-CB1292-Protection | 33.594
SubTransmissionGLD33.594 | SubTransmissionGLD3-1c 400 mm² Al XLPE33.594- | SubTransmission | GLD | 33 kV Bus | G217 | 2 | GEMA/Drawing 12189/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 521 | 30.3152 | 521 | 30.3152 | 521 | 30.3152 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 43.8 | 1.2 | 0.95 | 18 | 0.98 | 1.2 | 1 | 4 | 0.3 | 0.72 | 349.2367 | 20.3209 | 30.3152 | 30.3152 | 30.3152 | - | - | - | - | - | 20.3209 | GLD20.3208675872751 | SubTransmissionGLD33.594349.23672 | SubTransmissionGLD33.594349.23672 | 20.3209 | 349.2367 | 349.2367 | 33 kV Bus | G217 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionGLD33.594 | SubTransmissionGLDT55933.594- | SubTransmission | GLD | 33 kV Bus | G217 | 3 | GEMA | T559 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | GLD46.5492118635751 | SubTransmissionGLD33.594800 | SubTransmissionGLD33.594800 | 46.5492 | 800 | 800 | 33 kV Bus | G217 | ABS-T559 | 33.594
SubTransmissionGLD33.594 | SubTransmissionGLDDOG33.594- | SubTransmission | GLD | 33 kV Bus | G217 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 16513.2 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | GLD14.9457022636337 | SubTransmissionGLD33.594256.858523103439 | SubTransmissionGLD33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | 33 kV Bus | G217 | OH Line-DOG | 33.594
ZoneSubstationGLD33.594 | ZoneSubstationGLDG21733.594- | ZoneSubstation | GLD | G217 | G222 | 1 | GEMA | G217 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GLD | ZoneSubstationGLD33.594 | ZoneSubstationGLD33.594 |  |  |  | G217 | G222 | ABS-G217 | 33.594
ZoneSubstationGLD33.594 | ZoneSubstationGLDGX2733.594- | ZoneSubstation | GLD | G217 | G222 | 2 | GEMA | GX27 | ABS | - | - | 33.594 | 400 | 23.2746 | 400 | 23.2746 | 400 | 23.2746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.2746 | 23.2746 | 23.2746 | - | - | - | - | - | - | GLD23.2746059317875 | ZoneSubstationGLD33.594400 | ZoneSubstationGLD33.594400 | 23.2746 | 400 | 400 | G217 | G222 | ABS-GX27 | 33.594
ZoneSubstationGLD33.594 | ZoneSubstationGLDG22033.594- | ZoneSubstation | GLD | G217 | G222 | 3 | GEMA | G220 | ABS | - | - | 33.594 | 400 | 23.2746 | 400 | 23.2746 | 400 | 23.2746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.2746 | 23.2746 | 23.2746 | - | - | - | - | - | - | GLD23.2746059317875 | ZoneSubstationGLD33.594400 | ZoneSubstationGLD33.594400 | 23.2746 | 400 | 400 | G217 | G222 | ABS-G220 | 33.594
ZoneSubstationGLD33.594 | ZoneSubstationGLDGLD-G25933.594Protection | ZoneSubstation | GLD | G217 | G222 | 4 | GEMA/AEL Protection Database | GLD-G259 | Circuit Breaker | Relay SEL 351R | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 350 | 20.3653 | 220 | 12.801 | - | - | 500 | 29.0933 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 20.3653 | - | 29.0933 | - | GLD20.3652801903141 | ZoneSubstationGLD33.594350 | ZoneSubstationGLD33.594220 | 20.3653 | 350 | 220 | G217 | G222 | Circuit Breaker-GLD-G259-Protection | 33.594
ZoneSubstationGLD33.594 | ZoneSubstationGLDD823-T233.594HV Winding | ZoneSubstation | GLD | G217 | G222 | 5 | AEL Transformers Database | D823-T2 | Transformer | - | HV Winding | 33.594 | 257.7917 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GLD | ZoneSubstationGLD33.594 | ZoneSubstationGLD33.594257.791690118604 |  |  | 257.7917 | G217 | G222 | Transformer-D823-T2-HV Winding | 33.594
ZoneSubstationGLD11.055 | ZoneSubstationGLDD823-T211.055LV Winding | ZoneSubstation | GLD | G217 | G222 | 6 | AEL Transformers Database | D823-T2 | Transformer | - | LV Winding | 11.055 | 783.3789 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GLD | ZoneSubstationGLD11.055 | ZoneSubstationGLD11.055783.378926987281 |  |  | 783.3789 | G217 | G222 | Transformer-D823-T2-LV Winding | 11.055
ZoneSubstationGLD11.055 | ZoneSubstationGLDGLD-G26011.055Protection | ZoneSubstation | GLD | G217 | G222 | 7 | GEMA/AEL Protection Database | GLD-G260 | Circuit Breaker | Relay Nulec U-Series | Protection | 11.055 | 630 | 12.0631 | 630 | 12.0631 | 630 | 12.0631 | - | - | - | - | 948 | 18.1521 | - | - | 2000 | 38.2956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0631 | 12.0631 | 12.0631 | - | - | 18.1521 | 38.2956 | - | - | GLD12.0631276569346 | ZoneSubstationGLD11.055630 | ZoneSubstationGLD11.055630 | 12.0631 | 630 | 630 | G217 | G222 | Circuit Breaker-GLD-G260-Protection | 11.055
ZoneSubstationGLD11.055 | ZoneSubstationGLDG22211.055- | ZoneSubstation | GLD | G217 | G222 | 8 | GEMA | G222 | ABS | - | - | 11.055 | 800 | 15.3183 | 800 | 15.3183 | 800 | 15.3183 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.3183 | 15.3183 | 15.3183 | - | - | - | - | - | - | GLD15.3182573421391 | ZoneSubstationGLD11.055800 | ZoneSubstationGLD11.055800 | 15.3183 | 800 | 800 | G217 | G222 | ABS-G222 | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyG19311.055- | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 1 | GEMA | G193 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G194_Speechly | DistributionFeederG194_Speechly11.055 | DistributionFeederG194_Speechly11.055 |  |  |  | G222 | Pole 03224 | Link-G193 | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyGLD-G19411.055Protection | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 2 | GEMA/AEL Protection Database | GLD-G194 | Circuit Breaker | Relay Nulec U-Series | Protection | 11.055 | 630 | 12.0631 | 630 | 12.0631 | 630 | 12.0631 | - | - | - | - | 350 | 6.7017 | 300 | 5.7443 | - | - | 2000 | 38.2956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0631 | 12.0631 | 12.0631 | - | - | 6.7017 | - | 38.2956 | - | G194_Speechly6.70173758718588 | DistributionFeederG194_Speechly11.055350 | DistributionFeederG194_Speechly11.055300 | 6.7017 | 350 | 300 | G222 | Pole 03224 | Circuit Breaker-GLD-G194-Protection | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyG19511.055- | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 3 | GEMA | G195 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G194_Speechly | DistributionFeederG194_Speechly11.055 | DistributionFeederG194_Speechly11.055 |  |  |  | G222 | Pole 03224 | Link-G195 | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_Speechly70mm211.055 | DistributionFeeder | G194_Speechly | G195 | G318 | 4 | GEMA/AEL OH Amp Calc. | 70mm2 | OH Line |  |  | 11.055 |  | - |  | - | 247 | 4.7295 |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | - | - | 4.7295 | - | - | - | - | - | - | G194_Speechly4.72951195438546 | DistributionFeederG194_Speechly11.055247 | DistributionFeederG194_Speechly11.055247 | 4.7295 | 247 | 247 | G195 | G318 | OH Line - 70mm2 - | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyG31811.055- | DistributionFeeder | G194_Speechly | G195 | Pole 53271 | 5 | GEMA | G318 | ABS | - | - | 11.055 | 400 | 7.6591 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | 7.6591 | - | - | - | - | - | - | - | - | G194_Speechly7.65912867106957 | DistributionFeederG194_Speechly11.055400 | DistributionFeederG194_Speechly11.055400 | 7.6591 | 400 | 400 | G195 | Pole 53271 | ABS - G318 | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyMINK11.055- | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 4 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11.055 | 250.5823 | 4.7981 | - | - | 188.6266 | 3.6118 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 13.8 | - | - | - | - | - | - | - | - | - | - | - | 4.7981 | - | 3.6118 | - | - | - | - | - | - | G194_Speechly3.61178863871597 | DistributionFeederG194_Speechly11.055188.626607220145 | DistributionFeederG194_Speechly11.055188.626607220145 | 3.6118 | 188.6266 | 188.6266 | G222 | Pole 03224 | OH Line-MINK | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyG27311.055- | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 5 | GEMA | G273 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G194_Speechly | DistributionFeederG194_Speechly11.055 | DistributionFeederG194_Speechly11.055 |  |  |  | G222 | Pole 03224 | Link-G273 | 11.055
DistributionFeederG194_Speechly11.055 | DistributionFeederG194_SpeechlyMINK11.055- | DistributionFeeder | G194_Speechly | G222 | Pole 03224 | 6 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11.055 | 250.5823 | 4.7981 | - | - | 188.6266 | 3.6118 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 750 | - | - | - | - | - | - | - | - | - | - | - | 4.7981 | - | 3.6118 | - | - | - | - | - | - | G194_Speechly3.61178863871597 | DistributionFeederG194_Speechly11.055188.626607220145 | DistributionFeederG194_Speechly11.055188.626607220145 | 3.6118 | 188.6266 | 188.6266 | G222 | Pole 03224 | OH Line-MINK | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine TownshipG19011.055- | DistributionFeeder | G191_Geraldine Township | G222 | G191 | 1 | GEMA | G190 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G191_Geraldine Township | DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine Township11.055 |  |  |  | G222 | G191 | Link-G190 | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine TownshipGLD-G19111.055Protection | DistributionFeeder | G191_Geraldine Township | G190 | G192 | 2 | GEMA/AEL Protection Database | GLD-G191 | Circuit Breaker | Relay Nulec U-Series | Protection | 11.055 | 630 | 12.0631 | 630 | 12.0631 | 630 | 12.0631 | - | - | - | - | 350 | 6.7017 | 300 | 5.7443 | - | - | 2000 | 38.2956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0631 | 12.0631 | 12.0631 | - | - | 6.7017 | - | 38.2956 | - | G191_Geraldine Township6.70173758718588 | DistributionFeederG191_Geraldine Township11.055350 | DistributionFeederG191_Geraldine Township11.055300 | 6.7017 | 350 | 300 | G190 | G192 | Circuit Breaker-GLD-G191-Protection | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine TownshipG19211.055- | DistributionFeeder | G191_Geraldine Township | G191 | G320 | 3 | GEMA | G192 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G191_Geraldine Township | DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine Township11.055 |  |  |  | G191 | G320 | Link-G192 | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine Township7/0.136 Cu11.055- | DistributionFeeder | G191_Geraldine Township | G192 | G320 | 4 | GEMA/AEL OH Amp Calc. | 7/0.136 Cu | OH Line | - | - | 11.055 | 320 | 6.1273 | 467.5 | 8.9516 | 241 | 4.6146 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 29.4 | - | - | - | - | - | - | - | - | - | - | - | 6.1273 | 8.9516 | 4.6146 | - | - | - | - | - | - | G191_Geraldine Township4.61462502431942 | DistributionFeederG191_Geraldine Township11.055241 | DistributionFeederG191_Geraldine Township11.055241 | 4.6146 | 241 | 241 | G192 | G320 | OH Line-7/0.136 Cu | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine TownshipG32011.055- | DistributionFeeder | G191_Geraldine Township | G192 | G278 | 5 | GEMA | G320 | Switch | - | - | 11.055 | 400 | 7.6591 |  | - |  | - |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | 7.6591 | - | - | - | - | - | - | - | - | G191_Geraldine Township7.65912867106957 | DistributionFeederG191_Geraldine Township11.055400 | DistributionFeederG191_Geraldine Township11.055400 | 7.6591 | 400 | 400 | G192 | G278 | Switch - G320 | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine Township70mm211.055- | DistributionFeeder | G191_Geraldine Township | G320 | G278 | 6 | GEMA/AEL OH Amp Calc. | 70mm2 | OH Line | - | - | 11.055 |  | - |  | - | 247 | 4.7295 |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | - | - | 4.7295 | - | - | - | - | - | - | G191_Geraldine Township4.72951195438546 | DistributionFeederG191_Geraldine Township11.055247 | DistributionFeederG191_Geraldine Township11.055247 | 4.7295 | 247 | 247 | G320 | G278 | OH Line - 70mm2 | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine TownshipG27811.055- | DistributionFeeder | G191_Geraldine Township | G278 | Pole 26842 | 7 | GEMA | G278 | Link | - | - | 11.055 | 300 | 5.7443 | 300 | 5.7443 | 300 | 5.7443 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7443 | 5.7443 | 5.7443 | - | - | - | - | - | - | G191_Geraldine Township5.74434650330218 | DistributionFeederG191_Geraldine Township11.055300 | DistributionFeederG191_Geraldine Township11.055300 | 5.7443 | 300 | 300 | G278 | Pole 26842 | Link-G278 | 11.055
DistributionFeederG191_Geraldine Township11.055 | DistributionFeederG191_Geraldine Township7/0.136 Cu11.055- | DistributionFeeder | G191_Geraldine Township | G278 | Pole 26842 | 8 | GEMA/AEL OH Amp Calc. | 7/0.136 Cu | OH Line | - | - | 11.055 | 320 | 6.1273 | 263.5 | 5.0455 | 241 | 4.6146 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 127.1 | - | - | - | - | - | - | - | - | - | - | - | 6.1273 | 5.0455 | 4.6146 | - | - | - | - | - | - | G191_Geraldine Township4.61462502431942 | DistributionFeederG191_Geraldine Township11.055241 | DistributionFeederG191_Geraldine Township11.055241 | 4.6146 | 241 | 241 | G278 | Pole 26842 | OH Line-7/0.136 Cu | 11.055
DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_WoodburyG15711.055- | DistributionFeeder | G156_Woodbury | G222 | G277 | 1 | GEMA | G157 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G156_Woodbury | DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_Woodbury11.055 |  |  |  | G222 | G277 | Link-G157 | 11.055
DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_WoodburyGLD-G15611.055Protection | DistributionFeeder | G156_Woodbury | G222 | G277 | 2 | GEMA/AEL Protection Database | GLD-G156 | Circuit Breaker | Relay Nulec U-Series | Protection | 11.055 | 630 | 12.0631 | 630 | 12.0631 | 630 | 12.0631 | - | - | - | - | 350 | 6.7017 | 300 | 5.7443 | - | - | 2000 | 38.2956 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0631 | 12.0631 | 12.0631 | - | - | 6.7017 | - | 38.2956 | - | G156_Woodbury6.70173758718588 | DistributionFeederG156_Woodbury11.055350 | DistributionFeederG156_Woodbury11.055300 | 6.7017 | 350 | 300 | G222 | G277 | Circuit Breaker-GLD-G156-Protection | 11.055
DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_WoodburyG15811.055- | DistributionFeeder | G156_Woodbury | G222 | G277 | 3 | GEMA | G158 | Link | - | - | 11.055 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | G156_Woodbury | DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_Woodbury11.055 |  |  |  | G222 | G277 | Link-G158 | 11.055
DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_Woodbury7/0.136 Cu11.055- | DistributionFeeder | G156_Woodbury | G222 | G277 | 4 | GEMA/AEL OH Amp Calc. | 7/0.136 Cu | OH Line | - | - | 11.055 | 320 | 6.1273 | - | - | 241 | 4.6146 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 26.4 | - | - | - | - | - | - | - | - | - | - | - | 6.1273 | - | 4.6146 | - | - | - | - | - | - | G156_Woodbury4.61462502431942 | DistributionFeederG156_Woodbury11.055241 | DistributionFeederG156_Woodbury11.055241 | 4.6146 | 241 | 241 | G222 | G277 | OH Line-7/0.136 Cu | 11.055
DistributionFeederG156_Woodbury11.055 | DistributionFeederG156_WoodburyG27711.055- | DistributionFeeder | G156_Woodbury | G222 | G277 | 5 | GEMA | G277 | Link | - | - | 11.055 | 300 | 5.7443 | 300 | 5.7443 | 300 | 5.7443 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7443 | 5.7443 | 5.7443 | - | - | - | - | - | - | G156_Woodbury5.74434650330218 | DistributionFeederG156_Woodbury11.055300 | DistributionFeederG156_Woodbury11.055300 | 5.7443 | 300 | 300 | G222 | G277 | Link-G277 | 11.055
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1TMK-CB127233.594Protection | SubTransmission | RGA_T1 | 33 kV Bus | Pole 02001 | 1 | TP Branch Report TMK.FDR.1272/AEL Protection Database | TMK-CB1272 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 72.7331 | - | RGA_T129.6751225630291 | SubTransmissionRGA_T133.594510 | SubTransmissionRGA_T133.594510 | 29.6751 | 510 | 510 | 33 kV Bus | Pole 02001 | Circuit Breaker-TMK-CB1272-Protection | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T16-1c 300 mm² XLPE33.594- | SubTransmission | RGA_T1 | 33 kV Bus | Pole 02001 | 2 | GEMA/Drawing 10408 | 6-1c 300 mm² XLPE | Cable | - | - | 33.594 | 828 | 48.1784 | 828 | 48.1784 | 828 | 48.1784 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 231 | 1.1 | 0.97 | 18.5 | 0.98 | 1.2 | 1 | 4 | 0.4 | 0.75 | 590.3226 | 34.3488 | 48.1784 | 48.1784 | 48.1784 | - | - | - | - | - | 34.3488 | RGA_T134.3488147190706 | SubTransmissionRGA_T133.594590.3226 | SubTransmissionRGA_T133.594590.3226 | 34.3488 | 590.3226 | 590.3226 | 33 kV Bus | Pole 02001 | Cable-6-1c 300 mm² XLPE | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1JAGUAR33.594- | SubTransmission | RGA_T1 | Pole 02001 | Pole 02049 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5804 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | RGA_T133.9106986639602 | SubTransmissionRGA_T133.594582.793088112333 | SubTransmissionRGA_T133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02001 | Pole 02049 | OH Line-JAGUAR | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1WOLF33.594- | SubTransmission | RGA_T1 | Pole 02049 | Pole 02052 | 4 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 572.8673 | 33.3332 | - | - | 496.0602 | 28.864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 404 | - | - | - | - | - | - | - | - | - | - | - | 33.3332 | - | 28.864 | - | - | - | - | - | - | RGA_T128.8640140783565 | SubTransmissionRGA_T133.594496.060198191114 | SubTransmissionRGA_T133.594496.060198191114 | 28.864 | 496.0602 | 496.0602 | Pole 02049 | Pole 02052 | OH Line-WOLF | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T110 MW Limit33.594- | SubTransmission | RGA_T1 | Pole 02052 | CB1416 | 5 | AEL-Fonterra Agreement/Tesla study | 10 MW Limit | AEL-Fonterra Contractual | - | - | 33.594 | 171.8611 | 10 | 171.8611 | 10 | 171.8611 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10 | 10 | 10 | - | - | - | - | - | - | RGA_T110 | SubTransmissionRGA_T133.594171.861126745736 | SubTransmissionRGA_T133.594171.861126745736 | 10 | 171.8611 | 171.8611 | Pole 02052 | CB1416 | AEL-Fonterra Contractual-10 MW Limit | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1CHAFER33.594- | SubTransmission | RGA_T1 | Pole 02052 | CB1416 | 6 | GEMA/AEL OH Amp Calc/12387 | CHAFER | OH Line | - | - | 33.594 | 674.4536 | 39.2441 | - | - | 583.8801 | 33.974 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 61 | - | - | - | - | - | - | - | - | - | - | - | 39.2441 | - | 33.974 | - | - | - | - | - | - | RGA_T133.9739500994475 | SubTransmissionRGA_T133.594583.880134409445 | SubTransmissionRGA_T133.594583.880134409445 | 33.974 | 583.8801 | 583.8801 | Pole 02052 | CB1416 | OH Line-CHAFER | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1141433.594- | SubTransmission | RGA_T1 | Pole 02052 | CB1416 | 7 | GEMA | 1414 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | SubTransmissionRGA_T133.594 | SubTransmissionRGA_T133.594 |  |  |  | Pole 02052 | CB1416 | ABS-1414 | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1CNL-RGA-CB141233.594Protection | SubTransmission | RGA_T1 | Pole 02052 | CB1416 | 8 | GEMA/AEL Protection Database | CNL-RGA-CB1412 | Circuit Breaker | Relay SEL 751A | Protection | 33.594 | 2000 | 116.373 | 2000 | 116.373 | 2000 | 116.373 | - | - | - | - | 423 | 24.6129 | - | - | - | - | 300 | 17.456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116.373 | 116.373 | 116.373 | - | - | 24.6129 | - | 17.456 | - | RGA_T117.4559544488407 | SubTransmissionRGA_T133.594300 | SubTransmissionRGA_T133.594300 | 17.456 | 300 | 300 | Pole 02052 | CB1416 | Circuit Breaker-CNL-RGA-CB1412-Protection | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1141633.594- | SubTransmission | RGA_T1 | Pole 02052 | CB1416 | 9 | GEMA | 1416 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | SubTransmissionRGA_T133.594 | SubTransmissionRGA_T133.594 |  |  |  | Pole 02052 | CB1416 | ABS-1416 | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1JAGUAR33.594- | SubTransmission | RGA_T1 | CB1416 | ABS1516 | 10 | GEMA/AEL OH Amp Calc/12387 | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 13936.4 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | RGA_T133.9106986639602 | SubTransmissionRGA_T133.594582.793088112333 | SubTransmissionRGA_T133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | CB1416 | ABS1516 | OH Line-JAGUAR | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1151633.594- | SubTransmission | RGA_T1 | CB1416 | ABS1516 | 11 | GEMA | 1516 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | RGA_T146.5492118635751 | SubTransmissionRGA_T133.594800 | SubTransmissionRGA_T133.594800 | 46.5492 | 800 | 800 | CB1416 | ABS1516 | ABS-1516 | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1CHAFER33.594- | SubTransmission | RGA_T1 | ABS1516 | ABS1524 | 12 | GEMA/AEL OH Amp Calc/12387 | CHAFER | OH Line | - | - | 33.594 | 674.4536 | 39.2441 | - | - | 583.8801 | 33.974 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 87.6 | - | - | - | - | - | - | - | - | - | - | - | 39.2441 | - | 33.974 | - | - | - | - | - | - | RGA_T133.9739500994475 | SubTransmissionRGA_T133.594583.880134409445 | SubTransmissionRGA_T133.594583.880134409445 | 33.974 | 583.8801 | 583.8801 | ABS1516 | ABS1524 | OH Line-CHAFER | 33.594
SubTransmissionRGA_T133.594 | SubTransmissionRGA_T1DOG33.594- | SubTransmission | RGA_T1 | ABS1516 | ABS1524 | 13 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 439.0512 | 25.5469 | - | - | 380.7203 | 22.1528 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25.5469 | - | 22.1528 | - | - | - | - | - | - | RGA_T122.1527858300496 | SubTransmissionRGA_T133.594380.72027333093 | SubTransmissionRGA_T133.594380.72027333093 | 22.1528 | 380.7203 | 380.7203 | ABS1516 | ABS1524 | OH Line-DOG | 33.594
ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T1152433.594- | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 1 | GEMA | 1524 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T133.594 |  |  |  | ABS1524 | CB35 | ABS-1524 | 33.594
ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T1RGA_T1-CB152233.594Protection | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 2 | GEMA/AEL Protection Database | RGA_T1-CB1522 | Circuit Breaker | Relay SEL 387E-311C-1 | Protection | 33.594 | - | - | - | - | - | - | - | - | - | - | 402 | 23.391 | 402 | 23.391 | - | - | 300 | 17.456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.391 | - | 17.456 | - | RGA_T117.4559544488407 | ZoneSubstationRGA_T133.594300 | ZoneSubstationRGA_T133.594300 | 17.456 | 300 | 300 | ABS1524 | CB35 | Circuit Breaker-RGA_T1-CB1522-Protection | 33.594
ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T1152633.594- | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 3 | GEMA | 1526 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T133.594 |  |  |  | ABS1524 | CB35 | ABS-1526 | 33.594
ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T1D1479-T133.594HV Winding | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 4 | AEL Transformers Database | D1479-T1 | Transformer | - | HV Winding | 33.594 | 257.7917 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | ZoneSubstationRGA_T133.594 | ZoneSubstationRGA_T133.594257.791690118604 |  |  | 257.7917 | ABS1524 | CB35 | Transformer-D1479-T1-HV Winding | 33.594
ZoneSubstationRGA_T111.22 | ZoneSubstationRGA_T1D1479-T111.22LV Winding | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 5 | AEL Transformers Database | D1479-T1 | Transformer | - | LV Winding | 11.22 | 771.8586 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | ZoneSubstationRGA_T111.22 | ZoneSubstationRGA_T111.22771.858648649232 |  |  | 771.8586 | ABS1524 | CB35 | Transformer-D1479-T1-LV Winding | 11.22
ZoneSubstationRGA_T111.22 | ZoneSubstationRGA_T13-1c 630 mm² Cu XLPE11.22- | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 6 | GEMA/General Cables/12608 | 3-1c 630 mm² Cu XLPE | Cable | - | - | 11.22 | 810 | 15.7412 | 810 | 15.7412 | 810 | 15.7412 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 11.4 | 0.4 | 1 | 18 | 0.98 | 1.2 | 1 | 1 | 0 | 1 | 793.8 | 15.4264 | 15.7412 | 15.7412 | 15.7412 | - | - | - | - | - | 15.4264 | RGA_T115.4263996663605 | ZoneSubstationRGA_T111.22793.8 | ZoneSubstationRGA_T111.22793.8 | 15.4264 | 793.8 | 793.8 | ABS1524 | CB35 | Cable-3-1c 630 mm² Cu XLPE | 11.22
ZoneSubstationRGA_T111.22 | ZoneSubstationRGA_T1RGA_T1-CB3511.22Protection | ZoneSubstation | RGA_T1 | ABS1524 | CB35 | 7 | GEMA/AEL Protection Database | RGA_T1-CB35 | Circuit Breaker | Relay SEL 387E | Protection | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 1048 | 20.3664 | 1048 | 20.3664 | - | - | 800 | 15.5469 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 20.3664 | - | 15.5469 | - | RGA_T115.5468880487382 | ZoneSubstationRGA_T111.22800 | ZoneSubstationRGA_T111.22800 | 15.5469 | 800 | 800 | ABS1524 | CB35 | Circuit Breaker-RGA_T1-CB35-Protection | 11.22
DistributionFeederCB2_Arundel11.22 | DistributionFeederCB2_ArundelRGA_T1-CB211.22Protection | DistributionFeeder | CB2_Arundel | CB2 | T595 | 1 | GEMA/AEL Protection Database | RGA_T1-CB2 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 300 | 5.8301 | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 5.8301 | - | 7.7734 | - | CB2_Arundel5.83008301827684 | DistributionFeederCB2_Arundel11.22300 | DistributionFeederCB2_Arundel11.22300 | 5.8301 | 300 | 300 | CB2 | T595 | Circuit Breaker-RGA_T1-CB2-Protection | 11.22
DistributionFeederCB2_Arundel11.22 | DistributionFeederCB2_Arundel1-3c 185 mm² XLPE11.22- | DistributionFeeder | CB2_Arundel | CB2 | T595 | 2 | GEMA/General Cables/12608 | 1-3c 185 mm² XLPE | Cable | - | - | 11.22 | 367 | 7.1321 | 367 | 7.1321 | 367 | 7.1321 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 137.9 | 0.9 | 0.99 | 18 | 0.98 | 1.5 | 0.95 | 4 | 0.45 | 0.8 | 270.6082 | 5.2589 | 7.1321 | 7.1321 | 7.1321 | - | - | - | - | - | 5.2589 | CB2_Arundel5.25889392715045 | DistributionFeederCB2_Arundel11.22270.608184 | DistributionFeederCB2_Arundel11.22270.608184 | 5.2589 | 270.6082 | 270.6082 | CB2 | T595 | Cable-1-3c 185 mm² XLPE | 11.22
DistributionFeederCB2_Arundel11.22 | DistributionFeederCB2_ArundelT59511.22- | DistributionFeeder | CB2_Arundel | CB2 | T595 | 3 | GEMA | T595 | Link | - | - | 11.22 | 300 | 5.8301 | 300 | 5.8301 | 300 | 5.8301 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.8301 | 5.8301 | 5.8301 | - | - | - | - | - | - | CB2_Arundel5.83008301827684 | DistributionFeederCB2_Arundel11.22300 | DistributionFeederCB2_Arundel11.22300 | 5.8301 | 300 | 300 | CB2 | T595 | Link-T595 | 11.22
DistributionFeederCB2_Arundel11.22 | DistributionFeederCB2_ArundelDOG11.22- | DistributionFeeder | CB2_Arundel | T595 | Pole 05969 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1137.3 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB2_Arundel4.99168837881677 | DistributionFeederCB2_Arundel11.22256.858523103439 | DistributionFeederCB2_Arundel11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | T595 | Pole 05969 | OH Line-DOG | 11.22
DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan RoadRGA_T1-CB311.22Protection | DistributionFeeder | CB3_Mahan Road | CB3 | TX43 | 1 | GEMA/AEL Protection Database | RGA_T1-CB3 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | 300 | 5.8301 | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | 5.8301 | - | 7.7734 | - | CB3_Mahan Road5.83008301827684 | DistributionFeederCB3_Mahan Road11.22300 | DistributionFeederCB3_Mahan Road11.22300 | 5.8301 | 300 | 300 | CB3 | TX43 | Circuit Breaker-RGA_T1-CB3-Protection | 11.22
DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan Road1-3c 185 mm² XLPE11.22- | DistributionFeeder | CB3_Mahan Road | CB3 | TX43 | 2 | GEMA/General Cables/12608 | 1-3c 185 mm² XLPE | Cable | - | - | 11.22 | 367 | 7.1321 | 367 | 7.1321 | 367 | 7.1321 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 42.9 | 0.9 | 0.99 | 18 | 0.98 | 1.5 | 0.95 | 4 | 0.45 | 0.8 | 270.6082 | 5.2589 | 7.1321 | 7.1321 | 7.1321 | - | - | - | - | - | 5.2589 | CB3_Mahan Road5.25889392715045 | DistributionFeederCB3_Mahan Road11.22270.608184 | DistributionFeederCB3_Mahan Road11.22270.608184 | 5.2589 | 270.6082 | 270.6082 | CB3 | TX43 | Cable-1-3c 185 mm² XLPE | 11.22
DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan Road1-3c 95 mm² XLPE11.22- | DistributionFeeder | CB3_Mahan Road | CB3 | TX43 | 3 | GEMA/General Cables/12608 | 1-3c 95 mm² XLPE | Cable | - | - | 11.22 | 219 | 4.256 | 219 | 4.256 | 219 | 4.256 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 42.9 | 1.2 | 0.97 | 18 | 0.98 | 1.2 | 1 | 1 | 0 | 1 | 208.1814 | 4.0457 | 4.256 | 4.256 | 4.256 | - | - | - | - | - | 4.0457 | CB3_Mahan Road4.04571614953699 | DistributionFeederCB3_Mahan Road11.22208.1814 | DistributionFeederCB3_Mahan Road11.22208.1814 | 4.0457 | 208.1814 | 208.1814 | CB3 | TX43 | Cable-1-3c 95 mm² XLPE | 11.22
DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan RoadTX4311.22- | DistributionFeeder | CB3_Mahan Road | CB3 | TX43 | 4 | GEMA | TX43 | ABS | - | - | 11.22 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CB3_Mahan Road | DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan Road11.22 |  |  |  | CB3 | TX43 | ABS-TX43 | 11.22
DistributionFeederCB3_Mahan Road11.22 | DistributionFeederCB3_Mahan RoadDOG11.22- | DistributionFeeder | CB3_Mahan Road | TX43 | Pole 48705 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 267.9 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB3_Mahan Road4.99168837881677 | DistributionFeederCB3_Mahan Road11.22256.858523103439 | DistributionFeederCB3_Mahan Road11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | TX43 | Pole 48705 | OH Line-DOG | 11.22
DistributionFeederCB4_Main South Road11.22 | DistributionFeederCB4_Main South RoadRGA_T1-CB411.22Protection | DistributionFeeder | CB4_Main South Road | CB4 | T703 | 1 | GEMA/AEL Protection Database | RGA_T1-CB4 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 630 | 12.2432 | 630 | 12.2432 | 630 | 12.2432 | - | - | - | - | #N/A | #N/A | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.2432 | 12.2432 | 12.2432 | - | - | #N/A | - | 7.7734 | - | CB4_Main South Road | DistributionFeederCB4_Main South Road11.22 | #N/A |  |  | #N/A | CB4 | T703 | Circuit Breaker-RGA_T1-CB4-Protection | 11.22
DistributionFeederCB4_Main South Road11.22 | DistributionFeederCB4_Main South Road1-3c 185 mm² XLPE11.22- | DistributionFeeder | CB4_Main South Road | CB4 | T703 | 2 | GEMA/General Cables/12608 | 1-3c 185 mm² XLPE | Cable | - | - | 11.22 | 367 | 7.1321 | 367 | 7.1321 | 367 | 7.1321 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 44.6 | 0.9 | 0.99 | 18 | 0.98 | 1.5 | 0.95 | 4 | 0.45 | 0.8 | 270.6082 | 5.2589 | 7.1321 | 7.1321 | 7.1321 | - | - | - | - | - | 5.2589 | CB4_Main South Road5.25889392715045 | DistributionFeederCB4_Main South Road11.22270.608184 | DistributionFeederCB4_Main South Road11.22270.608184 | 5.2589 | 270.6082 | 270.6082 | CB4 | T703 | Cable-1-3c 185 mm² XLPE | 11.22
DistributionFeederCB4_Main South Road11.22 | DistributionFeederCB4_Main South RoadDOG11.22- | DistributionFeeder | CB4_Main South Road | CB4 | T703 | 3 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 157.1 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB4_Main South Road4.99168837881677 | DistributionFeederCB4_Main South Road11.22256.858523103439 | DistributionFeederCB4_Main South Road11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | CB4 | T703 | OH Line-DOG | 11.22
DistributionFeederCB4_Main South Road11.22 | DistributionFeederCB4_Main South RoadT70311.22- | DistributionFeeder | CB4_Main South Road | CB4 | T703 | 4 | GEMA | T703 | ABS | - | - | 11.22 | 600 | 11.6602 | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6602 | 11.6602 | 11.6602 | - | - | - | - | - | - | CB4_Main South Road11.6601660365537 | DistributionFeederCB4_Main South Road11.22600 | DistributionFeederCB4_Main South Road11.22600 | 11.6602 | 600 | 600 | CB4 | T703 | ABS-T703 | 11.22
DistributionFeederCB4_Main South Road11.22 | DistributionFeederCB4_Main South RoadDOG11.22- | DistributionFeeder | CB4_Main South Road | T703 | Pole 00335 | 5 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 70.22 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB4_Main South Road4.99168837881677 | DistributionFeederCB4_Main South Road11.22256.858523103439 | DistributionFeederCB4_Main South Road11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | T703 | Pole 00335 | OH Line-DOG | 11.22
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataTMK-CB120233.594Protection | SubTransmission | CB1202_Rangitata | 33 kV Bus | T557 | 1 | TP Branch Report TMK.FDR.1202/AEL Protection Database | TMK-CB1202 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 72.7331 | - | CB1202_Rangitata26.8821698512146 | SubTransmissionCB1202_Rangitata33.594462 | SubTransmissionCB1202_Rangitata33.594462 | 26.8822 | 462 | 462 | 33 kV Bus | T557 | Circuit Breaker-TMK-CB1202-Protection | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_Rangitata3-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1202_Rangitata | 33 kV Bus | T557 | 2 | GEMA/Drawing 12189/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 521 | 30.3152 | 521 | 30.3152 | 521 | 30.3152 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 50.2 | 1.2 | 0.95 | 18 | 0.98 | 1.2 | 1 | 4 | 0.3 | 0.72 | 349.2367 | 20.3209 | 30.3152 | 30.3152 | 30.3152 | - | - | - | - | - | 20.3209 | CB1202_Rangitata20.3208675872751 | SubTransmissionCB1202_Rangitata33.594349.23672 | SubTransmissionCB1202_Rangitata33.594349.23672 | 20.3209 | 349.2367 | 349.2367 | 33 kV Bus | T557 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataT55733.594- | SubTransmission | CB1202_Rangitata | 33 kV Bus | T557 | 3 | GEMA | T557 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | CB1202_Rangitata46.5492118635751 | SubTransmissionCB1202_Rangitata33.594800 | SubTransmissionCB1202_Rangitata33.594800 | 46.5492 | 800 | 800 | 33 kV Bus | T557 | ABS-T557 | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataDOG33.594- | SubTransmission | CB1202_Rangitata | T557 | G127 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2493.6 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1202_Rangitata14.9457022636337 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | T557 | G127 | OH Line-DOG | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataIODINE33.594- | SubTransmission | CB1202_Rangitata | T557 | G127 | 5 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33.594 | 368.604 | 21.4478 | - | - | 275.3865 | 16.0238 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1247.7 | - | - | - | - | - | - | - | - | - | - | - | 21.4478 | - | 16.0238 | - | - | - | - | - | - | CB1202_Rangitata16.0237799627034 | SubTransmissionCB1202_Rangitata33.594275.386487911596 | SubTransmissionCB1202_Rangitata33.594275.386487911596 | 16.0238 | 275.3865 | 275.3865 | T557 | G127 | OH Line-IODINE | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataDOG33.594- | SubTransmission | CB1202_Rangitata | T557 | G127 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 904.8 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1202_Rangitata14.9457022636337 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | T557 | G127 | OH Line-DOG | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_Rangitata1-3c 95 mm² Al XLPE33.594- | SubTransmission | CB1202_Rangitata | T557 | G127 | 7 | GEMA/General Cables | 1-3c 95 mm² Al XLPE | Cable | - | - | 33.594 | 218 | 12.6847 | 218 | 12.6847 | 218 | 12.6847 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 1202.5 | 1.25 | 0.97 | 18 | 0.98 | 1.2 | 1 | 1 | 0 | 1 | 207.2308 | 12.058 | 12.6847 | 12.6847 | 12.6847 | - | - | - | - | - | 12.058 | CB1202_Rangitata12.0580380173227 | SubTransmissionCB1202_Rangitata33.594207.2308 | SubTransmissionCB1202_Rangitata33.594207.2308 | 12.058 | 207.2308 | 207.2308 | T557 | G127 | Cable-1-3c 95 mm² Al XLPE | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataG12733.594- | SubTransmission | CB1202_Rangitata | T557 | G127 | 8 | GEMA | G127 | Link | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CB1202_Rangitata | SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_Rangitata33.594 |  |  |  | T557 | G127 | Link-G127 | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataDOG33.594- | SubTransmission | CB1202_Rangitata | G127 | ABS1556 | 9 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6230.2 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1202_Rangitata14.9457022636337 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | G127 | ABS1556 | OH Line-DOG | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataWOLF33.594- | SubTransmission | CB1202_Rangitata | G127 | ABS1556 | 10 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 445.8225 | 25.9409 | - | - | 330.4865 | 19.2299 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 234.9 | - | - | - | - | - | - | - | - | - | - | - | 25.9409 | - | 19.2299 | - | - | - | - | - | - | CB1202_Rangitata19.229855312552 | SubTransmissionCB1202_Rangitata33.594330.486460117266 | SubTransmissionCB1202_Rangitata33.594330.486460117266 | 19.2299 | 330.4865 | 330.4865 | G127 | ABS1556 | OH Line-WOLF | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataDOG33.594- | SubTransmission | CB1202_Rangitata | G127 | ABS1556 | 11 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7132.3 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1202_Rangitata14.9457022636337 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | G127 | ABS1556 | OH Line-DOG | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_Rangitata155633.594- | SubTransmission | CB1202_Rangitata | G127 | ABS1556 | 12 | GEMA | 1556 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | CB1202_Rangitata46.5492118635751 | SubTransmissionCB1202_Rangitata33.594800 | SubTransmissionCB1202_Rangitata33.594800 | 46.5492 | 800 | 800 | G127 | ABS1556 | ABS-1556 | 33.594
SubTransmissionCB1202_Rangitata33.594 | SubTransmissionCB1202_RangitataDOG33.594- | SubTransmission | CB1202_Rangitata | ABS1556 | ABS1564 | 13 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 63.9 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | CB1202_Rangitata14.9457022636337 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | SubTransmissionCB1202_Rangitata33.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | ABS1556 | ABS1564 | OH Line-DOG | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2TMK-CB120233.594Protection | SubTransmission | RGA_T2 | 33 kV Bus | T557 | 1 | TP Branch Report TMK.FDR.1202/AEL Protection Database | TMK-CB1202 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 462 | 26.8822 | 462 | 26.8822 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 26.8822 | 104.7357 | 72.7331 | - | RGA_T226.8821698512146 | SubTransmissionRGA_T233.594462 | SubTransmissionRGA_T233.594462 | 26.8822 | 462 | 462 | 33 kV Bus | T557 | Circuit Breaker-TMK-CB1202-Protection | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T23-1c 400 mm² Al XLPE33.594- | SubTransmission | RGA_T2 | 33 kV Bus | T557 | 2 | GEMA/Drawing 12189/GC Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 521 | 30.3152 | 521 | 30.3152 | 521 | 30.3152 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 50.2 | 1.2 | 0.95 | 18 | 0.98 | 1.2 | 1 | 4 | 0.3 | 0.72 | 349.2367 | 20.3209 | 30.3152 | 30.3152 | 30.3152 | - | - | - | - | - | 20.3209 | RGA_T220.3208675872751 | SubTransmissionRGA_T233.594349.23672 | SubTransmissionRGA_T233.594349.23672 | 20.3209 | 349.2367 | 349.2367 | 33 kV Bus | T557 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2T55733.594- | SubTransmission | RGA_T2 | 33 kV Bus | T557 | 3 | GEMA | T557 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | RGA_T246.5492118635751 | SubTransmissionRGA_T233.594800 | SubTransmissionRGA_T233.594800 | 46.5492 | 800 | 800 | 33 kV Bus | T557 | ABS-T557 | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2DOG33.594- | SubTransmission | RGA_T2 | T557 | G127 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2493.6 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | RGA_T214.9457022636337 | SubTransmissionRGA_T233.594256.858523103439 | SubTransmissionRGA_T233.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | T557 | G127 | OH Line-DOG | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2IODINE33.594- | SubTransmission | RGA_T2 | T557 | G127 | 5 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 33.594 | 368.604 | 21.4478 | - | - | 275.3865 | 16.0238 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1247.7 | - | - | - | - | - | - | - | - | - | - | - | 21.4478 | - | 16.0238 | - | - | - | - | - | - | RGA_T216.0237799627034 | SubTransmissionRGA_T233.594275.386487911596 | SubTransmissionRGA_T233.594275.386487911596 | 16.0238 | 275.3865 | 275.3865 | T557 | G127 | OH Line-IODINE | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2DOG33.594- | SubTransmission | RGA_T2 | T557 | G127 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 904.8 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | RGA_T214.9457022636337 | SubTransmissionRGA_T233.594256.858523103439 | SubTransmissionRGA_T233.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | T557 | G127 | OH Line-DOG | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T21-3c 95 mm² Al XLPE33.594- | SubTransmission | RGA_T2 | T557 | G127 | 7 | GEMA/General Cables | 1-3c 95 mm² Al XLPE | Cable | - | - | 33.594 | 218 | 12.6847 | 218 | 12.6847 | 218 | 12.6847 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 1202.5 | 1.25 | 0.97 | 18 | 0.98 | 1.2 | 1 | 1 | 0 | 1 | 207.2308 | 12.058 | 12.6847 | 12.6847 | 12.6847 | - | - | - | - | - | 12.058 | RGA_T212.0580380173227 | SubTransmissionRGA_T233.594207.2308 | SubTransmissionRGA_T233.594207.2308 | 12.058 | 207.2308 | 207.2308 | T557 | G127 | Cable-1-3c 95 mm² Al XLPE | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2G12733.594- | SubTransmission | RGA_T2 | T557 | G127 | 8 | GEMA | G127 | Link | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T2 | SubTransmissionRGA_T233.594 | SubTransmissionRGA_T233.594 |  |  |  | T557 | G127 | Link-G127 | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2DOG33.594- | SubTransmission | RGA_T2 | G127 | ABS1556 | 9 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6230.2 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | RGA_T214.9457022636337 | SubTransmissionRGA_T233.594256.858523103439 | SubTransmissionRGA_T233.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | G127 | ABS1556 | OH Line-DOG | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2WOLF33.594- | SubTransmission | RGA_T2 | G127 | ABS1556 | 10 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 445.8225 | 25.9409 | - | - | 330.4865 | 19.2299 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 234.9 | - | - | - | - | - | - | - | - | - | - | - | 25.9409 | - | 19.2299 | - | - | - | - | - | - | RGA_T219.229855312552 | SubTransmissionRGA_T233.594330.486460117266 | SubTransmissionRGA_T233.594330.486460117266 | 19.2299 | 330.4865 | 330.4865 | G127 | ABS1556 | OH Line-WOLF | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2DOG33.594- | SubTransmission | RGA_T2 | G127 | ABS1556 | 11 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7132.3 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | RGA_T214.9457022636337 | SubTransmissionRGA_T233.594256.858523103439 | SubTransmissionRGA_T233.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | G127 | ABS1556 | OH Line-DOG | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2155633.594- | SubTransmission | RGA_T2 | G127 | ABS1556 | 12 | GEMA | 1556 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | RGA_T246.5492118635751 | SubTransmissionRGA_T233.594800 | SubTransmissionRGA_T233.594800 | 46.5492 | 800 | 800 | G127 | ABS1556 | ABS-1556 | 33.594
SubTransmissionRGA_T233.594 | SubTransmissionRGA_T2DOG33.594- | SubTransmission | RGA_T2 | ABS1556 | ABS1564 | 13 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 33.594 | 343.6934 | 19.9983 | - | - | 256.8585 | 14.9457 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 63.9 | - | - | - | - | - | - | - | - | - | - | - | 19.9983 | - | 14.9457 | - | - | - | - | - | - | RGA_T214.9457022636337 | SubTransmissionRGA_T233.594256.858523103439 | SubTransmissionRGA_T233.594256.858523103439 | 14.9457 | 256.8585 | 256.8585 | ABS1556 | ABS1564 | OH Line-DOG | 33.594
ZoneSubstationRGA_T233.594 | ZoneSubstationRGA_T2156433.594- | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 1 | GEMA | 1564 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | RGA_T246.5492118635751 | ZoneSubstationRGA_T233.594800 | ZoneSubstationRGA_T233.594800 | 46.5492 | 800 | 800 | ABS1564 | CB36 | ABS-1564 | 33.594
ZoneSubstationRGA_T233.594 | ZoneSubstationRGA_T2RGA_T2-CB156233.594Protection | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 2 | GEMA/AEL Protection Database | RGA_T2-CB1562 | Circuit Breaker | Relay SEL 387E-311C-1 | Protection | 33.594 | - | - | - | - | - | - | - | - | - | - | 402 | 23.391 | 402 | 23.391 | - | - | 300 | 17.456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.391 | - | 17.456 | - | RGA_T217.4559544488407 | ZoneSubstationRGA_T233.594300 | ZoneSubstationRGA_T233.594300 | 17.456 | 300 | 300 | ABS1564 | CB36 | Circuit Breaker-RGA_T2-CB1562-Protection | 33.594
ZoneSubstationRGA_T233.594 | ZoneSubstationRGA_T2156633.594- | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 3 | GEMA | 1566 | ABS | - | - | 33.594 | 800 | 46.5492 | 800 | 46.5492 | 800 | 46.5492 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 46.5492 | 46.5492 | 46.5492 | - | - | - | - | - | - | RGA_T246.5492118635751 | ZoneSubstationRGA_T233.594800 | ZoneSubstationRGA_T233.594800 | 46.5492 | 800 | 800 | ABS1564 | CB36 | ABS-1566 | 33.594
ZoneSubstationRGA_T233.594 | ZoneSubstationRGA_T2D1479-T233.594HV Winding | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 4 | AEL Transformers Database | D1479-T2 | Transformer | - | HV Winding | 33.594 | 257.7917 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T2 | ZoneSubstationRGA_T233.594 | ZoneSubstationRGA_T233.594257.791690118604 |  |  | 257.7917 | ABS1564 | CB36 | Transformer-D1479-T2-HV Winding | 33.594
ZoneSubstationRGA_T211.22 | ZoneSubstationRGA_T2D1479-T211.22LV Winding | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 5 | AEL Transformers Database | D1479-T2 | Transformer | - | LV Winding | 11.22 | 771.8586 | 15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T2 | ZoneSubstationRGA_T211.22 | ZoneSubstationRGA_T211.22771.858648649232 |  |  | 771.8586 | ABS1564 | CB36 | Transformer-D1479-T2-LV Winding | 11.22
ZoneSubstationRGA_T211.22 | ZoneSubstationRGA_T26-1c 400 mm² Al XLPE11.22- | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 6 | GEMA/General Cables/12608 | 6-1c 400 mm² Al XLPE | Cable | - | - | 11.22 | 928 | 18.0344 | 928 | 18.0344 | 928 | 18.0344 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 14.9 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 1 | 0 | 0.98 | 873.4262 | 16.9738 | 18.0344 | 18.0344 | 18.0344 | - | - | - | - | - | 16.9738 | RGA_T216.9738237213869 | ZoneSubstationRGA_T211.22873.426176 | ZoneSubstationRGA_T211.22873.426176 | 16.9738 | 873.4262 | 873.4262 | ABS1564 | CB36 | Cable-6-1c 400 mm² Al XLPE | 11.22
ZoneSubstationRGA_T211.22 | ZoneSubstationRGA_T2RGA_T2-CB3611.22Protection | ZoneSubstation | RGA_T2 | ABS1564 | CB36 | 7 | GEMA/AEL Protection Database | RGA_T2-CB36 | Circuit Breaker | Relay SEL 387E | Protection | 11.22 | 1250 | 24.292 | 1250 | 24.292 | 1250 | 24.292 | - | - | - | - | 1048 | 20.3664 | 1048 | 20.3664 | - | - | 800 | 15.5469 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.292 | 24.292 | 24.292 | - | - | 20.3664 | - | 15.5469 | - | RGA_T215.5468880487382 | ZoneSubstationRGA_T211.22800 | ZoneSubstationRGA_T211.22800 | 15.5469 | 800 | 800 | ABS1564 | CB36 | Circuit Breaker-RGA_T2-CB36-Protection | 11.22
DistributionFeederCB11_Belfield11.22 | DistributionFeederCB11_BelfieldRGA_T2-CB1111.22Protection | DistributionFeeder | CB11_Belfield | CB11 | T587 | 1 | GEMA/AEL Protection Database | RGA_T2-CB11 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 800 | 15.5469 | 800 | 15.5469 | 800 | 15.5469 | - | - | - | - | 300 | 5.8301 | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5469 | 15.5469 | 15.5469 | - | - | 5.8301 | - | 7.7734 | - | CB11_Belfield5.83008301827684 | DistributionFeederCB11_Belfield11.22300 | DistributionFeederCB11_Belfield11.22300 | 5.8301 | 300 | 300 | CB11 | T587 | Circuit Breaker-RGA_T2-CB11-Protection | 11.22
DistributionFeederCB11_Belfield11.22 | DistributionFeederCB11_Belfield3-1c 400 mm² Al XLPE11.22- | DistributionFeeder | CB11_Belfield | CB11 | T587 | 2 | GEMA/Drawing 11217 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 40.6 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.55 | 0.89 | 459.004 | 8.9201 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 8.9201 | CB11_Belfield8.92010420826273 | DistributionFeederCB11_Belfield11.22459.003972 | DistributionFeederCB11_Belfield11.22459.003972 | 8.9201 | 459.004 | 459.004 | CB11 | T587 | Cable-3-1c 400 mm² Al XLPE | 11.22
DistributionFeederCB11_Belfield11.22 | DistributionFeederCB11_BelfieldT58711.22- | DistributionFeeder | CB11_Belfield | CB11 | T587 | 3 | GEMA | T587 | ABS | - | - | 11.22 | 600 | 11.6602 | 600 | 11.6602 | 600 | 11.6602 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.6602 | 11.6602 | 11.6602 | - | - | - | - | - | - | CB11_Belfield11.6601660365537 | DistributionFeederCB11_Belfield11.22600 | DistributionFeederCB11_Belfield11.22600 | 11.6602 | 600 | 600 | CB11 | T587 | ABS-T587 | 11.22
DistributionFeederCB11_Belfield11.22 | DistributionFeederCB11_BelfieldIODINE11.22- | DistributionFeeder | CB11_Belfield | T587 | Pole 808827 | 4 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 11.22 | 368.604 | 7.1633 | - | - | 275.3865 | 5.3518 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1155.9 | - | - | - | - | - | - | - | - | - | - | - | 7.1633 | - | 5.3518 | - | - | - | - | - | - | CB11_Belfield5.35175362212099 | DistributionFeederCB11_Belfield11.22275.386487911596 | DistributionFeederCB11_Belfield11.22275.386487911596 | 5.3518 | 275.3865 | 275.3865 | T587 | Pole 808827 | OH Line-IODINE | 11.22
DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_OrtonRGA_T2-CB1211.22Protection | DistributionFeeder | CB12_Orton | CB12 | T590 | 1 | GEMA/AEL Protection Database | RGA_T2-CB12 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 800 | 15.5469 | 800 | 15.5469 | 800 | 15.5469 | - | - | - | - | 300 | 5.8301 | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5469 | 15.5469 | 15.5469 | - | - | 5.8301 | - | 7.7734 | - | CB12_Orton5.83008301827684 | DistributionFeederCB12_Orton11.22300 | DistributionFeederCB12_Orton11.22300 | 5.8301 | 300 | 300 | CB12 | T590 | Circuit Breaker-RGA_T2-CB12-Protection | 11.22
DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_Orton3-1c 400 mm² Al XLPE11.22- | DistributionFeeder | CB12_Orton | CB12 | T590 | 2 | GEMA/Drawing 11217 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 10.4 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.55 | 0.89 | 459.004 | 8.9201 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 8.9201 | CB12_Orton8.92010420826273 | DistributionFeederCB12_Orton11.22459.003972 | DistributionFeederCB12_Orton11.22459.003972 | 8.9201 | 459.004 | 459.004 | CB12 | T590 | Cable-3-1c 400 mm² Al XLPE | 11.22
DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_Orton1-3c 300 mm² Al XLPE11.22- | DistributionFeeder | CB12_Orton | CB12 | T590 | 3 | GEMA/Drawing 11217 | 1-3c 300 mm² Al XLPE | Cable | - | - | 11.22 | 476 | 9.2504 | 476 | 9.2504 | 476 | 9.2504 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 112.1 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 2 | 0.55 | 0.89 | 406.8639 | 7.9068 | 9.2504 | 9.2504 | 9.2504 | - | - | - | - | - | 7.9068 | CB12_Orton7.90683352538745 | DistributionFeederCB12_Orton11.22406.863856 | DistributionFeederCB12_Orton11.22406.863856 | 7.9068 | 406.8639 | 406.8639 | CB12 | T590 | Cable-1-3c 300 mm² Al XLPE | 11.22
DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_OrtonT59011.22- | DistributionFeeder | CB12_Orton | CB12 | T590 | 4 | GEMA | T590 | ABS | - | - | 11.22 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CB12_Orton | DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_Orton11.22 |  |  |  | CB12 | T590 | ABS-T590 | 11.22
DistributionFeederCB12_Orton11.22 | DistributionFeederCB12_OrtonIODINE11.22- | DistributionFeeder | CB12_Orton | T590 | Pole 46673 | 5 | GEMA/AEL OH Amp Calc. | IODINE | OH Line | - | - | 11.22 | 368.604 | 7.1633 | - | - | 275.3865 | 5.3518 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2096 | - | - | - | - | - | - | - | - | - | - | - | 7.1633 | - | 5.3518 | - | - | - | - | - | - | CB12_Orton5.35175362212099 | DistributionFeederCB12_Orton11.22275.386487911596 | DistributionFeederCB12_Orton11.22275.386487911596 | 5.3518 | 275.3865 | 275.3865 | T590 | Pole 46673 | OH Line-IODINE | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata IslandRGA_T2-CB1311.22Protection | DistributionFeeder | CB13_Rangitata Island | CB13 | T435 | 1 | GEMA/AEL Protection Database | RGA_T2-CB13 | Circuit Breaker | Relay SEL 311C-1 | Protection | 11.22 | 800 | 15.5469 | 800 | 15.5469 | 800 | 15.5469 | - | - | - | - | 300 | 5.8301 | 300 | 5.8301 | - | - | 400 | 7.7734 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 15.5469 | 15.5469 | 15.5469 | - | - | 5.8301 | - | 7.7734 | - | CB13_Rangitata Island5.83008301827684 | DistributionFeederCB13_Rangitata Island11.22300 | DistributionFeederCB13_Rangitata Island11.22300 | 5.8301 | 300 | 300 | CB13 | T435 | Circuit Breaker-RGA_T2-CB13-Protection | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata Island3-1c 400 mm² Al XLPE11.22- | DistributionFeeder | CB13_Rangitata Island | CB13 | T435 | 2 | GEMA/Drawing 11217 | 3-1c 400 mm² Al XLPE | Cable | - | - | 11.22 | 537 | 10.4358 | 537 | 10.4358 | 537 | 10.4358 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 23.5 | 1 | 0.98 | 18 | 0.98 | 1.2 | 1 | 3 | 0.55 | 0.83 | 428.0599 | 8.3187 | 10.4358 | 10.4358 | 10.4358 | - | - | - | - | - | 8.3187 | CB13_Rangitata Island8.31874886837985 | DistributionFeederCB13_Rangitata Island11.22428.059884 | DistributionFeederCB13_Rangitata Island11.22428.059884 | 8.3187 | 428.0599 | 428.0599 | CB13 | T435 | Cable-3-1c 400 mm² Al XLPE | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata Island1-3c 185 mm² XLPE11.22- | DistributionFeeder | CB13_Rangitata Island | CB13 | T435 | 3 | GEMA/General Cables/12608 | 1-3c 185 mm² XLPE | Cable | - | - | 11.22 | 367 | 7.1321 | 367 | 7.1321 | 367 | 7.1321 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 44.6 | 0.9 | 0.99 | 18 | 0.98 | 1.5 | 0.95 | 4 | 0.45 | 0.8 | 270.6082 | 5.2589 | 7.1321 | 7.1321 | 7.1321 | - | - | - | - | - | 5.2589 | CB13_Rangitata Island5.25889392715045 | DistributionFeederCB13_Rangitata Island11.22270.608184 | DistributionFeederCB13_Rangitata Island11.22270.608184 | 5.2589 | 270.6082 | 270.6082 | CB13 | T435 | Cable-1-3c 185 mm² XLPE | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata IslandDOG11.22- | DistributionFeeder | CB13_Rangitata Island | T435 | T596 | 4 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 172 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB13_Rangitata Island4.99168837881677 | DistributionFeederCB13_Rangitata Island11.22256.858523103439 | DistributionFeederCB13_Rangitata Island11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | T435 | T596 | OH Line-DOG | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata IslandT59611.22- | DistributionFeeder | CB13_Rangitata Island | T435 | T596 | 5 | GEMA | T596 | Link | - | - | 11.22 | 300 | 5.8301 | 300 | 5.8301 | 300 | 5.8301 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.8301 | 5.8301 | 5.8301 | - | - | - | - | - | - | CB13_Rangitata Island5.83008301827684 | DistributionFeederCB13_Rangitata Island11.22300 | DistributionFeederCB13_Rangitata Island11.22300 | 5.8301 | 300 | 300 | T435 | T596 | Link-T596 | 11.22
DistributionFeederCB13_Rangitata Island11.22 | DistributionFeederCB13_Rangitata IslandDOG11.22- | DistributionFeeder | CB13_Rangitata Island | T435 | T596 | 6 | GEMA/AEL OH Amp Calc. | DOG | OH Line | - | - | 11.22 | 343.6934 | 6.6792 | - | - | 256.8585 | 4.9917 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1536.36 | - | - | - | - | - | - | - | - | - | - | - | 6.6792 | - | 4.9917 | - | - | - | - | - | - | CB13_Rangitata Island4.99168837881677 | DistributionFeederCB13_Rangitata Island11.22256.858523103439 | DistributionFeederCB13_Rangitata Island11.22256.858523103439 | 4.9917 | 256.8585 | 256.8585 | T435 | T596 | OH Line-DOG | 11.22
SwitchingStationCNL-RGA33.594 | SubTransmissionRGA_T1Limit33.594- | SwitchingStation | CNL-RGA | Pole 02052 | CB1416 | 5 | AEL-Fonterra Agreement/Tesla study | 10 MW Limit | AEL-Fonterra Contractual | - | - | 33.594 | 171.8611 | 10 | 171.8611 | 10 | 171.8611 | 10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 10 | 10 | 10 | - | - | - | - | - | - | RGA_T110 | SwitchingStationCNL-RGA33.594171.861126745736 | SwitchingStationCNL-RGA33.594171.861126745736 | 10 | 171.8611 | 171.8611 | Pole 02052 | CB1416 | AEL-Fonterra Contractual-10 MW Limit | 33.594
SwitchingStationCNL-RGA33.594 | SubTransmissionRGA_T1141433.594- | SwitchingStation | CNL-RGA | Pole 02052 | CB1416 | 7 | GEMA | 1414 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | SwitchingStationCNL-RGA33.594 | SwitchingStationCNL-RGA33.594 |  |  |  | Pole 02052 | CB1416 | ABS-1414 | 33.594
SwitchingStationCNL-RGA33.594 | SubTransmissionRGA_T1RGA_T1-CB141233.594Protection | SwitchingStation | CNL-RGA | Pole 02052 | CB1416 | 8 | GEMA/AEL Protection Database | CNL-RGA-CB1412 | Circuit Breaker | Relay SEL 751A | Protection | 33.594 | 2000 | 116.373 | 2000 | 116.373 | 2000 | 116.373 | - | - | - | - | 423 | 24.6129 | - | - | - | - | 300 | 17.456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116.373 | 116.373 | 116.373 | - | - | 24.6129 | - | 17.456 | - | CNL-RGA17.4559544488407 | SwitchingStationCNL-RGA33.594300 | SwitchingStationCNL-RGA33.594300 | 17.456 | 300 | 300 | Pole 02052 | CB1416 | Circuit Breaker-CNL-RGA-CB1412-Protection | 33.594
SwitchingStationCNL-RGA33.594 | SubTransmissionRGA_T1141633.594- | SwitchingStation | CNL-RGA | Pole 02052 | CB1416 | 9 | GEMA | 1416 | ABS | - | - | 33.594 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | RGA_T1 | SwitchingStationCNL-RGA33.594 | SwitchingStationCNL-RGA33.594 |  |  |  | Pole 02052 | CB1416 | ABS-1416 | 33.594
SubTransmissionCB1192_Clandeboye No.133.594 | SubTransmissionCB1192_Clandeboye No.1TMK-CB119233.594Protection | SubTransmission | CB1192_Clandeboye No.1 | 33 kV Bus | Pole 02081 | 1 | TP Branch Report TMK.FDR.1192/AEL Protection Database | TMK-CB1192 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 34.9119 | - | CB1192_Clandeboye No.129.6751225630291 | SubTransmissionCB1192_Clandeboye No.133.594510 | SubTransmissionCB1192_Clandeboye No.133.594510 | 29.6751 | 510 | 510 | 33 kV Bus | Pole 02081 | Circuit Breaker-TMK-CB1192-Protection | 33.594
SubTransmissionCB1192_Clandeboye No.133.594 | SubTransmissionCB1192_Clandeboye No.13-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1192_Clandeboye No.1 | 33 kV Bus | Pole 02081 | 2 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 10840 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CB1192_Clandeboye No.123.6932032106616 | SubTransmissionCB1192_Clandeboye No.133.594407.19406 | SubTransmissionCB1192_Clandeboye No.133.594407.19406 | 23.6932 | 407.1941 | 407.1941 | 33 kV Bus | Pole 02081 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCB1192_Clandeboye No.133.594 | SubTransmissionCB1192_Clandeboye No.1JAGUAR33.594- | SubTransmission | CB1192_Clandeboye No.1 | Pole 02081 | REC T615 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CB1192_Clandeboye No.133.9106986639602 | SubTransmissionCB1192_Clandeboye No.133.594582.793088112333 | SubTransmissionCB1192_Clandeboye No.133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02081 | REC T615 | OH Line-JAGUAR | 33.594
SubTransmissionCD_133.594T1 | SubTransmissionCD_1TMK-CB119233.594Protection | SubTransmission | CD_1 | 33 kV Bus | Pole 02081 | 1 | TP Branch Report TMK.FDR.1192/AEL Protection Database | TMK-CB1192 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 34.9119 | - | CD_129.6751225630291 | SubTransmissionCD_133.594510 | SubTransmissionCD_133.594510 | 29.6751 | 510 | 510 | 33 kV Bus | Pole 02081 | Circuit Breaker-TMK-CB1192-Protection | 33.594
SubTransmissionCD_133.594T1 | SubTransmissionCD_13-1c 400 mm² Al XLPE33.594- | SubTransmission | CD_1 | 33 kV Bus | Pole 02081 | 2 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 10840 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CD_123.6932032106616 | SubTransmissionCD_133.594407.19406 | SubTransmissionCD_133.594407.19406 | 23.6932 | 407.1941 | 407.1941 | 33 kV Bus | Pole 02081 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCD_133.594T1 | SubTransmissionCD_1JAGUAR33.594- | SubTransmission | CD_1 | Pole 02081 | REC T615 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CD_133.9106986639602 | SubTransmissionCD_133.594582.793088112333 | SubTransmissionCD_133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02081 | REC T615 | OH Line-JAGUAR | 33.594
ZoneSubstationCD_133.594T1 | ZoneSubstationCD_1T61533.594Protection | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 4 | GEMA/AEL Protection Database | T615 | Recloser | Relay SEL 387E | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 512 | 29.7915 | 512 | 29.7915 | - | - | 400 | 23.2746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 29.7915 | - | 23.2746 | - | CD_123.2746059317875 | ZoneSubstationCD_133.594400 | ZoneSubstationCD_133.594400 | 23.2746 | 400 | 400 | Recloser T615 | 11 kV Bus | Recloser-T615-Protection | 33.594
ZoneSubstationCD_133.594T1 | ZoneSubstationCD_13-1c 300 mm² Al XLPE33.594- | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 5 | GEMA/General Cable | 3-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 414 | 24.0892 | 414 | 24.0892 | 414 | 24.0892 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 269 | 1.2 | 0.96 | 18 | 0.983 | 1.2 | 1 | 2 | 0.6 | 0.89 | 347.7083 | 20.2319 | 24.0892 | 24.0892 | 24.0892 | - | - | - | - | - | 20.2319 | CD_120.2319360627971 | ZoneSubstationCD_133.594347.7083328 | ZoneSubstationCD_133.594347.7083328 | 20.2319 | 347.7083 | 347.7083 | Recloser T615 | 11 kV Bus | Cable-3-1c 300 mm² Al XLPE | 33.594
ZoneSubstationCD_133.594T1 | ZoneSubstationCD_1D1246-T133.594HV Winding | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 6 | AEL Transformers Database | D1246-T1 | Transformer | - | HV Winding | 33.594 | 343.7223 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_1 | ZoneSubstationCD_133.594 | ZoneSubstationCD_133.594343.722253491472 |  |  | 343.7223 | Recloser T615 | 11 kV Bus | Transformer-D1246-T1-HV Winding | 33.594
ZoneSubstationCD_111T1 | ZoneSubstationCD_1D1246-T111LV Winding | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 7 | AEL Transformers Database | D1246-T1 | Transformer | - | LV Winding | 11 | 1049.7278 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_1 | ZoneSubstationCD_111 | ZoneSubstationCD_1111049.72776216296 |  |  | 1049.7278 | Recloser T615 | 11 kV Bus | Transformer-D1246-T1-LV Winding | 11
ZoneSubstationCD_111T1 | ZoneSubstationCD_16-1c 500 mm² Al XLPE11- | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 8 | GEMA/General Cable | 6-1c 500 mm² Al XLPE | Cable | - | - | 11 | 1462 | 27.8548 | 1462 | 27.8548 | 1462 | 27.8548 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 4 | 0.8 | 1 | 18 | 0.983 | 1.2 | 1 | 1 | 0 | 1 | 1437.146 | 27.3813 | 27.8548 | 27.8548 | 27.8548 | - | - | - | - | - | 27.3813 | CD_127.3813087888382 | ZoneSubstationCD_1111437.146 | ZoneSubstationCD_1111437.146 | 27.3813 | 1437.146 | 1437.146 | Recloser T615 | 11 kV Bus | Cable-6-1c 500 mm² Al XLPE | 11
ZoneSubstationCD_111T1 | ZoneSubstationCD_1CD1-T60611Protection | ZoneSubstation | CD_1 | Recloser T615 | 11 kV Bus | 9 | GEMA/AEL Protection Database | CD1-T606 | Circuit Breaker | Relay SEL 387E | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1440 | 27.4357 | 1440 | 27.4357 | - | - | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 27.4357 | - | 22.8631 | - | CD_122.8630706599092 | ZoneSubstationCD_1111200 | ZoneSubstationCD_1111200 | 22.8631 | 1200 | 1200 | Recloser T615 | 11 kV Bus | Circuit Breaker-CD1-T606-Protection | 11
SubTransmissionCB1272_Clandeboye No.233.594 | SubTransmissionCB1272_Clandeboye No.2TMK-CB127233.594Protection | SubTransmission | CB1272_Clandeboye No.2 | 33 kV Bus | Pole 02001 | 1 | TP Branch Report TMK.FDR.1272/AEL Protection Database | TMK-CB1272 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 72.7331 | - | CB1272_Clandeboye No.229.6751225630291 | SubTransmissionCB1272_Clandeboye No.233.594510 | SubTransmissionCB1272_Clandeboye No.233.594510 | 29.6751 | 510 | 510 | 33 kV Bus | Pole 02001 | Circuit Breaker-TMK-CB1272-Protection | 33.594
SubTransmissionCB1272_Clandeboye No.233.594 | SubTransmissionCB1272_Clandeboye No.26-1c 300 mm² Al XLPE33.594- | SubTransmission | CB1272_Clandeboye No.2 | 33 kV Bus | Pole 02001 | 2 | GEMA/General Cable | 6-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 828 | 48.1784 | 828 | 48.1784 | 828 | 48.1784 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 231 | 1.1 | 0.97 | 18.5 | 0.98 | 1.2 | 1 | 4 | 0.4 | 0.75 | 590.3226 | 34.3488 | 48.1784 | 48.1784 | 48.1784 | - | - | - | - | - | 34.3488 | CB1272_Clandeboye No.234.3488147190706 | SubTransmissionCB1272_Clandeboye No.233.594590.3226 | SubTransmissionCB1272_Clandeboye No.233.594590.3226 | 34.3488 | 590.3226 | 590.3226 | 33 kV Bus | Pole 02001 | Cable-6-1c 300 mm² Al XLPE | 33.594
SubTransmissionCB1272_Clandeboye No.233.594 | SubTransmissionCB1272_Clandeboye No.2JAGUAR33.594- | SubTransmission | CB1272_Clandeboye No.2 | Pole 02001 | Pole 02049 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5804 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CB1272_Clandeboye No.233.9106986639602 | SubTransmissionCB1272_Clandeboye No.233.594582.793088112333 | SubTransmissionCB1272_Clandeboye No.233.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02001 | Pole 02049 | OH Line-JAGUAR | 33.594
SubTransmissionCB1272_Clandeboye No.233.594 | SubTransmissionCB1272_Clandeboye No.2WOLF33.594- | SubTransmission | CB1272_Clandeboye No.2 | Pole 02049 | Pole 02052 | 5 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 572.8673 | 33.3332 | - | - | 496.0602 | 28.864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 404 | - | - | - | - | - | - | - | - | - | - | - | 33.3332 | - | 28.864 | - | - | - | - | - | - | CB1272_Clandeboye No.228.8640140783565 | SubTransmissionCB1272_Clandeboye No.233.594496.060198191114 | SubTransmissionCB1272_Clandeboye No.233.594496.060198191114 | 28.864 | 496.0602 | 496.0602 | Pole 02049 | Pole 02052 | OH Line-WOLF | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_1TMK-CB127233.594Protection | SubTransmission | CD_1 | 33 kV Bus | Pole 02001 | 1 | TP Branch Report TMK.FDR.1272/AEL Protection Database | TMK-CB1272 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 510 | 29.6751 | 510 | 29.6751 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 29.6751 | 104.7357 | 72.7331 | - | CD_129.6751225630291 | SubTransmissionCD_133.594510 | SubTransmissionCD_133.594510 | 29.6751 | 510 | 510 | 33 kV Bus | Pole 02001 | Circuit Breaker-TMK-CB1272-Protection | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_16-1c 300 mm² Al XLPE33.594- | SubTransmission | CD_1 | 33 kV Bus | Pole 02001 | 2 | GEMA/General Cable | 6-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 828 | 48.1784 | 828 | 48.1784 | 828 | 48.1784 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 231 | 1.1 | 0.97 | 18.5 | 0.98 | 1.2 | 1 | 4 | 0.4 | 0.75 | 590.3226 | 34.3488 | 48.1784 | 48.1784 | 48.1784 | - | - | - | - | - | 34.3488 | CD_134.3488147190706 | SubTransmissionCD_133.594590.3226 | SubTransmissionCD_133.594590.3226 | 34.3488 | 590.3226 | 590.3226 | 33 kV Bus | Pole 02001 | Cable-6-1c 300 mm² Al XLPE | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_1JAGUAR33.594- | SubTransmission | CD_1 | Pole 02001 | Pole 02049 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5804 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CD_133.9106986639602 | SubTransmissionCD_133.594582.793088112333 | SubTransmissionCD_133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02001 | Pole 02049 | OH Line-JAGUAR | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_1WOLF33.594- | SubTransmission | CD_1 | Pole 02049 | Pole 02052 | 5 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 572.8673 | 33.3332 | - | - | 496.0602 | 28.864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 404 | - | - | - | - | - | - | - | - | - | - | - | 33.3332 | - | 28.864 | - | - | - | - | - | - | CD_128.8640140783565 | SubTransmissionCD_133.594496.060198191114 | SubTransmissionCD_133.594496.060198191114 | 28.864 | 496.0602 | 496.0602 | Pole 02049 | Pole 02052 | OH Line-WOLF | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_1JAGUAR33.594- | SubTransmission | CD_1 | Pole 02052 | REC T616 | 6 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3831 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CD_133.9106986639602 | SubTransmissionCD_133.594582.793088112333 | SubTransmissionCD_133.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02052 | REC T616 | OH Line-JAGUAR | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_1T61633.594Protection | SubTransmission | CD_1 | REC T616 | 11 kV Bus | 1 | GEMA/AEL Protection Database | T616 | Recloser | Relay SEL 387E | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 512 | 29.7915 | 512 | 29.7915 | - | - | 400 | 23.2746 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 29.7915 | - | 23.2746 | - | CD_123.2746059317875 | SubTransmissionCD_133.594400 | SubTransmissionCD_133.594400 | 23.2746 | 400 | 400 | REC T616 | 11 kV Bus | Recloser-T616-Protection | 33.594
SubTransmissionCD_133.594T2 | SubTransmissionCD_13-1c 300 mm² Al XLPE33.594- | SubTransmission | CD_1 | REC T616 | 11 kV Bus | 2 | GEMA/General Cable | 3-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 414 | 24.0892 | 414 | 24.0892 | 414 | 24.0892 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 261 | 1.2 | 0.96 | 18 | 0.983 | 1.2 | 1 | 2 | 0.6 | 0.89 | 347.7083 | 20.2319 | 24.0892 | 24.0892 | 24.0892 | - | - | - | - | - | 20.2319 | CD_120.2319360627971 | SubTransmissionCD_133.594347.7083328 | SubTransmissionCD_133.594347.7083328 | 20.2319 | 347.7083 | 347.7083 | REC T616 | 11 kV Bus | Cable-3-1c 300 mm² Al XLPE | 33.594
ZoneSubstationCD_133.594T2 | ZoneSubstationCD_1D1246-T233.594HV Winding | ZoneSubstation | CD_1 | REC T616 | 11 kV Bus | 3 | AEL Transformers Database | D1246-T2 | Transformer | - | HV Winding | 33.594 | 343.7223 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_1 | ZoneSubstationCD_133.594 | ZoneSubstationCD_133.594343.722253491472 |  |  | 343.7223 | REC T616 | 11 kV Bus | Transformer-D1246-T2-HV Winding | 33.594
ZoneSubstationCD_111T2 | ZoneSubstationCD_1D1246-T211LV Winding | ZoneSubstation | CD_1 | REC T616 | 11 kV Bus | 4 | AEL Transformers Database | D1246-T2 | Transformer | - | LV Winding | 11 | 1049.7278 | 20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_1 | ZoneSubstationCD_111 | ZoneSubstationCD_1111049.72776216296 |  |  | 1049.7278 | REC T616 | 11 kV Bus | Transformer-D1246-T2-LV Winding | 11
ZoneSubstationCD_111T2 | ZoneSubstationCD_16-1c 500 mm² Al XLPE11- | ZoneSubstation | CD_1 | REC T616 | 11 kV Bus | 5 | GEMA/General Cable | 6-1c 500 mm² Al XLPE | Cable | - | - | 11 | 1462 | 27.8548 | 1462 | 27.8548 | 1462 | 27.8548 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 5 | 0.8 | 1 | 18 | 0.983 | 1.2 | 1 | 1 | 0 | 1 | 1437.146 | 27.3813 | 27.8548 | 27.8548 | 27.8548 | - | - | - | - | - | 27.3813 | CD_127.3813087888382 | ZoneSubstationCD_1111437.146 | ZoneSubstationCD_1111437.146 | 27.3813 | 1437.146 | 1437.146 | REC T616 | 11 kV Bus | Cable-6-1c 500 mm² Al XLPE | 11
ZoneSubstationCD_111T2 | ZoneSubstationCD_1CD1-T60811Protection | ZoneSubstation | CD_1 | REC T616 | 11 kV Bus | 6 | GEMA/AEL Protection Database | CD1-T608 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 1250 | 23.8157 | 1250 | 23.8157 | 1250 | 23.8157 | - | - | - | - | 1440 | 27.4357 | 1440 | 27.4357 | - | - | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 23.8157 | 23.8157 | 23.8157 | - | - | 27.4357 | - | 22.8631 | - | CD_122.8630706599092 | ZoneSubstationCD_1111200 | ZoneSubstationCD_1111200 | 22.8631 | 1200 | 1200 | REC T616 | 11 kV Bus | Circuit Breaker-CD1-T608-Protection | 11
DistributionFeederT600_Tie to Milk Powder 211 | DistributionFeederT600_Tie to Milk Powder 2CD1-T60011Protection | DistributionFeeder | T600_Tie to Milk Powder 2 | 11 kV Bus | T465 | 1 | GEMA/AEL Protection Database | CD1-T600 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | 7.621 | - | T600_Tie to Milk Powder 27.62102355330306 | DistributionFeederT600_Tie to Milk Powder 211400 | DistributionFeederT600_Tie to Milk Powder 211400 | 7.621 | 400 | 400 | 11 kV Bus | T465 | Circuit Breaker-CD1-T600-Protection | 11
DistributionFeederT600_Tie to Milk Powder 211 | DistributionFeederT600_Tie to Milk Powder 21-3c 300 mm² Al XLPE11- | DistributionFeeder | T600_Tie to Milk Powder 2 | 11 kV Bus | T465 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 454.9 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.24 | 0.67 | 303.1654 | 5.7761 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.7761 | T600_Tie to Milk Powder 25.77607572034353 | DistributionFeederT600_Tie to Milk Powder 211303.165352 | DistributionFeederT600_Tie to Milk Powder 211303.165352 | 5.7761 | 303.1654 | 303.1654 | 11 kV Bus | T465 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT600_Tie to Milk Powder 211 | DistributionFeederT600_Tie to Milk Powder 2T46511- | DistributionFeeder | T600_Tie to Milk Powder 2 | 11 kV Bus | T465 | 3 | GEMA | T465 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T600_Tie to Milk Powder 212.0031120964523 | DistributionFeederT600_Tie to Milk Powder 211630 | DistributionFeederT600_Tie to Milk Powder 211630 | 12.0031 | 630 | 630 | 11 kV Bus | T465 | RMU Switch-T465 | 11
DistributionFeederT601_Fire Services11 | DistributionFeederT601_Fire ServicesCD1-T60111- | DistributionFeeder | T601_Fire Services | 11 kV Bus | T256 | 1 | GEMA/AEL Protection Database | CD1-T601 | Circuit Breaker | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | 7.621 | - | T601_Fire Services7.62102355330306 | DistributionFeederT601_Fire Services11400 | DistributionFeederT601_Fire Services11400 | 7.621 | 400 | 400 | 11 kV Bus | T256 | Circuit Breaker-CD1-T601 | 11
DistributionFeederT601_Fire Services11 | DistributionFeederT601_Fire Services1-3c 300 mm² Al XLPE11- | DistributionFeeder | T601_Fire Services | 11 kV Bus | T256 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 150.3 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.24 | 0.67 | 303.1654 | 5.7761 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.7761 | T601_Fire Services5.77607572034353 | DistributionFeederT601_Fire Services11303.165352 | DistributionFeederT601_Fire Services11303.165352 | 5.7761 | 303.1654 | 303.1654 | 11 kV Bus | T256 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT601_Fire Services11 | DistributionFeederT601_Fire ServicesT46511- | DistributionFeeder | T601_Fire Services | 11 kV Bus | T256 | 3 | GEMA | T465 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T601_Fire Services12.0031120964523 | DistributionFeederT601_Fire Services11630 | DistributionFeederT601_Fire Services11630 | 12.0031 | 630 | 630 | 11 kV Bus | T256 | RMU Switch-T465 | 11
DistributionFeederT602_Whey Processing11 | DistributionFeederT602_Whey ProcessingCD1-T60211- | DistributionFeeder | T602_Whey Processing | 11 kV Bus | T172 | 1 | GEMA/AEL Protection Database | CD1-T602 | Circuit Breaker | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | 7.621 | - | T602_Whey Processing7.62102355330306 | DistributionFeederT602_Whey Processing11400 | DistributionFeederT602_Whey Processing11400 | 7.621 | 400 | 400 | 11 kV Bus | T172 | Circuit Breaker-CD1-T602 | 11
DistributionFeederT602_Whey Processing11 | DistributionFeederT602_Whey Processing1-3c 185 mm² Al PILC11- | DistributionFeeder | T602_Whey Processing | 11 kV Bus | T172 | 2 | GEMA/General Cable | 1-3c 185 mm² Al PILC | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 109.5 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 3 | 0.45 | 0.84 | 239.5512 | 4.5641 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.5641 | T602_Whey Processing4.56406334355503 | DistributionFeederT602_Whey Processing11239.5512 | DistributionFeederT602_Whey Processing11239.5512 | 4.5641 | 239.5512 | 239.5512 | 11 kV Bus | T172 | Cable-1-3c 185 mm² Al PILC | 11
DistributionFeederT602_Whey Processing11 | DistributionFeederT602_Whey ProcessingT46511- | DistributionFeeder | T602_Whey Processing | 11 kV Bus | T172 | 3 | GEMA | T465 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T602_Whey Processing12.0031120964523 | DistributionFeederT602_Whey Processing11630 | DistributionFeederT602_Whey Processing11630 | 12.0031 | 630 | 630 | 11 kV Bus | T172 | RMU Switch-T465 | 11
DistributionFeederT603_Lactose Plant11 | DistributionFeederT603_Lactose PlantCD1-T60311- | DistributionFeeder | T603_Lactose Plant | 11 kV Bus | T569 | 1 | GEMA/AEL Protection Database | CD1-T603 | Circuit Breaker | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | 7.621 | - | T603_Lactose Plant7.62102355330306 | DistributionFeederT603_Lactose Plant11400 | DistributionFeederT603_Lactose Plant11400 | 7.621 | 400 | 400 | 11 kV Bus | T569 | Circuit Breaker-CD1-T603 | 11
DistributionFeederT603_Lactose Plant11 | DistributionFeederT603_Lactose Plant3-1c 400 mm² Al XLPE11- | DistributionFeeder | T603_Lactose Plant | 11 kV Bus | T569 | 2 | GEMA/General Cable | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 76.4 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.24 | 0.67 | 342.0164 | 6.5163 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 6.5163 | T603_Lactose Plant6.51628710467327 | DistributionFeederT603_Lactose Plant11342.016374 | DistributionFeederT603_Lactose Plant11342.016374 | 6.5163 | 342.0164 | 342.0164 | 11 kV Bus | T569 | Cable-3-1c 400 mm² Al XLPE | 11
DistributionFeederT603_Lactose Plant11 | DistributionFeederT603_Lactose PlantT46511- | DistributionFeeder | T603_Lactose Plant | 11 kV Bus | T569 | 3 | GEMA | T465 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T603_Lactose Plant12.0031120964523 | DistributionFeederT603_Lactose Plant11630 | DistributionFeederT603_Lactose Plant11630 | 12.0031 | 630 | 630 | 11 kV Bus | T569 | RMU Switch-T465 | 11
DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to MilfordCD1-T60511- | DistributionFeeder | T605_Tie to Milford | 11 kV Bus | T166 | 1 | GEMA/AEL Protection Database | CD1-T605 | Circuit Breaker | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 252 | 4.8012 | 252 | 4.8012 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 4.8012 | - | 7.621 | - | T605_Tie to Milford4.80124483858093 | DistributionFeederT605_Tie to Milford11252 | DistributionFeederT605_Tie to Milford11252 | 4.8012 | 252 | 252 | 11 kV Bus | T166 | Circuit Breaker-CD1-T605 | 11
DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to Milford1-3c 95 mm² Al PILC11- | DistributionFeeder | T605_Tie to Milford | 11 kV Bus | T166 | 2 | GEMA/General Cable | 1-3c 95 mm² Al PILC | Cable | - | - | 11 | 205 | 3.9058 | 205 | 3.9058 | 205 | 3.9058 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 290.3 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 122.77 | 2.3391 | 3.9058 | 3.9058 | 3.9058 | - | - | - | - | - | 2.3391 | T605_Tie to Milford2.33908246357195 | DistributionFeederT605_Tie to Milford11122.76999 | DistributionFeederT605_Tie to Milford11122.76999 | 2.3391 | 122.77 | 122.77 | 11 kV Bus | T166 | Cable-1-3c 95 mm² Al PILC | 11
DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to MilfordT16611- | DistributionFeeder | T605_Tie to Milford | 11 kV Bus | T166 | 3 | GEMA | T166 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T605_Tie to Milford | DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to Milford11 |  |  |  | 11 kV Bus | T166 | Link-T166 | 11
DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to MilfordCHAFER11- | DistributionFeeder | T605_Tie to Milford | T166 | T129 | 4 | GEMA/AEL OH Amp Calc. | CHAFER | OH Line | - | - | 11 | 524.3264 | 9.9898 | - | - | 388.1048 | 7.3944 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 51 | - | - | - | - | - | - | - | - | - | - | - | 9.9898 | - | 7.3944 | - | - | - | - | - | - | T605_Tie to Milford7.3943903990836 | DistributionFeederT605_Tie to Milford11388.104844309464 | DistributionFeederT605_Tie to Milford11388.104844309464 | 7.3944 | 388.1048 | 388.1048 | T166 | T129 | OH Line-CHAFER | 11
DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to MilfordT12911- | DistributionFeeder | T605_Tie to Milford | T166 | T129 | 5 | GEMA | T129 | ABS | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | T605_Tie to Milford | DistributionFeederT605_Tie to Milford11 | DistributionFeederT605_Tie to Milford11 |  |  |  | T166 | T129 | ABS-T129 | 11
DistributionFeederT609_Milk Reception11 | DistributionFeederT609_Milk ReceptionCD1-T60911- | DistributionFeeder | T609_Milk Reception | 11 kV Bus | T153 | 1 | GEMA/AEL Protection Database | CD1-T609 | Circuit Breaker | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | 7.621 | - | T609_Milk Reception7.62102355330306 | DistributionFeederT609_Milk Reception11400 | DistributionFeederT609_Milk Reception11400 | 7.621 | 400 | 400 | 11 kV Bus | T153 | Circuit Breaker-CD1-T609 | 11
DistributionFeederT609_Milk Reception11 | DistributionFeederT609_Milk Reception1-3c 300 mm² Al XLPE11- | DistributionFeeder | T609_Milk Reception | 11 kV Bus | T153 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 355.4 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.24 | 0.67 | 303.1654 | 5.7761 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.7761 | T609_Milk Reception5.77607572034353 | DistributionFeederT609_Milk Reception11303.165352 | DistributionFeederT609_Milk Reception11303.165352 | 5.7761 | 303.1654 | 303.1654 | 11 kV Bus | T153 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT609_Milk Reception11 | DistributionFeederT609_Milk ReceptionT15311- | DistributionFeeder | T609_Milk Reception | 11 kV Bus | T153 | 3 | GEMA | T153 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T609_Milk Reception12.0031120964523 | DistributionFeederT609_Milk Reception11630 | DistributionFeederT609_Milk Reception11630 | 12.0031 | 630 | 630 | 11 kV Bus | T153 | RMU Switch-T153 | 11
DistributionFeederT610_Chilled Water 111 | DistributionFeederT610_Chilled Water 1CD1-T61011- | DistributionFeeder | T610_Chilled Water 1 | 11 kV Bus | T249 | 1 | GEMA/AEL Protection Database | CD1-T610 | Circuit Breaker | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.069 | 9.069 | 9.069 | - | - | 9.1452 | - | 7.621 | - | T610_Chilled Water 17.62102355330306 | DistributionFeederT610_Chilled Water 111400 | DistributionFeederT610_Chilled Water 111400 | 7.621 | 400 | 400 | 11 kV Bus | T249 | Circuit Breaker-CD1-T610 | 11
DistributionFeederT610_Chilled Water 111 | DistributionFeederT610_Chilled Water 11-3c 185 mm² Al PILC11- | DistributionFeeder | T610_Chilled Water 1 | 11 kV Bus | T249 | 2 | GEMA/General Cable | 1-3c 185 mm² Al PILC | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 251.1 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 179.6634 | 3.423 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.423 | T610_Chilled Water 13.42304750766627 | DistributionFeederT610_Chilled Water 111179.6634 | DistributionFeederT610_Chilled Water 111179.6634 | 3.423 | 179.6634 | 179.6634 | 11 kV Bus | T249 | Cable-1-3c 185 mm² Al PILC | 11
DistributionFeederT610_Chilled Water 111 | DistributionFeederT610_Chilled Water 1T24911- | DistributionFeeder | T610_Chilled Water 1 | 11 kV Bus | T249 | 3 | GEMA | T249 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T610_Chilled Water 112.0031120964523 | DistributionFeederT610_Chilled Water 111630 | DistributionFeederT610_Chilled Water 111630 | 12.0031 | 630 | 630 | 11 kV Bus | T249 | RMU Switch-T249 | 11
DistributionFeederT611_Effluent Plant11 | DistributionFeederT611_Effluent PlantCD1-T61111- | DistributionFeeder | T611_Effluent Plant | 11 kV Bus | T246 | 1 | GEMA/AEL Protection Database | CD1-T611 | Circuit Breaker | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.069 | 9.069 | 9.069 | - | - | 9.1452 | - | 7.621 | - | T611_Effluent Plant7.62102355330306 | DistributionFeederT611_Effluent Plant11400 | DistributionFeederT611_Effluent Plant11400 | 7.621 | 400 | 400 | 11 kV Bus | T246 | Circuit Breaker-CD1-T611 | 11
DistributionFeederT611_Effluent Plant11 | DistributionFeederT611_Effluent Plant1-3c 185 mm² Al PILC11- | DistributionFeeder | T611_Effluent Plant | 11 kV Bus | T246 | 2 | GEMA/General Cable | 1-3c 185 mm² Al PILC | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 337.6 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 179.6634 | 3.423 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.423 | T611_Effluent Plant3.42304750766627 | DistributionFeederT611_Effluent Plant11179.6634 | DistributionFeederT611_Effluent Plant11179.6634 | 3.423 | 179.6634 | 179.6634 | 11 kV Bus | T246 | Cable-1-3c 185 mm² Al PILC | 11
DistributionFeederT611_Effluent Plant11 | DistributionFeederT611_Effluent PlantT24611- | DistributionFeeder | T611_Effluent Plant | 11 kV Bus | T246 | 3 | GEMA | T246 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T611_Effluent Plant12.0031120964523 | DistributionFeederT611_Effluent Plant11630 | DistributionFeederT611_Effluent Plant11630 | 12.0031 | 630 | 630 | 11 kV Bus | T246 | RMU Switch-T246 | 11
DistributionFeederT612_Milk Treatment11 | DistributionFeederT612_Milk TreatmentCD1-T61211- | DistributionFeeder | T612_Milk Treatment | 11 kV Bus | T139 | 1 | GEMA/AEL Protection Database | CD1-T612 | Circuit Breaker | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.069 | 9.069 | 9.069 | - | - | 9.1452 | - | 7.621 | - | T612_Milk Treatment7.62102355330306 | DistributionFeederT612_Milk Treatment11400 | DistributionFeederT612_Milk Treatment11400 | 7.621 | 400 | 400 | 11 kV Bus | T139 | Circuit Breaker-CD1-T612 | 11
DistributionFeederT612_Milk Treatment11 | DistributionFeederT612_Milk Treatment1-3c 95 mm² Al PILC11- | DistributionFeeder | T612_Milk Treatment | 11 kV Bus | T139 | 2 | GEMA/General Cable | 1-3c 95 mm² Al PILC | Cable | - | - | 11 | 205 | 3.9058 | 205 | 3.9058 | 205 | 3.9058 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 194.3 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 122.77 | 2.3391 | 3.9058 | 3.9058 | 3.9058 | - | - | - | - | - | 2.3391 | T612_Milk Treatment2.33908246357195 | DistributionFeederT612_Milk Treatment11122.76999 | DistributionFeederT612_Milk Treatment11122.76999 | 2.3391 | 122.77 | 122.77 | 11 kV Bus | T139 | Cable-1-3c 95 mm² Al PILC | 11
DistributionFeederT612_Milk Treatment11 | DistributionFeederT612_Milk TreatmentT13911- | DistributionFeeder | T612_Milk Treatment | 11 kV Bus | T139 | 3 | GEMA | T139 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T612_Milk Treatment12.0031120964523 | DistributionFeederT612_Milk Treatment11630 | DistributionFeederT612_Milk Treatment11630 | 12.0031 | 630 | 630 | 11 kV Bus | T139 | RMU Switch-T139 | 11
DistributionFeederT613_Rolleston Rd11 | DistributionFeederT613_Rolleston RdCD1-T61311- | DistributionFeeder | T613_Rolleston Rd | 11 kV Bus | T131 | 1 | GEMA/AEL Protection Database | CD1-T613 | Circuit Breaker | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | 360 | 6.8589 | 360 | 6.8589 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.069 | 9.069 | 9.069 | - | - | 6.8589 | - | 7.621 | - | T613_Rolleston Rd6.85892119797275 | DistributionFeederT613_Rolleston Rd11360 | DistributionFeederT613_Rolleston Rd11360 | 6.8589 | 360 | 360 | 11 kV Bus | T131 | Circuit Breaker-CD1-T613 | 11
DistributionFeederT613_Rolleston Rd11 | DistributionFeederT613_Rolleston Rd1-3c 185 mm² Al PILC11- | DistributionFeeder | T613_Rolleston Rd | 11 kV Bus | T131 | 2 | GEMA/General Cable | 1-3c 185 mm² Al PILC | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 239.4 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 179.6634 | 3.423 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 3.423 | T613_Rolleston Rd3.42304750766627 | DistributionFeederT613_Rolleston Rd11179.6634 | DistributionFeederT613_Rolleston Rd11179.6634 | 3.423 | 179.6634 | 179.6634 | 11 kV Bus | T131 | Cable-1-3c 185 mm² Al PILC | 11
DistributionFeederT613_Rolleston Rd11 | DistributionFeederT613_Rolleston RdT13111- | DistributionFeeder | T613_Rolleston Rd | 11 kV Bus | T131 | 3 | GEMA | T131 | ABS | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | T613_Rolleston Rd11.4315353299546 | DistributionFeederT613_Rolleston Rd11600 | DistributionFeederT613_Rolleston Rd11600 | 11.4315 | 600 | 600 | 11 kV Bus | T131 | ABS-T131 | 11
DistributionFeederT613_Rolleston Rd11 | DistributionFeederT613_Rolleston RdMINK11- | DistributionFeeder | T613_Rolleston Rd | T131 | Pole 51393 | 4 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11 | 250.5823 | 4.7742 | - | - | 188.6266 | 3.5938 | - | - | - | - | - | - | - | - | - | - | 750 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 4.7742 | - | 3.5938 | - | - | - | - | - | - | T613_Rolleston Rd3.59381954101092 | DistributionFeederT613_Rolleston Rd11188.626607220145 | DistributionFeederT613_Rolleston Rd11188.626607220145 | 3.5938 | 188.6266 | 188.6266 | T131 | Pole 51393 | OH Line-MINK | 11
DistributionFeederT614_Tie to Powder Handling11 | DistributionFeederT614_Tie to Powder HandlingCD1-T61411- | DistributionFeeder | T614_Tie to Powder Handling | 11 kV Bus | T580 | 1 | GEMA/AEL Protection Database | CD1-T614 | Circuit Breaker | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | 400 | 7.621 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 9.069 | 9.069 | 9.069 | - | - | 9.1452 | - | 7.621 | - | T614_Tie to Powder Handling7.62102355330306 | DistributionFeederT614_Tie to Powder Handling11400 | DistributionFeederT614_Tie to Powder Handling11400 | 7.621 | 400 | 400 | 11 kV Bus | T580 | Circuit Breaker-CD1-T614 | 11
DistributionFeederT614_Tie to Powder Handling11 | DistributionFeederT614_Tie to Powder Handling1-3c 300 mm² Al XLPE11- | DistributionFeeder | T614_Tie to Powder Handling | 11 kV Bus | T580 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 474.1 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 6 | 0.3 | 0.71 | 321.2648 | 6.1209 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.1209 | T614_Tie to Powder Handling6.12091606185658 | DistributionFeederT614_Tie to Powder Handling11321.264776 | DistributionFeederT614_Tie to Powder Handling11321.264776 | 6.1209 | 321.2648 | 321.2648 | 11 kV Bus | T580 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT614_Tie to Powder Handling11 | DistributionFeederT614_Tie to Powder Handling3-1c 300 mm² Al XLPE11- | DistributionFeeder | T614_Tie to Powder Handling | 11 kV Bus | T580 | 3 | GEMA/General Cable | 3-1c 300 mm² Al XLPE | Cable | - | - | 11 | 466 | 8.8785 | 466 | 8.8785 | 466 | 8.8785 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 3.1 | 1 | 0.98 | - | - | - | - | - | - | - | - | - | 8.8785 | 8.8785 | 8.8785 | - | - | - | - | - | - | T614_Tie to Powder Handling8.87849243959807 | DistributionFeederT614_Tie to Powder Handling11466 | DistributionFeederT614_Tie to Powder Handling11466 | 8.8785 | 466 | 466 | 11 kV Bus | T580 | Cable-3-1c 300 mm² Al XLPE | 11
DistributionFeederT614_Tie to Powder Handling11 | DistributionFeederT614_Tie to Powder HandlingT58011- | DistributionFeeder | T614_Tie to Powder Handling | 11 kV Bus | T580 | 4 | GEMA | T580 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T614_Tie to Powder Handling12.0031120964523 | DistributionFeederT614_Tie to Powder Handling11630 | DistributionFeederT614_Tie to Powder Handling11630 | 12.0031 | 630 | 630 | 11 kV Bus | T580 | RMU Switch-T580 | 11
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.3TMK-CB122233.594Protection | SubTransmission | CB1222_Clandeboye No.3 | 33 kV Bus | Pole 02002 | 1 | TP Branch Report TMK.FDR.1222/AEL Protection Database | TMK-CB1222 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 540 | 31.4207 | 540 | 31.4207 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 31.4207 | 104.7357 | 72.7331 | - | CB1222_Clandeboye No.331.4207180079132 | SubTransmissionCB1222_Clandeboye No.333.594540 | SubTransmissionCB1222_Clandeboye No.333.594540 | 31.4207 | 540 | 540 | 33 kV Bus | Pole 02002 | Circuit Breaker-TMK-CB1222-Protection | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.36-1c 300 mm² Al XLPE33.594- | SubTransmission | CB1222_Clandeboye No.3 | 33 kV Bus | Pole 02002 | 2 | GEMA/General Cable | 6-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 828 | 48.1784 | 828 | 48.1784 | 828 | 48.1784 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 233 | 1.1 | 0.97 | 18.5 | 0.98 | 1.2 | 1 | 4 | 0.4 | 0.75 | 590.3226 | 34.3488 | 48.1784 | 48.1784 | 48.1784 | - | - | - | - | - | 34.3488 | CB1222_Clandeboye No.334.3488147190706 | SubTransmissionCB1222_Clandeboye No.333.594590.3226 | SubTransmissionCB1222_Clandeboye No.333.594590.3226 | 34.3488 | 590.3226 | 590.3226 | 33 kV Bus | Pole 02002 | Cable-6-1c 300 mm² Al XLPE | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.3JAGUAR33.594- | SubTransmission | CB1222_Clandeboye No.3 | Pole 02002 | Pole 02049 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5804 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CB1222_Clandeboye No.333.9106986639602 | SubTransmissionCB1222_Clandeboye No.333.594582.793088112333 | SubTransmissionCB1222_Clandeboye No.333.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02002 | Pole 02049 | OH Line-JAGUAR | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.3WOLF33.594- | SubTransmission | CB1222_Clandeboye No.3 | Pole 02049 | Pole 02053 | 4 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 572.8673 | 33.3332 | - | - | 496.0602 | 28.864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 401 | - | - | - | - | - | - | - | - | - | - | - | 33.3332 | - | 28.864 | - | - | - | - | - | - | CB1222_Clandeboye No.328.8640140783565 | SubTransmissionCB1222_Clandeboye No.333.594496.060198191114 | SubTransmissionCB1222_Clandeboye No.333.594496.060198191114 | 28.864 | 496.0602 | 496.0602 | Pole 02049 | Pole 02053 | OH Line-WOLF | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.3JAGUAR33.594- | SubTransmission | CB1222_Clandeboye No.3 | Pole 02053 | Pole 02081 | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3815 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CB1222_Clandeboye No.333.9106986639602 | SubTransmissionCB1222_Clandeboye No.333.594582.793088112333 | SubTransmissionCB1222_Clandeboye No.333.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02053 | Pole 02081 | OH Line-JAGUAR | 33.594
SubTransmissionCB1222_Clandeboye No.333.594 | SubTransmissionCB1222_Clandeboye No.33-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1222_Clandeboye No.3 | Pole 02081 | CBT662 | 6 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 660 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CB1222_Clandeboye No.323.6932032106616 | SubTransmissionCB1222_Clandeboye No.333.594407.19406 | SubTransmissionCB1222_Clandeboye No.333.594407.19406 | 23.6932 | 407.1941 | 407.1941 | Pole 02081 | CBT662 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_2TMK-CB122233.594Protection | SubTransmission | CD_2 | 33 kV Bus | Pole 02002 | 1 | TP Branch Report TMK.FDR.1222/AEL Protection Database | TMK-CB1222 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 540 | 31.4207 | 540 | 31.4207 | 1800 | 104.7357 | 1250 | 72.7331 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 31.4207 | 104.7357 | 72.7331 | - | CD_231.4207180079132 | SubTransmissionCD_233.594540 | SubTransmissionCD_233.594540 | 31.4207 | 540 | 540 | 33 kV Bus | Pole 02002 | Circuit Breaker-TMK-CB1222-Protection | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_26-1c 300 mm² Al XLPE33.594- | SubTransmission | CD_2 | 33 kV Bus | Pole 02002 | 2 | GEMA/General Cable | 6-1c 300 mm² Al XLPE | Cable | - | - | 33.594 | 828 | 48.1784 | 828 | 48.1784 | 828 | 48.1784 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 233 | 1.1 | 0.97 | 18.5 | 0.98 | 1.2 | 1 | 4 | 0.4 | 0.75 | 590.3226 | 34.3488 | 48.1784 | 48.1784 | 48.1784 | - | - | - | - | - | 34.3488 | CD_234.3488147190706 | SubTransmissionCD_233.594590.3226 | SubTransmissionCD_233.594590.3226 | 34.3488 | 590.3226 | 590.3226 | 33 kV Bus | Pole 02002 | Cable-6-1c 300 mm² Al XLPE | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_2JAGUAR33.594- | SubTransmission | CD_2 | Pole 02002 | Pole 02049 | 3 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5804 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CD_233.9106986639602 | SubTransmissionCD_233.594582.793088112333 | SubTransmissionCD_233.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02002 | Pole 02049 | OH Line-JAGUAR | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_2WOLF33.594- | SubTransmission | CD_2 | Pole 02049 | Pole 02053 | 4 | GEMA/AEL OH Amp Calc. | WOLF | OH Line | - | - | 33.594 | 572.8673 | 33.3332 | - | - | 496.0602 | 28.864 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 401 | - | - | - | - | - | - | - | - | - | - | - | 33.3332 | - | 28.864 | - | - | - | - | - | - | CD_228.8640140783565 | SubTransmissionCD_233.594496.060198191114 | SubTransmissionCD_233.594496.060198191114 | 28.864 | 496.0602 | 496.0602 | Pole 02049 | Pole 02053 | OH Line-WOLF | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_2JAGUAR33.594- | SubTransmission | CD_2 | Pole 02053 | Pole 02081 | 5 | GEMA/AEL OH Amp Calc. | JAGUAR | OH Line | - | - | 33.594 | 673.2838 | 39.176 | - | - | 582.7931 | 33.9107 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3815 | - | - | - | - | - | - | - | - | - | - | - | 39.176 | - | 33.9107 | - | - | - | - | - | - | CD_233.9106986639602 | SubTransmissionCD_233.594582.793088112333 | SubTransmissionCD_233.594582.793088112333 | 33.9107 | 582.7931 | 582.7931 | Pole 02053 | Pole 02081 | OH Line-JAGUAR | 33.594
SubTransmissionCD_233.594T3 | SubTransmissionCD_23-1c 400 mm² Al XLPE33.594- | SubTransmission | CD_2 | Pole 02081 | CBT662 | 6 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 660 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CD_223.6932032106616 | SubTransmissionCD_233.594407.19406 | SubTransmissionCD_233.594407.19406 | 23.6932 | 407.1941 | 407.1941 | Pole 02081 | CBT662 | Cable-3-1c 400 mm² Al XLPE | 33.594
ZoneSubstationCD_233.594T3 | ZoneSubstationCD_2T66233.594Protection | ZoneSubstation | CD_2 | REC T662 | 11 kV Bus | 1 | GEMA/AEL Protection Database | T662 | Recloser | Relay SEL 387E | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 540 | 31.4207 | 540 | 31.4207 | - | - | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 31.4207 | - | 34.9119 | - | CD_231.4207180079132 | ZoneSubstationCD_233.594540 | ZoneSubstationCD_233.594540 | 31.4207 | 540 | 540 | REC T662 | 11 kV Bus | Recloser-T662-Protection | 33.594
ZoneSubstationCD_233.594T3 | ZoneSubstationCD_2D1462-T333.594HV Winding | ZoneSubstation | CD_2 | REC T662 | 11 kV Bus | 2 | AEL Transformers Database | D1462-T3 | Transformer | - | HV Winding | 33.594 | 429.6528 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_2 | ZoneSubstationCD_233.594 | ZoneSubstationCD_233.594429.65281686434 |  |  | 429.6528 | REC T662 | 11 kV Bus | Transformer-D1462-T3-HV Winding | 33.594
ZoneSubstationCD_211T3 | ZoneSubstationCD_2D1462-T311LV Winding | ZoneSubstation | CD_2 | REC T662 | 11 kV Bus | 3 | AEL Transformers Database | D1462-T3 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_2 | ZoneSubstationCD_211 | ZoneSubstationCD_2111312.1597027037 |  |  | 1312.1597 | REC T662 | 11 kV Bus | Transformer-D1462-T3-LV Winding | 11
ZoneSubstationCD_211T3 | ZoneSubstationCD_26-1c 630 mm² Al XLPE11- | ZoneSubstation | CD_2 | REC T662 | 11 kV Bus | 4 | GEMA/General Cable/11349-02 | 6-1c 630 mm² Al XLPE | Cable | - | - | 11 | 1620 | 30.8651 | 1620 | 30.8651 | 1620 | 30.8651 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 7 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 1 | 0 | 1 | 1582.74 | 30.1552 | 30.8651 | 30.8651 | 30.8651 | - | - | - | - | - | 30.1552 | CD_230.1552470468872 | ZoneSubstationCD_2111582.74 | ZoneSubstationCD_2111582.74 | 30.1552 | 1582.74 | 1582.74 | REC T662 | 11 kV Bus | Cable-6-1c 630 mm² Al XLPE | 11
ZoneSubstationCD_211T3 | ZoneSubstationCD_2CD2-T65711Protection | ZoneSubstation | CD_2 | REC T662 | 11 kV Bus | 5 | GEMA/AEL Protection Database | CD2-T657 | Circuit Breaker | Relay Micom-P141 | Protection | 11 | 2000 | 38.1051 | 2000 | 38.1051 | 2000 | 38.1051 | - | - | - | - | 1400 | 26.6736 | 1400 | 26.6736 | - | - | 2000 | 38.1051 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 38.1051 | 38.1051 | 38.1051 | - | - | 26.6736 | - | 38.1051 | - | CD_226.6735824365607 | ZoneSubstationCD_2111400 | ZoneSubstationCD_2111400 | 26.6736 | 1400 | 1400 | REC T662 | 11 kV Bus | Circuit Breaker-CD2-T657-Protection | 11
SubTransmissionCB1282_Clandeboye No.433.594 | SubTransmissionCB1282_Clandeboye No.4TMK-CB128233.594Protection | SubTransmission | CB1282_Clandeboye No.4 | 33 kV Bus | CBT663 | 1 | TP Branch Report TMK.FDR.1282/AEL Protection Database | TMK-CB1282 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 660 | 38.4031 | 660 | 38.4031 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 38.4031 | 104.7357 | 34.9119 | - | CB1282_Clandeboye No.434.9119088976813 | SubTransmissionCB1282_Clandeboye No.433.594600 | SubTransmissionCB1282_Clandeboye No.433.594600 | 34.9119 | 600 | 600 | 33 kV Bus | CBT663 | Circuit Breaker-TMK-CB1282-Protection | 33.594
SubTransmissionCB1282_Clandeboye No.433.594 | SubTransmissionCB1282_Clandeboye No.43-1c 400 mm² Al XLPE33.594- | SubTransmission | CB1282_Clandeboye No.4 | 33 kV Bus | CBT663 | 2 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 10825 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CB1282_Clandeboye No.423.6932032106616 | SubTransmissionCB1282_Clandeboye No.433.594407.19406 | SubTransmissionCB1282_Clandeboye No.433.594407.19406 | 23.6932 | 407.1941 | 407.1941 | 33 kV Bus | CBT663 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCB1282_Clandeboye No.433.594 | SubTransmissionCB1282_Clandeboye No.4T66333.594Protection | SubTransmission | CB1282_Clandeboye No.4 | REC T663 | 11 kV Bus | 1 | GEMA/AEL Protection Database | T663 | Recloser | Relay SEL 387E | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 540 | 31.4207 | 540 | 31.4207 | - | - | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 31.4207 | - | 34.9119 | - | CB1282_Clandeboye No.431.4207180079132 | SubTransmissionCB1282_Clandeboye No.433.594540 | SubTransmissionCB1282_Clandeboye No.433.594540 | 31.4207 | 540 | 540 | REC T663 | 11 kV Bus | Recloser-T663-Protection | 33.594
SubTransmissionCD_233.594T4 | SubTransmissionCD_2TMK-CB128233.594Protection | SubTransmission | CD_2 | 33 kV Bus | CBT663 | 1 | TP Branch Report TMK.FDR.1282/AEL Protection Database | TMK-CB1282 | Circuit Breaker | Relay SR760 | Protection | 33.594 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 630 | 36.6575 | 660 | 38.4031 | 660 | 38.4031 | 1800 | 104.7357 | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 36.6575 | 38.4031 | 104.7357 | 34.9119 | - | CD_234.9119088976813 | SubTransmissionCD_233.594600 | SubTransmissionCD_233.594600 | 34.9119 | 600 | 600 | 33 kV Bus | CBT663 | Circuit Breaker-TMK-CB1282-Protection | 33.594
SubTransmissionCD_233.594T4 | SubTransmissionCD_23-1c 400 mm² Al XLPE33.594- | SubTransmission | CD_2 | 33 kV Bus | CBT663 | 2 | GEMA/General Cable Technical | 3-1c 400 mm² Al XLPE | Cable | - | - | 33.594 | 458 | 26.6494 | 458 | 26.6494 | 458 | 26.6494 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | Yes | 10825 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 2 | 0.7 | 0.91 | 407.1941 | 23.6932 | 26.6494 | 26.6494 | 26.6494 | - | - | - | - | - | 23.6932 | CD_223.6932032106616 | SubTransmissionCD_233.594407.19406 | SubTransmissionCD_233.594407.19406 | 23.6932 | 407.1941 | 407.1941 | 33 kV Bus | CBT663 | Cable-3-1c 400 mm² Al XLPE | 33.594
SubTransmissionCD_233.594T4 | SubTransmissionCD_2T66333.594Protection | SubTransmission | CD_2 | REC T663 | 11 kV Bus | 1 | GEMA/AEL Protection Database | T663 | Recloser | Relay SEL 387E | Protection | 33.594 | 560 | 32.5844 | 560 | 32.5844 | 560 | 32.5844 | - | - | - | - | 540 | 31.4207 | 540 | 31.4207 | - | - | 600 | 34.9119 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 32.5844 | 32.5844 | 32.5844 | - | - | 31.4207 | - | 34.9119 | - | CD_231.4207180079132 | SubTransmissionCD_233.594540 | SubTransmissionCD_233.594540 | 31.4207 | 540 | 540 | REC T663 | 11 kV Bus | Recloser-T663-Protection | 33.594
ZoneSubstationCD_233.594T4 | ZoneSubstationCD_2D1462-T433.594HV Winding | ZoneSubstation | CD_2 | REC T663 | 11 kV Bus | 2 | AEL Transformers Database | D1462-T4 | Transformer | - | HV Winding | 33.594 | 429.6528 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_2 | ZoneSubstationCD_233.594 | ZoneSubstationCD_233.594429.65281686434 |  |  | 429.6528 | REC T663 | 11 kV Bus | Transformer-D1462-T4-HV Winding | 33.594
ZoneSubstationCD_211T4 | ZoneSubstationCD_2D1462-T411LV Winding | ZoneSubstation | CD_2 | REC T663 | 11 kV Bus | 3 | AEL Transformers Database | D1462-T4 | Transformer | - | LV Winding | 11 | 1312.1597 | 25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CD_2 | ZoneSubstationCD_211 | ZoneSubstationCD_2111312.1597027037 |  |  | 1312.1597 | REC T663 | 11 kV Bus | Transformer-D1462-T4-LV Winding | 11
ZoneSubstationCD_211T4 | ZoneSubstationCD_26-1c 630 mm² Al XLPE11- | ZoneSubstation | CD_2 | REC T663 | 11 kV Bus | 4 | GEMA/General Cable/11349-02 | 6-1c 630 mm² Al XLPE | Cable | - | - | 11 | 1620 | 30.8651 | 1620 | 30.8651 | 1620 | 30.8651 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 7 | 0.8 | 1 | 19 | 0.977 | 1.2 | 1 | 1 | 0 | 1 | 1582.74 | 30.1552 | 30.8651 | 30.8651 | 30.8651 | - | - | - | - | - | 30.1552 | CD_230.1552470468872 | ZoneSubstationCD_2111582.74 | ZoneSubstationCD_2111582.74 | 30.1552 | 1582.74 | 1582.74 | REC T663 | 11 kV Bus | Cable-6-1c 630 mm² Al XLPE | 11
ZoneSubstationCD_211T4 | ZoneSubstationCD_2CD2-T65511Protection | ZoneSubstation | CD_2 | REC T663 | 11 kV Bus | 5 | GEMA/AEL Protection Database | CD2-T655 | Circuit Breaker | Relay Micom-P141 | Protection | 11 | 2000 | 38.1051 | 2000 | 38.1051 | 2000 | 38.1051 | - | - | - | - | 1600 | 30.4841 | 1400 | 26.6736 | - | - | 2000 | 38.1051 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 38.1051 | 38.1051 | 38.1051 | - | - | 30.4841 | - | 38.1051 | - | CD_230.4840942132122 | ZoneSubstationCD_2111600 | ZoneSubstationCD_2111400 | 30.4841 | 1600 | 1400 | REC T663 | 11 kV Bus | Circuit Breaker-CD2-T655-Protection | 11
DistributionFeederT650_Tie to Milk Powder 111 | DistributionFeederT650_Tie to Milk Powder 1CD2-T65011Protection | DistributionFeeder | T650_Tie to Milk Powder 1 | 11 kV Bus | T278 | 1 | GEMA/AEL Protection Database | CD2-T650 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | - | DistributionFeederT650_Tie to Milk Powder 111480 | DistributionFeederT650_Tie to Milk Powder 111480 | 9.1452 | 480 | 480 | - | - | - | -
DistributionFeederT650_Tie to Milk Powder 111 | DistributionFeederT650_Tie to Milk Powder 11-3c 300 mm² Al XLPE11- | DistributionFeeder | T650_Tie to Milk Powder 1 | 11 kV Bus | T278 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 166.8 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 285.0659 | 5.4312 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.4312 | T650_Tie to Milk Powder 15.43123537883049 | DistributionFeederT650_Tie to Milk Powder 111285.065928 | DistributionFeederT650_Tie to Milk Powder 111285.065928 | 5.4312 | 285.0659 | 285.0659 | 11 kV Bus | T278 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT650_Tie to Milk Powder 111 | DistributionFeederT650_Tie to Milk Powder 1T27811- | DistributionFeeder | T650_Tie to Milk Powder 1 | 11 kV Bus | T278 | 3 | GEMA | T278 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T650_Tie to Milk Powder 112.0031120964523 | DistributionFeederT650_Tie to Milk Powder 111630 | DistributionFeederT650_Tie to Milk Powder 111630 | 12.0031 | 630 | 630 | 11 kV Bus | T278 | RMU Switch-T278 | 11
DistributionFeederT651_Milk Powder 311 | DistributionFeederT651_Milk Powder 3CD2-T65111Protection | DistributionFeeder | T651_Milk Powder 3 | 11 kV Bus | T364 | 1 | GEMA/AEL Protection Database | CD2-T651 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T651_Milk Powder 39.14522826396367 | DistributionFeederT651_Milk Powder 311480 | DistributionFeederT651_Milk Powder 311480 | 9.1452 | 480 | 480 | 11 kV Bus | T364 | Circuit Breaker-CD2-T651-Protection | 11
DistributionFeederT651_Milk Powder 311 | DistributionFeederT651_Milk Powder 31-3c 300 mm² Al XLPE11- | DistributionFeeder | T651_Milk Powder 3 | 11 kV Bus | T364 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 70.4 | 1 | 0.98 | 20 | 0.97 | 1.2 | 1 | 5 | 0.3 | 0.73 | 330.3145 | 6.2933 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.2933 | T651_Milk Powder 36.2933362326131 | DistributionFeederT651_Milk Powder 311330.314488 | DistributionFeederT651_Milk Powder 311330.314488 | 6.2933 | 330.3145 | 330.3145 | 11 kV Bus | T364 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT651_Milk Powder 311 | DistributionFeederT651_Milk Powder 3T36411- | DistributionFeeder | T651_Milk Powder 3 | 11 kV Bus | T364 | 3 | GEMA | T364 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T651_Milk Powder 312.0031120964523 | DistributionFeederT651_Milk Powder 311630 | DistributionFeederT651_Milk Powder 311630 | 12.0031 | 630 | 630 | 11 kV Bus | T364 | RMU Switch-T364 | 11
DistributionFeederT652_Tie to WPC11 | DistributionFeederT652_Tie to WPCCD2-T65211Protection | DistributionFeeder | T652_Tie to WPC | 11 kV Bus | T379 | 1 | GEMA/AEL Protection Database | CD2-T652 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 1200 | 22.8631 | 1200 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 22.8631 | - | - | - | T652_Tie to WPC12.0031120964523 | DistributionFeederT652_Tie to WPC11630 | DistributionFeederT652_Tie to WPC11630 | 12.0031 | 630 | 630 | 11 kV Bus | T379 | Circuit Breaker-CD2-T652-Protection | 11
DistributionFeederT652_Tie to WPC11 | DistributionFeederT652_Tie to WPC1-3c 185 mm² XLPE11- | DistributionFeeder | T652_Tie to WPC | 11 kV Bus | T379 | 2 | GEMA/General Cable | 1-3c 185 mm² XLPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 256.6 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 219.7882 | 4.1875 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 4.1875 | T652_Tie to WPC4.18752811771174 | DistributionFeederT652_Tie to WPC11219.788226 | DistributionFeederT652_Tie to WPC11219.788226 | 4.1875 | 219.7882 | 219.7882 | 11 kV Bus | T379 | Cable-1-3c 185 mm² XLPE | 11
DistributionFeederT652_Tie to WPC11 | DistributionFeederT652_Tie to WPC1-3c 185 mm² Al PILC11- | DistributionFeeder | T652_Tie to WPC | 11 kV Bus | T379 | 3 | GEMA/General Cable | 1-3c 185 mm² Al PILC | Cable | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 131.5 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 2 | 0.15 | 0.85 | 242.403 | 4.6184 | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | 4.6184 | T652_Tie to WPC4.6183974309783 | DistributionFeederT652_Tie to WPC11242.403 | DistributionFeederT652_Tie to WPC11242.403 | 4.6184 | 242.403 | 242.403 | 11 kV Bus | T379 | Cable-1-3c 185 mm² Al PILC | 11
DistributionFeederT652_Tie to WPC11 | DistributionFeederT652_Tie to WPCT37911- | DistributionFeeder | T652_Tie to WPC | 11 kV Bus | T379 | 4 | GEMA | T379 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T652_Tie to WPC12.0031120964523 | DistributionFeederT652_Tie to WPC11630 | DistributionFeederT652_Tie to WPC11630 | 12.0031 | 630 | 630 | 11 kV Bus | T379 | RMU Switch-T379 | 11
DistributionFeederT653_Chilled Water 311 | DistributionFeederT653_Chilled Water 3CD2-T65311Protection | DistributionFeeder | T653_Chilled Water 3 | 11 kV Bus | T373 | 1 | GEMA/AEL Protection Database | CD2-T653 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T653_Chilled Water 39.14522826396367 | DistributionFeederT653_Chilled Water 311480 | DistributionFeederT653_Chilled Water 311480 | 9.1452 | 480 | 480 | 11 kV Bus | T373 | Circuit Breaker-CD2-T653-Protection | 11
DistributionFeederT653_Chilled Water 311 | DistributionFeederT653_Chilled Water 31-3c 300 mm² Al XLPE11- | DistributionFeeder | T653_Chilled Water 3 | 11 kV Bus | T373 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 62.1 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 4 | 0.15 | 0.7 | 316.7399 | 6.0347 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 6.0347 | T653_Chilled Water 36.03470597647832 | DistributionFeederT653_Chilled Water 311316.73992 | DistributionFeederT653_Chilled Water 311316.73992 | 6.0347 | 316.7399 | 316.7399 | 11 kV Bus | T373 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT653_Chilled Water 311 | DistributionFeederT653_Chilled Water 3T37311- | DistributionFeeder | T653_Chilled Water 3 | 11 kV Bus | T373 | 3 | GEMA | T373 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T653_Chilled Water 312.0031120964523 | DistributionFeederT653_Chilled Water 311630 | DistributionFeederT653_Chilled Water 311630 | 12.0031 | 630 | 630 | 11 kV Bus | T373 | RMU Switch-T373 | 11
DistributionFeederT654_Tie to Boiler House11 | DistributionFeederT654_Tie to Boiler HouseCD2-T65411Protection | DistributionFeeder | T654_Tie to Boiler House | 11 kV Bus | T670 | 1 | GEMA/AEL Protection Database | CD2-T654 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T654_Tie to Boiler House9.14522826396367 | DistributionFeederT654_Tie to Boiler House11480 | DistributionFeederT654_Tie to Boiler House11480 | 9.1452 | 480 | 480 | 11 kV Bus | T670 | Circuit Breaker-CD2-T654-Protection | 11
DistributionFeederT654_Tie to Boiler House11 | DistributionFeederT654_Tie to Boiler House1-3c 300 mm² Al XLPE11- | DistributionFeeder | T654_Tie to Boiler House | 11 kV Bus | T670 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 417 | 7.9449 | 417 | 7.9449 | 417 | 7.9449 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 232.1 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 4 | 0.15 | 0.78 | 309.1922 | 5.8909 | 7.9449 | 7.9449 | 7.9449 | - | - | - | - | - | 5.8909 | T654_Tie to Boiler House5.89090175843138 | DistributionFeederT654_Tie to Boiler House11309.192156 | DistributionFeederT654_Tie to Boiler House11309.192156 | 5.8909 | 309.1922 | 309.1922 | 11 kV Bus | T670 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT654_Tie to Boiler House11 | DistributionFeederT654_Tie to Boiler House3-1c 400 mm² Al XLPE11- | DistributionFeeder | T654_Tie to Boiler House | 11 kV Bus | T670 | 3 | GEMA/General Cable | 3-1c 400 mm² Al XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 6.9 | 1 | 0.97 | 19 | 0.97 | 1.2 | 1 | 2 | 0.15 | 0.81 | 409.2633 | 7.7975 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 7.7975 | T654_Tie to Boiler House7.79751260758725 | DistributionFeederT654_Tie to Boiler House11409.263273 | DistributionFeederT654_Tie to Boiler House11409.263273 | 7.7975 | 409.2633 | 409.2633 | 11 kV Bus | T670 | Cable-3-1c 400 mm² Al XLPE | 11
DistributionFeederT654_Tie to Boiler House11 | DistributionFeederT654_Tie to Boiler HouseT67011- | DistributionFeeder | T654_Tie to Boiler House | 11 kV Bus | T670 | 4 | GEMA | T670 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T654_Tie to Boiler House12.0031120964523 | DistributionFeederT654_Tie to Boiler House11630 | DistributionFeederT654_Tie to Boiler House11630 | 12.0031 | 630 | 630 | 11 kV Bus | T670 | RMU Switch-T670 | 11
DistributionFeederT658_Milk Powder 211 | DistributionFeederT658_Milk Powder 2CD2-T65811Protection | DistributionFeeder | T658_Milk Powder 2 | 11 kV Bus | T482 | 1 | GEMA/AEL Protection Database | CD2-T658 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T658_Milk Powder 29.14522826396367 | DistributionFeederT658_Milk Powder 211480 | DistributionFeederT658_Milk Powder 211480 | 9.1452 | 480 | 480 | 11 kV Bus | T482 | Circuit Breaker-CD2-T658-Protection | 11
DistributionFeederT658_Milk Powder 211 | DistributionFeederT658_Milk Powder 21-3c 300 mm² Al XLPE11- | DistributionFeeder | T658_Milk Powder 2 | 11 kV Bus | T482 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 196.7 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 285.0659 | 5.4312 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.4312 | T658_Milk Powder 25.43123537883049 | DistributionFeederT658_Milk Powder 211285.065928 | DistributionFeederT658_Milk Powder 211285.065928 | 5.4312 | 285.0659 | 285.0659 | 11 kV Bus | T482 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT658_Milk Powder 211 | DistributionFeederT658_Milk Powder 2T48211- | DistributionFeeder | T658_Milk Powder 2 | 11 kV Bus | T482 | 3 | GEMA | T482 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T658_Milk Powder 212.0031120964523 | DistributionFeederT658_Milk Powder 211630 | DistributionFeederT658_Milk Powder 211630 | 12.0031 | 630 | 630 | 11 kV Bus | T482 | RMU Switch-T482 | 11
DistributionFeederT659_Tie to Energy Centre 111 | DistributionFeederT659_Tie to Energy Centre 1CD2-T65911Protection | DistributionFeeder | T659_Tie to Energy Centre 1 | 11 kV Bus | T383 | 1 | GEMA/AEL Protection Database | CD2-T659 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T659_Tie to Energy Centre 19.14522826396367 | DistributionFeederT659_Tie to Energy Centre 111480 | DistributionFeederT659_Tie to Energy Centre 111480 | 9.1452 | 480 | 480 | 11 kV Bus | T383 | Circuit Breaker-CD2-T659-Protection | 11
DistributionFeederT659_Tie to Energy Centre 111 | DistributionFeederT659_Tie to Energy Centre 11-3c 300 mm² Al XLPE11- | DistributionFeeder | T659_Tie to Energy Centre 1 | 11 kV Bus | T383 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 417 | 7.9449 | 417 | 7.9449 | 417 | 7.9449 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | Yes | 548.6 | 1.1 | 0.97 | 19 | 0.97 | 1.2 | 1 | 4 | 0.15 | 0.78 | 306.0371 | 5.8308 | 7.9449 | 7.9449 | 7.9449 | - | - | - | - | - | 5.8308 | T659_Tie to Energy Centre 15.83079051599841 | DistributionFeederT659_Tie to Energy Centre 111306.037134 | DistributionFeederT659_Tie to Energy Centre 111306.037134 | 5.8308 | 306.0371 | 306.0371 | 11 kV Bus | T383 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT659_Tie to Energy Centre 111 | DistributionFeederT659_Tie to Energy Centre 1T38311- | DistributionFeeder | T659_Tie to Energy Centre 1 | 11 kV Bus | T383 | 3 | GEMA | T383 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T659_Tie to Energy Centre 112.0031120964523 | DistributionFeederT659_Tie to Energy Centre 111630 | DistributionFeederT659_Tie to Energy Centre 111630 | 12.0031 | 630 | 630 | 11 kV Bus | T383 | RMU Switch-T383 | 11
DistributionFeederT660_Refrigeration11 | DistributionFeederT660_RefrigerationCD2-T66011Protection | DistributionFeeder | T660_Refrigeration | 11 kV Bus | T338 | 1 | GEMA/AEL Protection Database | CD2-T660 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T660_Refrigeration9.14522826396367 | DistributionFeederT660_Refrigeration11480 | DistributionFeederT660_Refrigeration11480 | 9.1452 | 480 | 480 | 11 kV Bus | T338 | Circuit Breaker-CD2-T660-Protection | 11
DistributionFeederT660_Refrigeration11 | DistributionFeederT660_Refrigeration1-3c 300 mm² Al XLPE11- | DistributionFeeder | T660_Refrigeration | 11 kV Bus | T338 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 507.2 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 285.0659 | 5.4312 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.4312 | T660_Refrigeration5.43123537883049 | DistributionFeederT660_Refrigeration11285.065928 | DistributionFeederT660_Refrigeration11285.065928 | 5.4312 | 285.0659 | 285.0659 | 11 kV Bus | T338 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT660_Refrigeration11 | DistributionFeederT660_RefrigerationT33811- | DistributionFeeder | T660_Refrigeration | 11 kV Bus | T338 | 3 | GEMA | T338 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T660_Refrigeration12.0031120964523 | DistributionFeederT660_Refrigeration11630 | DistributionFeederT660_Refrigeration11630 | 12.0031 | 630 | 630 | 11 kV Bus | T338 | RMU Switch-T338 | 11
DistributionFeederT661_Laboratory11 | DistributionFeederT661_LaboratoryCD2-T66111Protection | DistributionFeeder | T661_Laboratory | 11 kV Bus | T182 | 1 | GEMA/AEL Protection Database | CD2-T661 | Circuit Breaker | Relay Micom-P122 | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 480 | 9.1452 | 480 | 9.1452 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 9.1452 | - | - | - | T661_Laboratory9.14522826396367 | DistributionFeederT661_Laboratory11480 | DistributionFeederT661_Laboratory11480 | 9.1452 | 480 | 480 | 11 kV Bus | T182 | Circuit Breaker-CD2-T661-Protection | 11
DistributionFeederT661_Laboratory11 | DistributionFeederT661_Laboratory1-3c 300 mm² Al XLPE11- | DistributionFeeder | T661_Laboratory | 11 kV Bus | T182 | 2 | GEMA/General Cable | 1-3c 300 mm² Al XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 169.7 | 1 | 0.98 | 19 | 0.97 | 1.2 | 1 | 6 | 0.15 | 0.63 | 285.0659 | 5.4312 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 5.4312 | T661_Laboratory5.43123537883049 | DistributionFeederT661_Laboratory11285.065928 | DistributionFeederT661_Laboratory11285.065928 | 5.4312 | 285.0659 | 285.0659 | 11 kV Bus | T182 | Cable-1-3c 300 mm² Al XLPE | 11
DistributionFeederT661_Laboratory11 | DistributionFeederT661_LaboratoryT18211- | DistributionFeeder | T661_Laboratory | 11 kV Bus | T182 | 3 | GEMA | T182 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | T661_Laboratory12.0031120964523 | DistributionFeederT661_Laboratory11630 | DistributionFeederT661_Laboratory11630 | 12.0031 | 630 | 630 | 11 kV Bus | T182 | RMU Switch-T182 | 11
DistributionFeederCB2_Mozz3_111 | DistributionFeederCB2_Mozz3_1CD2-CB211Protection | DistributionFeeder | CB2_Mozz3_1 | 11 kV Bus | T708 | 1 | GEMA/AEL Protection Database | CD2-CB2 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 11.4315 | - | - | - | CB2_Mozz3_111.4315353299546 | DistributionFeederCB2_Mozz3_111600 | DistributionFeederCB2_Mozz3_111600 | 11.4315 | 600 | 600 | 11 kV Bus | T708 | Circuit Breaker-CD2-CB2-Protection | 11
DistributionFeederCB2_Mozz3_111 | DistributionFeederCB2_Mozz3_13-1c 400 mm² Cu XLPE11- | DistributionFeeder | CB2_Mozz3_1 | 11 kV Bus | T708 | 2 | GEMA/General Cable | 3-1c 400 mm² Cu XLPE | Cable | - | - | 11 | 662 | 12.6128 | 662 | 12.6128 | 662 | 12.6128 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.6128 | 12.6128 | 12.6128 | - | - | - | - | - | - | CB2_Mozz3_112.6127939807166 | DistributionFeederCB2_Mozz3_111662 | DistributionFeederCB2_Mozz3_111662 | 12.6128 | 662 | 662 | 11 kV Bus | T708 | Cable-3-1c 400 mm² Cu XLPE | 11
DistributionFeederCB2_Mozz3_111 | DistributionFeederCB2_Mozz3_1T70811- | DistributionFeeder | CB2_Mozz3_1 | 11 kV Bus | T708 | 3 | GEMA | T708 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB2_Mozz3_112.0031120964523 | DistributionFeederCB2_Mozz3_111630 | DistributionFeederCB2_Mozz3_111630 | 12.0031 | 630 | 630 | 11 kV Bus | T708 | RMU Switch-T708 | 11
DistributionFeederCB15_Mozz3_211 | DistributionFeederCB15_Mozz3_2CD2-CB1511Protection | DistributionFeeder | CB15_Mozz3_2 | 11 kV Bus | T737 | 1 | GEMA/AEL Protection Database | CD2-CB15 | Circuit Breaker | Relay SEL 751A | Protection | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | 11.4315 | - | - | - | CB15_Mozz3_211.4315353299546 | DistributionFeederCB15_Mozz3_211600 | DistributionFeederCB15_Mozz3_211600 | 11.4315 | 600 | 600 | 11 kV Bus | T737 | Circuit Breaker-CD2-CB15-Protection | 11
DistributionFeederCB15_Mozz3_211 | DistributionFeederCB15_Mozz3_23-1c 400 mm² Cu XLPE11- | DistributionFeeder | CB15_Mozz3_2 | 11 kV Bus | T737 | 2 | GEMA/General Cable | 3-1c 400 mm² Cu XLPE | Cable | - | - | 11 | 662 | 12.6128 | 662 | 12.6128 | 662 | 12.6128 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.6128 | 12.6128 | 12.6128 | - | - | - | - | - | - | CB15_Mozz3_212.6127939807166 | DistributionFeederCB15_Mozz3_211662 | DistributionFeederCB15_Mozz3_211662 | 12.6128 | 662 | 662 | 11 kV Bus | T737 | Cable-3-1c 400 mm² Cu XLPE | 11
DistributionFeederCB15_Mozz3_211 | DistributionFeederCB15_Mozz3_2T73711- | DistributionFeeder | CB15_Mozz3_2 | 11 kV Bus | T737 | 3 | GEMA | T737 | RMU Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | CB15_Mozz3_212.0031120964523 | DistributionFeederCB15_Mozz3_211630 | DistributionFeederCB15_Mozz3_211630 | 12.0031 | 630 | 630 | 11 kV Bus | T737 | RMU Switch-T737 | 11
[13 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3.9058 | 3.7248 | 3.3533 | 36.6575 | 36.6575 | #N/A | 38.2956 | 7.621 | 2.3391 | - | - |  | 2.3391 | - |  | - | - | - | -
Note on D38: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D39: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D40: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D41: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D100: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D101: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D102: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D103: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D171: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D172: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D173: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D174: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N174: Author: Based on 50°C design
Note on R174: Author: Based on 50°C design
Note on D175: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N175: Author: Based on 50°C design
Note on R175: Author: Based on 50°C design
Note on D176: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N176: Author: Based on 50°C design
Note on R176: Author: Based on 50°C design
Note on D177: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D178: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D179: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N179: Author: Based on 50°C design
Note on R179: Author: Based on 50°C design
Note on D180: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N180: Author: Based on 50°C design
Note on R180: Author: Based on 50°C design
Note on D181: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N181: Author: Based on 50°C design
Note on R181: Author: Based on 50°C design
Note on D182: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D183: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N183: Author: Based on 50°C design
Note on R183: Author: Based on 50°C design
Note on N187: Author: Based on 50°C design
Note on R187: Author: Based on 50°C design
Note on N188: Author: Based on 50°C design
Note on R188: Author: Based on 50°C design
Note on N189: Author: Based on 50°C design
Note on R189: Author: Based on 50°C design
Note on N192: Author: Based on 50°C design
Note on R192: Author: Based on 50°C design
Note on N193: Author: Based on 50°C design
Note on R193: Author: Based on 50°C design
Note on N194: Author: Based on 50°C design
Note on R194: Author: Based on 50°C design
Note on N196: Author: Based on 50°C design
Note on R196: Author: Based on 50°C design
Note on AQ202: Author: derating for one crossing with 1x11 kv and 1x0.415 kV cables
Note on N207: Author: Based on 50°C design
Note on R207: Author: Based on 50°C design
Note on N212: Author: Based on 50°C design
Note on R212: Author: Based on 50°C design
Note on N216: Author: Based on 50°C design
Note on R216: Author: Based on 50°C design
Note on N218: Author: Based on 50°C design
Note on R218: Author: Based on 50°C design
Note on D223: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D224: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N224: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P224: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R224: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on D225: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N225: Author: Based on 75°C design
Note on R225: Author: Based on 75°C design
Note on N227: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P227: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R227: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on N228: Author: Based on 75°C design
Note on R228: Author: Based on 75°C design
Note on D235: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D236: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D237: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N237: Author: Based on 75°C design
Note on R237: Author: Based on 75°C design
Note on D238: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N238: Author: Based on 75°C design
Note on R238: Author: Based on 75°C design
Note on N241: Author: Based on 75°C design
Note on R241: Author: Based on 75°C design
Note on N242: Author: Based on 75°C design
Note on R242: Author: Based on 75°C design
Note on N243: Author: Based on 75°C design
Note on R243: Author: Based on 75°C design
Note on N265: Author: Based on 50°C design
Note on R265: Author: Based on 50°C design
Note on N282: Author: Based on 50°C design
Note on R282: Author: Based on 50°C design
Note on D287: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D288: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D289: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N289: Author: Based on 75°C design
Note on R289: Author: Based on 75°C design
Note on D290: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N290: Author: Based on 75°C design
Note on R290: Author: Based on 75°C design
Note on D291: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N291: Author: Based on 75°C design
Note on R291: Author: Based on 75°C design
Note on D292: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N292: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P292: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R292: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on N295: Author: Based on 75°C design
Note on R295: Author: Based on 75°C design
Note on N296: Author: Based on 75°C design
Note on R296: Author: Based on 75°C design
Note on N297: Author: Based on 75°C design
Note on R297: Author: Based on 75°C design
Note on N298: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P298: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R298: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on N299: Author: Ivan to provide ratings
Note on D304: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on D305: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N305: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P305: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R305: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on D306: Author: Branches duplicated with their respective zone substations as their ratings affect both supply levels
Note on N306: Author: Ivan to provide ratings
Note on N308: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on P308: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on R308: Author: Based on conditions outlines in \\nsldc01\vol1\Engineers\PlanningTeam\100_Projects\2016-007_NDPlanning\2016_NDP_TMK\Clandeboye\Clandeboye2\1Core 400mm Al Xlpe 11kV cable Sept 2016
Note on N309: Author: Ivan to provide ratings

## TWZ_Region
SCADA Reference | SCADA Reference | Supply | Station/ | Section |  |  |  | Equipment |  | Device |  | Operating | Continuous Rating | [5 empty] | 24 Hour Post Contingency |  |  |  | Protection Limit | [7 empty] | Cable Derating Factors | [13 empty] | Rating Summary
Take CB into | Protection | Level | DistributionFeeder | From | To | Order | Source of | ID | Type | ID | Type | Voltage | Winter |  | Shoulder |  | Summer |  | Winter |  | Summer |  | Forward |  | Reverse |  | Relay Thermal |  | CT Thermal |  | Core | In Duct | Distance | Depth |  | Soil Temp |  | Soil Thermal R. |  | Mutual Heating |  |  | Derated Rating |  | Continuous Rating |  |  | Post Contingency |  | Protection Limit |  |  | Cable Derating | ID | SCADA ID | SCADA ID | Lowest Rating |  |  | From | To | Equipment | Voltage (kV)
Account | Account | [5 empty] | Data |  |  |  |  | (kV) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (A) | (MVA) | (#) | - | (m) | (m) | Factor | (°C) | Factor | (°C.m/W) | Factor | Ccts (#) | Spacing (m) | Factor | (A) | (MVA) | Winter | Shoulder | Summer | Winter | Summer | Forward | Relay | CT |  | Rating | Rating | Rating | MVA | A | A
Load Capability Reference | OC Protection Reference | Supply Level | Station/Feeder | From | To | Order | Source of Data | Equipment ID | Equipment Type | Device ID | Device type | Voltage | Cont Winter A | Cont Winter MVA | Cont Shoulder A | Cont Shoulder MVA | Cont Summer A | Cont Summer MVA | 24 Hr Winter A | 24 Hr Winter MVA | 24 Hr Summer A | 24 Hr Summer MVA | Forward A | Forwards MVA | Reverse A | Reverse MVA | Relay A | Relay MVA | CT A | CT MVA | Core | In Duct | Distance | Depth m | Depth Factor | Soil Temp C | Soil Temp Factor | Soil TR °C.m/W | Soil TR Factor | Ccts | Spacing | Mutual Heat Factor | Derating A | Derating MVA | Summ Cont Winter A | Summ Cont Shoulder MVA | Summ Cont Summer A | Summ Post Winter A | Summ Post Summer A | Summ Forward A | Summ Reverse A | Summ CT A | Cable Derating | ID Rating | Limiting Equipment Reference-No PTX | Limiting Equipment Reference-PTX | Lowest MVA | Lowest A-No PTX | Lowest A-PTX | Summ From | Summ To | Summ Equipment | Summ Voltage
GXPTWZ_GXP220 | GXPTWZ_GXPDS2494220Disconnector | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 1 | TP Branch Report TWZ.TF.T18 | DS2494 | Disconnector | TWZ-DS-2494 | Disconnector | 220 | 1200 | 457.2614 | 1200 | 457.2614 | 1200 | 457.2614 | - | - | 1200 | 457.2614 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 457.2614 | 457.2614 | 457.2614 | - | 457.2614 | - | - | - | - | TWZ_GXP457.261413198184 | GXPTWZ_GXP2201200 | GXPTWZ_GXP2201200 | 457.2614 | 1200 | 1200 | 220 kV Bus | 33 kV Bus | Disconnector-DS2494-Disconnector | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Circuit Breaker | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | TWZ-CB-2492 | Circuit Breaker | 220 | 4000 | 1524.2047 | 4000 | 1524.2047 | 4000 | 1524.2047 | - | - | 4000 | 1524.2047 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1524.2047 | 1524.2047 | 1524.2047 | - | 1524.2047 | - | - | - | - | TWZ_GXP1524.20471066061 | GXPTWZ_GXP2204000 | GXPTWZ_GXP2204000 | 1524.2047 | 4000 | 4000 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Circuit Breaker | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | TWZ-CT-CT2492 | Current Transformer | 220 | 2500 | 952.6279 | 2500 | 952.6279 | 2500 | 952.6279 | - | - | 2500 | 952.6279 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 952.6279 | 952.6279 | 952.6279 | - | 952.6279 | - | - | - | - | TWZ_GXP952.627944162882 | GXPTWZ_GXP2202500 | GXPTWZ_GXP2202500 | 952.6279 | 2500 | 2500 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Current Transformer | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | TWZ-CT-CT2492 | Current Transformer | 220 | 2500 | 952.6279 | 2500 | 952.6279 | 2500 | 952.6279 | - | - | 2500 | 952.6279 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 952.6279 | 952.6279 | 952.6279 | - | 952.6279 | - | - | - | - | TWZ_GXP952.627944162882 | GXPTWZ_GXP2202500 | GXPTWZ_GXP2202500 | 952.6279 | 2500 | 2500 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Current Transformer | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | TWZ-CT-CT2492 | Current Transformer | 220 | 2500 | 952.6279 | 2500 | 952.6279 | 2500 | 952.6279 | - | - | 2500 | 952.6279 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 952.6279 | 952.6279 | 952.6279 | - | 952.6279 | - | - | - | - | TWZ_GXP952.627944162882 | GXPTWZ_GXP2202500 | GXPTWZ_GXP2202500 | 952.6279 | 2500 | 2500 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Current Transformer | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Protection | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | Relay SEL 351S | Protection | 220 | - | - | - | - | - | - | - | - | - | - | 114 | 43.4398 | 114 | 43.4398 | 1500 | 571.5768 | 1000 | 381.0512 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 43.4398 | 571.5768 | 381.0512 | - | TWZ_GXP43.4398342538274 | GXPTWZ_GXP220114 | GXPTWZ_GXP220114 | 43.4398 | 114 | 114 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Protection | 220
GXPTWZ_GXP220 | GXPTWZ_GXPTWZ-CB2492220Protection | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 2 | TP Branch Report TWZ.TF.T18 | TWZ-CB2492 | Circuit Breaker | Relay SR745 | Protection | 220 | - | - | - | - | - | - | - | - | - | - | 115 | 43.8209 | 115 | 43.8209 | 600 | 228.6307 | 400 | 152.4205 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 43.8209 | 228.6307 | 152.4205 | - | TWZ_GXP43.8208854314926 | GXPTWZ_GXP220115 | GXPTWZ_GXP220115 | 43.8209 | 115 | 115 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB2492-Protection | 220
GXPTWZ_GXP220 | GXPTWZ_GXPT18220Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 220 | 630 | 240.0622 | 630 | 240.0622 | 630 | 240.0622 | - | - | 756 | 288.0747 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 240.0622 | 240.0622 | 240.0622 | - | 288.0747 | - | - | - | - | TWZ_GXP240.062241929046 | GXPTWZ_GXP220630 | GXPTWZ_GXP220630 | 240.0622 | 630 | 630 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 220
GXPTWZ_GXP220 | GXPTWZ_GXPT18220Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 220 | 630 | 240.0622 | 630 | 240.0622 | 630 | 240.0622 | - | - | 756 | 288.0747 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 240.0622 | 240.0622 | 240.0622 | - | 288.0747 | - | - | - | - | TWZ_GXP240.062241929046 | GXPTWZ_GXP220630 | GXPTWZ_GXP220630 | 240.0622 | 630 | 630 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 220
GXPTWZ_GXP220 | GXPTWZ_GXPT18220Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 220 | 630 | 240.0622 | 630 | 240.0622 | 630 | 240.0622 | - | - | 756 | 288.0747 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 240.0622 | 240.0622 | 240.0622 | - | 288.0747 | - | - | - | - | TWZ_GXP240.062241929046 | GXPTWZ_GXP220630 | GXPTWZ_GXP220630 | 240.0622 | 630 | 630 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 220
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 960 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 54.8714 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 33
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 960 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 54.8714 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 33
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 960 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 54.8714 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 33
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Bushings | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Bushings | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 960 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 54.8714 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Transformer-T18-Bushings | 33
GXPTWZ_GXP220 | GXPTWZ_GXPT18220HV Winding | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | HV Winding | 220 | 52 | 19.8147 | 52 | 19.8147 | 52 | 19.8147 | 72 | 27.4357 | 68 | 25.9115 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 27.4357 | 25.9115 | - | - | - | - | TWZ_GXP25.9114800812304 | GXPTWZ_GXP22068 | GXPTWZ_GXP22052 | 25.9115 | 68 | 52 | 220 kV Bus | 33 kV Bus | Transformer-T18-HV Winding | 220
GXPTWZ_GXP33 | GXPTWZ_GXPT1833LV Winding | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | LV Winding | 33 | 350 | 20.0052 | 350 | 20.0052 | 350 | 20.0052 | 479 | 27.3785 | 451 | 25.7781 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 27.3785 | 25.7781 | - | - | - | - | TWZ_GXP25.7781121690476 | GXPTWZ_GXP33451 | GXPTWZ_GXP33350 | 25.7781 | 451 | 350 | 220 kV Bus | 33 kV Bus | Transformer-T18-LV Winding | 33
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Tap Changer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Tap Changer | 33 | 420 | 24.0062 | 420 | 24.0062 | 420 | 24.0062 | - | - | 504 | 28.8075 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 24.0062 | 24.0062 | 24.0062 | - | 28.8075 | - | - | - | - | TWZ_GXP24.0062241929046 | GXPTWZ_GXP33420 | GXPTWZ_GXP33420 | 24.0062 | 420 | 420 | 220 kV Bus | 33 kV Bus | Transformer-T18-Tap Changer | 33
GXPTWZ_GXP220 | GXPTWZ_GXPT18220Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Transformer | 220 | 52 | 19.8147 | 52 | 19.8147 | 52 | 19.8147 | - | - | 68 | 25.9115 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 19.8147 | 19.8147 | 19.8147 | - | 25.9115 | - | - | - | - | TWZ_GXP19.814661238588 | GXPTWZ_GXP22052 | GXPTWZ_GXP22052 | 19.8147 | 52 | 52 | 220 kV Bus | 33 kV Bus | Transformer-T18-Transformer | 220
GXPTWZ_GXP33 | GXPTWZ_GXPT1833Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 3 | TP Branch Report TWZ.TF.T18 | T18 | Transformer | TWZ-TF-T18 | Transformer | 33 | 350 | 20.0052 | 350 | 20.0052 | 350 | 20.0052 | - | - | 451 | 25.7781 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 20.0052 | 20.0052 | 20.0052 | - | 25.7781 | - | - | - | - | TWZ_GXP20.0051868274205 | GXPTWZ_GXP33350 | GXPTWZ_GXP33350 | 20.0052 | 350 | 350 | 220 kV Bus | 33 kV Bus | Transformer-T18-Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB630233Circuit Breaker | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 4 | TP Branch Report TWZ.TF.T18 | TWZ-CB6302 | Circuit Breaker | TWZ-CB-6302 | Circuit Breaker | 33 | 1200 | 68.5892 | 1200 | 68.5892 | 1200 | 68.5892 | - | - | 1200 | 68.5892 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 68.5892 | 68.5892 | 68.5892 | - | 68.5892 | - | - | - | - | TWZ_GXP68.5892119797275 | GXPTWZ_GXP331200 | GXPTWZ_GXP331200 | 68.5892 | 1200 | 1200 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB6302-Circuit Breaker | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB630233Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 4 | TP Branch Report TWZ.TF.T18 | TWZ-CB6302 | Circuit Breaker | TWZ-CT-CT6302 | Current Transformer | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB6302-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB630233Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 4 | TP Branch Report TWZ.TF.T18 | TWZ-CB6302 | Circuit Breaker | TWZ-CT-CT6302 | Current Transformer | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB6302-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB630233Current Transformer | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 4 | TP Branch Report TWZ.TF.T18 | TWZ-CB6302 | Circuit Breaker | TWZ-CT-CT6302 | Current Transformer | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB6302-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB630233Protection | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 4 | TP Branch Report TWZ.TF.T18 | TWZ-CB6302 | Circuit Breaker | Relay SEL 351S | Protection | 33 | - | - | - | - | - | - | - | - | - | - | 623 | 35.6092 | 623 | 35.6092 | 2400 | 137.1784 | 960 | 54.8714 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 35.6092 | 137.1784 | 54.8714 | - | TWZ_GXP35.6092325528085 | GXPTWZ_GXP33623 | GXPTWZ_GXP33623 | 35.6092 | 623 | 623 | 220 kV Bus | 33 kV Bus | Circuit Breaker-TWZ-CB6302-Protection | 33
GXPTWZ_GXP33 | GXPTWZ_GXPDS630433Disconnector | GXP | TWZ_GXP | 220 kV Bus | 33 kV Bus | 5 | TP Branch Report TWZ.TF.T18 | DS6304 | Disconnector | TWZ-DS-6304 | Disconnector | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 220 kV Bus | 33 kV Bus | Disconnector-DS6304-Disconnector | 33
GXPTWZ_GXP33 | GXPTWZ_GXPDS631433Disconnector | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 6 | TP Branch Report TWZ.FDR.6312 | DS6314 | Disconnector | TWZ-DS-6314 | Disconnector | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 33 kV Bus | CB6316 | Disconnector-DS6314-Disconnector | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Circuit Breaker | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CB-6312 | Circuit Breaker | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | 22.8631 | - | - | - | - | TWZ_GXP22.8630706599092 | GXPTWZ_GXP33400 | GXPTWZ_GXP33400 | 22.8631 | 400 | 400 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Circuit Breaker | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Current Transformer | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CB-6312 | Current Transformer | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | 22.8631 | - | - | - | - | TWZ_GXP22.8630706599092 | GXPTWZ_GXP33400 | GXPTWZ_GXP33400 | 22.8631 | 400 | 400 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Current Transformer | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CB-6312 | Current Transformer | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | 22.8631 | - | - | - | - | TWZ_GXP22.8630706599092 | GXPTWZ_GXP33400 | GXPTWZ_GXP33400 | 22.8631 | 400 | 400 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Current Transformer | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CT-CT6312 | Current Transformer | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | 22.8631 | - | - | - | - | TWZ_GXP22.8630706599092 | GXPTWZ_GXP33400 | GXPTWZ_GXP33400 | 22.8631 | 400 | 400 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Current Transformer | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CT-CT6312 | Current Transformer | 33 | 400 | 22.8631 | 400 | 22.8631 | 400 | 22.8631 | - | - | 400 | 22.8631 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 22.8631 | 22.8631 | 22.8631 | - | 22.8631 | - | - | - | - | TWZ_GXP22.8630706599092 | GXPTWZ_GXP33400 | GXPTWZ_GXP33400 | 22.8631 | 400 | 400 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Current Transformer | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Other Equipment | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312 | TWZ-CB6312 | Circuit Breaker | TWZ-CT-CT6312-OEL | Other Equipment | 33 | 120 | 6.8589 | 120 | 6.8589 | 120 | 6.8589 | - | - | 120 | 6.8589 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 6.8589 | 6.8589 | 6.8589 | - | 6.8589 | - | - | - | - | TWZ_GXP6.85892119797275 | GXPTWZ_GXP33120 | GXPTWZ_GXP33120 | 6.8589 | 120 | 120 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Other Equipment | 33
GXPTWZ_GXP33 | GXPTWZ_GXPTWZ-CB631233Protection | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 7 | TP Branch Report TWZ.FDR.6312/AEL Protection Database | TWZ-CB6312 | Circuit Breaker | Relay SEL 351S | Protection | 33 | - | - | - | - | - | - | - | - | - | - | 252 | 14.4037 | 232 | 13.2606 | 1200 | 68.5892 | 480 | 27.4357 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 14.4037 | 68.5892 | 27.4357 | - | TWZ_GXP14.4037345157428 | GXPTWZ_GXP33252 | GXPTWZ_GXP33232 | 14.4037 | 252 | 232 | 33 kV Bus | CB6316 | Circuit Breaker-TWZ-CB6312-Protection | 33
GXPTWZ_GXP33 | GXPTWZ_GXPDS631633Disconnector | GXP | TWZ_GXP | 33 kV Bus | CB6316 | 8 | TP Branch Report TWZ.FDR.6312 | DS6316 | Disconnector | TWZ-DS-6316 | Disconnector | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | 45.7261 | - | - | - | - | TWZ_GXP45.7261413198184 | GXPTWZ_GXP33800 | GXPTWZ_GXP33800 | 45.7261 | 800 | 800 | 33 kV Bus | CB6316 | Disconnector-DS6316-Disconnector | 33
SubTransmissionTWZ_GXP33 | SubTransmissionTWZ_GXPWAXWING33- | SubTransmission | TWZ_GXP | CB6316 | Z69 | 1 | GEMA/AEL OH Amp Calc. | WAXWING | OH Line | - | - | 33 | 398 | 22.7488 | - | - | 296 | 16.9187 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 7.6 | - | - | - | - | - | - | - | - | - | - | - | 22.7488 | - | 16.9187 | - | - | - | - | - | - | TWZ_GXP16.9186722883328 | SubTransmissionTWZ_GXP33296 | SubTransmissionTWZ_GXP33296 | 16.9187 | 296 | 296 | CB6316 | Z69 | OH Line-WAXWING | 33
SubTransmissionTWZ_GXP33 | SubTransmissionTWZ_GXPZ2133- | SubTransmission | TWZ_GXP | CB6316 | Z69 | 2 | GEMA | Z21 | ABS | - | - | 33 | 800 | 45.7261 | 800 | 45.7261 | 800 | 45.7261 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 45.7261 | 45.7261 | 45.7261 | - | - | - | - | - | - | TWZ_GXP45.7261413198184 | SubTransmissionTWZ_GXP33800 | SubTransmissionTWZ_GXP33800 | 45.7261 | 800 | 800 | CB6316 | Z69 | ABS-Z21 | 33
SubTransmissionTWZ_GXP33 | SubTransmissionTWZ_GXPWAXWING33- | SubTransmission | TWZ_GXP | CB6316 | Z69 | 3 | GEMA/AEL OH Amp Calc. | WAXWING | OH Line | - | - | 33 | 398 | 22.7488 | - | - | 296 | 16.9187 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1878.3 | - | - | - | - | - | - | - | - | - | - | - | 22.7488 | - | 16.9187 | - | - | - | - | - | - | TWZ_GXP16.9186722883328 | SubTransmissionTWZ_GXP33296 | SubTransmissionTWZ_GXP33296 | 16.9187 | 296 | 296 | CB6316 | Z69 | OH Line-WAXWING | 33
ZoneSubstationTVS33 | ZoneSubstationTVSZ6933- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 1 | GEMA | Z69 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS33 | ZoneSubstationTVS33 |  |  |  | Z69 | 11 kV Bus | ABS-Z69 | 33
ZoneSubstationTVS33 | ZoneSubstationTVSTVS-Z6833Protection | ZoneSubstation | TVS | Z69 | 11 kV Bus | 2 | AEL Protection Database | TVS-Z68 | Circuit Breaker | Relay E.E. PBO2/CAG | Protection | 33 | - | - | - | - | - | - | - | - | - | - | 150 | 8.5737 | 150 | 8.5737 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 8.5737 | - | - | - | TVS8.57365149746594 | ZoneSubstationTVS33150 | ZoneSubstationTVS33150 | 8.5737 | 150 | 150 | Z69 | 11 kV Bus | Circuit Breaker-TVS-Z68-Protection | 33
ZoneSubstationTVS33 | ZoneSubstationTVSZ6733- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 3 | GEMA | Z67 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS33 | ZoneSubstationTVS33 |  |  |  | Z69 | 11 kV Bus | ABS-Z67 | 33
ZoneSubstationTVS33 | ZoneSubstationTVSZ6333- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 4 | GEMA | Z63 | ABS | - | - | 33 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS33 | ZoneSubstationTVS33 |  |  |  | Z69 | 11 kV Bus | ABS-Z63 | 33
ZoneSubstationTVS33 | ZoneSubstationTVSE12033HV Winding | ZoneSubstation | TVS | Z69 | 11 kV Bus | 5 | AEL Transformers Database | E120 | Transformer | - | HV Winding | 33 | 109.3466 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS33 | ZoneSubstationTVS33109.346641891975 |  |  | 109.3466 | Z69 | 11 kV Bus | Transformer-E120-HV Winding | 33
ZoneSubstationTVS11 | ZoneSubstationTVSE12011LV Winding | ZoneSubstation | TVS | Z69 | 11 kV Bus | 6 | AEL Transformers Database | E120 | Transformer | - | LV Winding | 11 | 328.0399 | 6.25 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS11 | ZoneSubstationTVS11328.039925675924 |  |  | 328.0399 | Z69 | 11 kV Bus | Transformer-E120-LV Winding | 11
ZoneSubstationTVS11 | ZoneSubstationTVSZ6211- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 7 | GEMA | Z62 | ABS | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS11 | ZoneSubstationTVS11 |  |  |  | Z69 | 11 kV Bus | ABS-Z62 | 11
ZoneSubstationTVS11 | ZoneSubstationTVSZ6111- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 8 | GEMA | Z61 | Link | - | - | 11 | 600 | 11.4315 | 600 | 11.4315 | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | 11.4315 | 11.4315 | - | - | - | - | - | - | TVS11.4315353299546 | ZoneSubstationTVS11600 | ZoneSubstationTVS11600 | 11.4315 | 600 | 600 | Z69 | 11 kV Bus | Link-Z61 | 11
ZoneSubstationTVS11 | ZoneSubstationTVSTVS-Z611- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 9 | AEL Protection Database | TVS-Z6 | Circuit Breaker | Z6 | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TVS | ZoneSubstationTVS11 | ZoneSubstationTVS11 |  |  |  | Z69 | 11 kV Bus | Circuit Breaker-TVS-Z6 | 11
ZoneSubstationTVS11 | ZoneSubstationTVS3-1c 400 mm² AL XLPE11- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 10 | GEMA/General Cables | 3-1c 400 mm² AL XLPE | Cable | - | - | 11 | 537 | 10.2312 | 537 | 10.2312 | 537 | 10.2312 | - | - | - | - | - | - | - | - | - | - | - | - | 1 | No | 40 | 0.9 | 0.97 | 15 | 1 | 1.5 | 0.9 | 4 | 0.15 | 0.7 | 328.1607 | 6.2523 | 10.2312 | 10.2312 | 10.2312 | - | - | - | - | - | 6.2523 | TVS6.25230105992105 | ZoneSubstationTVS11328.1607 | ZoneSubstationTVS11328.1607 | 6.2523 | 328.1607 | 328.1607 | Z69 | 11 kV Bus | Cable-3-1c 400 mm² AL XLPE | 11
ZoneSubstationTVS11 | ZoneSubstationTVSTVS-Z611- | ZoneSubstation | TVS | Z69 | 11 kV Bus | 11 | AEL Protection Database | TVS-Z6 | Circuit Breaker | Z6 | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600 | 11.4315 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 11.4315 | - | TVS11.4315353299546 | ZoneSubstationTVS11600 | ZoneSubstationTVS11600 | 11.4315 | 600 | 600 | Z69 | 11 kV Bus | Circuit Breaker-TVS-Z6 | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 1TVS-Z111Protection | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 1 | AEL Protection Database | TVS-Z1 | Circuit Breaker | Relay SEL 551C | Protection | 11 | - | - | - | - | - | - | - | - | - | - | 152 | 2.896 | 152 | 2.896 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.896 | - | - | - | Z1_Urban No. 12.89598895025516 | DistributionFeederZ1_Urban No. 111152 | DistributionFeederZ1_Urban No. 111152 | 2.896 | 152 | 152 | 11 kV Bus | Z110 | Circuit Breaker-TVS-Z1-Protection | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 11-3c 185 mm² AL XLPE11- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 2 | Drawing 9280-02/General Cable | 1-3c 185 mm² AL XLPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 19.1 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.835 | 300.3161 | 5.7218 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 5.7218 | Z1_Urban No. 15.72179017884029 | DistributionFeederZ1_Urban No. 111300.3161 | DistributionFeederZ1_Urban No. 111300.3161 | 5.7218 | 300.3161 | 300.3161 | 11 kV Bus | Z110 | Cable-1-3c 185 mm² AL XLPE | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 1Z10111- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 3 | GEMA | Z101 | Link | - | - | 11 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | - | - | - | - | - | - | - | - | Z1_Urban No. 15.7157676649773 | DistributionFeederZ1_Urban No. 111300 | DistributionFeederZ1_Urban No. 111300 | 5.7158 | 300 | 300 | 11 kV Bus | Z110 | Link-Z101 | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 11-3c 300 mm² AL XLPE11- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 4 | Drawing 9280-02/General Cable | 1-3c 300 mm² AL XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 179.8 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 3 | 0.5 | 0.845 | 394.1756 | 7.5101 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.5101 | Z1_Urban No. 17.51005382934341 | DistributionFeederZ1_Urban No. 111394.1756 | DistributionFeederZ1_Urban No. 111394.1756 | 7.5101 | 394.1756 | 394.1756 | 11 kV Bus | Z110 | Cable-1-3c 300 mm² AL XLPE | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 1MINK11- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 5 | GEMA | MINK | OH Line | - | - | 11 | 251 | 4.7822 | - | - | 189 | 3.6009 |  | - |  | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | 4.7822 | - | 3.6009 | - | - | - | - | - | - | Z1_Urban No. 13.6009336289357 | DistributionFeederZ1_Urban No. 111189 | DistributionFeederZ1_Urban No. 111189 | 3.6009 | 189 | 189 | 11 kV Bus | Z110 | OH Line - MINK | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 11-3c 150mm2 AL PILC11- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 6 | GEMA/General Cables | 1-3c 150mm2 AL PILC | Cable | - | - | 11 | 265 | 5.0489 | 265 | 5.0489 | 265 | 5.0489 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 84.3 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 259.7 | 4.9479 | 5.0489 | 5.0489 | 5.0489 | - | - | - | - | - | 4.9479 | Z1_Urban No. 14.94794954198201 | DistributionFeederZ1_Urban No. 111259.7 | DistributionFeederZ1_Urban No. 111259.7 | 4.9479 | 259.7 | 259.7 | 11 kV Bus | Z110 | Cable-1-3c 150mm2 AL PILC | 11
DistributionFeederZ1_Urban No. 111 | DistributionFeederZ1_Urban No. 1Z11011- | DistributionFeeder | Z1_Urban No. 1 | 11 kV Bus | Z110 | 7 | GEMA | Z110 | Switch | - | - | 11 | 630 | 12.0031 | 630 | 12.0031 | 630 | 12.0031 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12.0031 | 12.0031 | 12.0031 | - | - | - | - | - | - | Z1_Urban No. 112.0031120964523 | DistributionFeederZ1_Urban No. 111630 | DistributionFeederZ1_Urban No. 111630 | 12.0031 | 630 | 630 | 11 kV Bus | Z110 | Switch-Z110 | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 2TVS-Z211Protection | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 1 | AEL Protection Database | TVS-Z2 | Circuit Breaker | Relay SEL 551C | Protection | 11 | - | - | - | - | - | - | - | - | - | - | 152 | 2.896 | 152 | 2.896 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.896 | - | - | - | Z2_Urban No. 22.89598895025516 | DistributionFeederZ2_Urban No. 211152 | DistributionFeederZ2_Urban No. 211152 | 2.896 | 152 | 152 | 11 kV Bus | Pole 12571 | Circuit Breaker-TVS-Z2-Protection | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 21-3c 185 mm² Cu XLPE11- | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 2 | Drawing 9280-02/General Cable | 1-3c 185 mm² Cu XLPE | Cable | - | - | 11 | 469 | 8.9357 | 469 | 8.9357 | 469 | 8.9357 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 15.8 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.835 | 383.7827 | 7.312 | 8.9357 | 8.9357 | 8.9357 | - | - | - | - | - | 7.312 | Z2_Urban No. 27.31204249012561 | DistributionFeederZ2_Urban No. 211383.7827 | DistributionFeederZ2_Urban No. 211383.7827 | 7.312 | 383.7827 | 383.7827 | 11 kV Bus | Pole 12571 | Cable-1-3c 185 mm² Cu XLPE | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 2Z20111- | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 3 | GEMA | Z201 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Z2_Urban No. 2 | DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 211 |  |  |  | 11 kV Bus | Pole 12571 | Link-Z201 | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 21-3c 300 mm² AL XLPE11- | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 4 | Drawing 9280-02/General Cable | 1-3c 300 mm² AL XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 182.4 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 3 | 0.5 | 0.845 | 394.1756 | 7.5101 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.5101 | Z2_Urban No. 27.51005382934341 | DistributionFeederZ2_Urban No. 211394.1756 | DistributionFeederZ2_Urban No. 211394.1756 | 7.5101 | 394.1756 | 394.1756 | 11 kV Bus | Pole 12571 | Cable-1-3c 300 mm² AL XLPE | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 2Z1511- | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 5 | GEMA | Z15 | Link | - | - | 11 | 300 | 5.7158 | 300 | 5.7158 | 300 | 5.7158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 5.7158 | 5.7158 | 5.7158 | - | - | - | - | - | - | Z2_Urban No. 25.7157676649773 | DistributionFeederZ2_Urban No. 211300 | DistributionFeederZ2_Urban No. 211300 | 5.7158 | 300 | 300 | 11 kV Bus | Pole 12571 | Link-Z15 | 11
DistributionFeederZ2_Urban No. 211 | DistributionFeederZ2_Urban No. 2MINK11- | DistributionFeeder | Z2_Urban No. 2 | 11 kV Bus | Pole 12571 | 6 | GEMA/AEL OH Amp Calc. | MINK | OH Line | - | - | 11 | 251 | 4.7822 | - | - | 189 | 3.6009 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 65.46 | - | - | - | - | - | - | - | - | - | - | - | 4.7822 | - | 3.6009 | - | - | - | - | - | - | Z2_Urban No. 23.6009336289357 | DistributionFeederZ2_Urban No. 211189 | DistributionFeederZ2_Urban No. 211189 | 3.6009 | 189 | 189 | 11 kV Bus | Pole 12571 | OH Line-MINK | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_IndustrialTVS-Z311Protection | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 1 | AEL Protection Database | TVS-Z3 | Circuit Breaker | Relay SEL 551C | Protection | 11 | - | - | - | - | - | - | - | - | - | - | 150 | 2.8579 | 150 | 2.8579 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.8579 | - | - | - | Z3_Industrial2.85788383248865 | DistributionFeederZ3_Industrial11150 | DistributionFeederZ3_Industrial11150 | 2.8579 | 150 | 150 | 11 kV Bus | E48 | Circuit Breaker-TVS-Z3-Protection | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial1-3c 150 mm² Cu XLPE11- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 2 | Drawing 9280-02/General Cable | 1-3c 150 mm² Cu XLPE | Cable | - | - | 11 | 414 | 7.8878 | 414 | 7.8878 | 414 | 7.8878 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 15.6 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.835 | 338.7762 | 6.4546 | 7.8878 | 7.8878 | 7.8878 | - | - | - | - | - | 6.4546 | Z3_Industrial6.45455349874627 | DistributionFeederZ3_Industrial11338.7762 | DistributionFeederZ3_Industrial11338.7762 | 6.4546 | 338.7762 | 338.7762 | 11 kV Bus | E48 | Cable-1-3c 150 mm² Cu XLPE | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial1-3c 185 mm² AL XLPE11- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 3 | Drawing 9280-02/General Cable | 1-3c 185 mm² AL XLPE | Cable | - | - | 11 | 367 | 6.9923 | 367 | 6.9923 | 367 | 6.9923 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 5 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 359.66 | 6.8524 | 6.9923 | 6.9923 | 6.9923 | - | - | - | - | - | 6.8524 | Z3_Industrial6.85244332795245 | DistributionFeederZ3_Industrial11359.66 | DistributionFeederZ3_Industrial11359.66 | 6.8524 | 359.66 | 359.66 | 11 kV Bus | E48 | Cable-1-3c 185 mm² AL XLPE | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_IndustrialZ30111- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 4 | GEMA | Z301 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Z3_Industrial | DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial11 |  |  |  | 11 kV Bus | E48 | Link-Z301 | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_IndustrialZ30411- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 5 | GEMA | Z304 | Fuse | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Z3_Industrial | DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial11 |  |  |  | 11 kV Bus | E48 | Fuse-Z304 | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial1-3c 35 mm² AL PILC11- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 6 | Drawing 9280-02/General Cable | 1-3c 35 mm² AL PILC | Cable | - | - | 11 | 115 | 2.191 | 115 | 2.191 | 115 | 2.191 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 37.8 | 0.9 | 0.99 | 15 | 1 | 1.2 | 1 | 3 | 0.15 | 0.75 | 85.3875 | 1.6269 | 2.191 | 2.191 | 2.191 | - | - | - | - | - | 1.6269 | Z3_Industrial1.62685037164416 | DistributionFeederZ3_Industrial1185.3875 | DistributionFeederZ3_Industrial1185.3875 | 1.6269 | 85.3875 | 85.3875 | 11 kV Bus | E48 | Cable-1-3c 35 mm² AL PILC | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial1-3c 0.0225 in² Cu PILC11- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 7 | Drawing 9280-02/General Cable | 1-3c 0.0225 in² Cu PILC | Cable | - | - | 11 | 100 | 1.9053 | 100 | 1.9053 | 100 | 1.9053 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 126.6 | 0.9 | 0.99 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 99 | 1.8862 | 1.9053 | 1.9053 | 1.9053 | - | - | - | - | - | 1.8862 | Z3_Industrial1.88620332944251 | DistributionFeederZ3_Industrial1199 | DistributionFeederZ3_Industrial1199 | 1.8862 | 99 | 99 | 11 kV Bus | E48 | Cable-1-3c 0.0225 in² Cu PILC | 11
DistributionFeederZ3_Industrial11 | DistributionFeederZ3_Industrial1-3c 0.04 in² Cu PILC11- | DistributionFeeder | Z3_Industrial | 11 kV Bus | E48 | 8 | GEMA | 1-3c 0.04 in² Cu PILC | Cable | - | - | 11 | 125 | 2.3816 | 125 | 2.3816 | 125 | 2.3816 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 18.8 | 0.9 | 0.99 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 123.75 | 2.3578 | 2.3816 | 2.3816 | 2.3816 | - | - | - | - | - | 2.3578 | Z3_Industrial2.35775416180313 | DistributionFeederZ3_Industrial11123.75 | DistributionFeederZ3_Industrial11123.75 | 2.3578 | 123.75 | 123.75 | 11 kV Bus | E48 | Cable-1-3c 0.04 in² Cu PILC | 11
DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel RuralTVS-Z411Protection | DistributionFeeder | Z4_Twizel Rural | 11 kV Bus | Z401 | 1 | AEL Protection Database | TVS-Z4 | Circuit Breaker | Relay SEL 551C | Protection | 11 | - | - | - | - | - | - | - | - | - | - | 152 | 2.896 | 152 | 2.896 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2.896 | - | - | - | Z4_Twizel Rural2.89598895025516 | DistributionFeederZ4_Twizel Rural11152 | DistributionFeederZ4_Twizel Rural11152 | 2.896 | 152 | 152 | 11 kV Bus | Z401 | Circuit Breaker-TVS-Z4-Protection | 11
DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel Rural1-3c 150 mm² Cu XLPE11- | DistributionFeeder | Z4_Twizel Rural | 11 kV Bus | Pole 18576 | 2 | Drawing 9280-02/General Cable | 1-3c 150 mm² Cu XLPE | Cable | - | - | 11 | 414 | 7.8878 | 414 | 7.8878 | 414 | 7.8878 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 12.5 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 4 | 0.5 | 0.835 | 338.7762 | 6.4546 | 7.8878 | 7.8878 | 7.8878 | - | - | - | - | - | 6.4546 | Z4_Twizel Rural6.45455349874627 | DistributionFeederZ4_Twizel Rural11338.7762 | DistributionFeederZ4_Twizel Rural11338.7762 | 6.4546 | 338.7762 | 338.7762 | 11 kV Bus | Pole 18576 | Cable-1-3c 150 mm² Cu XLPE | 11
DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel RuralZ40111- | DistributionFeeder | Z4_Twizel Rural | 11 kV Bus | Pole 18576 | 3 | GEMA | Z401 | Link | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Z4_Twizel Rural | DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel Rural11 |  |  |  | 11 kV Bus | Pole 18576 | Link-Z401 | 11
DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel Rural1-3c 300 mm² AL XLPE11- | DistributionFeeder | Z4_Twizel Rural | 12 kV Bus | Pole 18576 | 4 | GEMA | 1-3c 300 mm² AL XLPE | Cable | - | - | 11 | 476 | 9.069 | 476 | 9.069 | 476 | 9.069 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 179.8 | 1 | 0.98 | 15 | 1 | 1.2 | 1 | 3 | 0.5 | 0.845 | 394.1756 | 7.5101 | 9.069 | 9.069 | 9.069 | - | - | - | - | - | 7.5101 | Z4_Twizel Rural7.51005382934341 | DistributionFeederZ4_Twizel Rural11394.1756 | DistributionFeederZ4_Twizel Rural11394.1756 | 7.5101 | 394.1756 | 394.1756 | 12 kV Bus | Pole 18576 | Cable - 1-3c 300 mm² AL XLPE | 11
DistributionFeederZ4_Twizel Rural11 | DistributionFeederZ4_Twizel RuralMINK11- | DistributionFeeder | Z4_Twizel Rural | 11 kV Bus | Pole 18576 | 5 | GEMA | MINK | OH line | - | - | 11 | 251 | 4.7822 | - | - | 189 | 3.6009 | - | - | - | - |  | - |  | - |  | - |  | - | [12 empty] | - | - | 4.7822 | - | 3.6009 | - | - | - | - | - | - | Z4_Twizel Rural3.6009336289357 | DistributionFeederZ4_Twizel Rural11189 | DistributionFeederZ4_Twizel Rural11189 | 3.6009 | 189 | 189 | 11 kV Bus | Pole 18576 | OH line - MINK | 11
DistributionFeederZ5_Spare11 | DistributionFeederZ5_SpareTVS-Z511- | DistributionFeeder | Z5_Spare | 11 kV Bus | Spare | 1 | AEL Protection Database | TVS-Z5 | Circuit Breaker | - | - | 11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Z5_Spare | DistributionFeederZ5_Spare11 | DistributionFeederZ5_Spare11 |  |  |  | 11 kV Bus | Z401 | Link-Z401 | 11
DistributionFeederZ9_Local Supply11 | DistributionFeederZ9_Local SupplyTVS-Z911Protection | DistributionFeeder | Z9_Local Supply | 11 kV Bus | E120 | 1 | AEL Protection Database | TVS-Z9 | Circuit Breaker | Relay SEL 551C | Protection | 11 | 10 | 0.19053 | 10 | 0.19053 | 10 | 0.19053 | - | - | - | - | 30 | 0.57158 | 30 | 0.57158 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.57158 | - | - | - | Z9_Local Supply0.571576766497729 | DistributionFeederZ9_Local Supply1130 | DistributionFeederZ9_Local Supply1110 | 0.57158 | 30 | 10 | 11 kV Bus | E120 | Circuit Breaker - TVS-Z9 - Protection | 11
DistributionFeederZ9_Local Supply11 | DistributionFeederZ9_Local Supply1-3c 95 mm² Cu XLPE11- | DistributionFeeder | Z9_Local Supply | 12 kV Bus | E120 | 2 | GEMA | 1-3c 95 mm² Cu XLPE | Cable | - | - | 11 | 251.6 | 4.7936 | 251.6 | 4.7936 | 251.6 | 4.7936 | - | - | - | - | - | - | - | - | - | - | - | - | 3 | No | 3 | 0.9 | 1 | 15 | 1 | 1.2 | 1 | 1 | 0 | 1 | 251.6 | 4.7936 | 4.7936 | 4.7936 | 4.7936 | - | - | - | - | - | 4.7936 | Z9_Local Supply4.79362381502762 | DistributionFeederZ9_Local Supply11251.6 | DistributionFeederZ9_Local Supply11251.6 | 4.7936 | 251.6 | 251.6 | 12 kV Bus | E120 | Cable - 1-3c 95 mm² Cu XLPE | 11
[13 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1.9053 | 1.9053 | 1.9053 | 27.3785 | 6.8589 | 0.57158 | 68.5892 | 11.4315 | 1.6269 | - | - |  | 0.57158 | - |  | - | - | - | -
Note on S46: Author: ODAF
Note on S47: Author: ODAF

## Dropdown List
Supply Levels | Supply Level | SOS | Simplification | Combined | Definition
GXP | - | - | - | -
SubTransmission | SubTransmission | ST1 | N-1 | ST1 (N-1) | No interruption
ZoneSubstation | SubTransmission | ST2 | N-1 | ST2 (N-1) | 15 seconds for 100% load
SecondarySubstation | SubTransmission | ST3 | N-1 SW | ST3 (N-1 SW) | 45 minutes for 100% load
SwitchingStation | SubTransmission | ST4 | N-0.75 SW | ST4 (N-0.75 SW) | Restore 75% of lost load (in MVA) in switching time.
DistributionFeeder | SubTransmission | ST5 | N-0.5 SW | ST5 (N-0.5 SW) | Restore 50% of lost load (in MVA) in switching time.
LV Reticulation | SubTransmission | ST6 | N | ST6 (N) | Repair time
| SwitchingStation | ZS1 | N-1 | ZS1 (N-1) | No interruption
| SwitchingStation | ZS2 | N-1 | ZS2 (N-1) | 15 seconds for 100% load
| SwitchingStation | ZS3 | N-1 SW | ZS3 (N-1 SW) | 45 minutes for 100% load
| SwitchingStation | ZS4 | N-1 SW | ZS4 (N-1 SW) | Restore 100% of lost load in switching time.
| SwitchingStation | ZS5 | N-0.5 SW | ZS5 (N-0.5 SW) | Restore 50% of lost load in switching time.
| SwitchingStation | ZS6 | N | ZS6 (N) | Restore 100% of lost load in repair time
| ZoneSubstation | ZS1 | N-1 | ZS1 (N-1) | No interruption
| ZoneSubstation | ZS2 | N-1 | ZS2 (N-1) | 15 seconds for 100% load
| ZoneSubstation | ZS3 | N-1 SW | ZS3 (N-1 SW) | 45 minutes for 100% load
| ZoneSubstation | ZS4 | N-1 SW | ZS4 (N-1 SW) | Restore 100% of lost load in switching time.
| ZoneSubstation | ZS5 | N-0.5 SW | ZS5 (N-0.5 SW) | Restore 50% of lost load in switching time.
| ZoneSubstation | ZS6 | N | ZS6 (N) | Restore 100% of lost load in repair time
| DistributionFeeder | DF1 | N-1 SW | DF1 (N-1 SW) | Restore 100% supply in one hour. The isolated section shall be limited to 300 kVA installed capacity.
| DistributionFeeder | DF2 | N-1 SW | DF2 (N-1 SW) | Restore 100% supply in two hours. The isolated section shall be limited to 500 kVA installed capacity.
| DistributionFeeder | DF3 | N-1 SW | DF3 (N-1 SW) | Restore 100% supply in three hours. The isolated section shall be limited to 1.5 MVA of installed capacity.
| DistributionFeeder | DF4 | N-0.5 SW | DF4 (N-0.5 SW) | Restore 50% supply in four hours. The isolated section shall be limited to 1.5 MVA of installed capacity.
| DistributionFeeder | DF5 | N | DF5 (N) | After a fault, part supply can be restored by switching using adjacent feeder capacity
| DistributionFeeder | DF6 | N | DF6 (N) | After a fault, supply may remain interrupted until repairs are completed.
ABY_GXP | BPD_GXP | STU_GXP | TIM_GXP | TKA_GXP | TMK_GXP | TWZ_GXP
ABY | BPD | STU | TIM | TKA | CB1292_Geraldine | TWZ
CB2732_Raincliff | CB11_Waihao Downs | CB1_Otaio | TIM_NST_SUBTRANS | TEK | CB1282_Clandeboye No.4 | TVS
CB2742_Cave | CB12_Ikawai | CB2_Glenavy | CB2692_North ST.1 | M200_Haldon_Lilybank | CB1272_Clandeboye No.2 | Z1_Urban No. 1
CB2722_Fairlie | CB13_Waikakahi | CB3_Waimate | CB2982_North ST.2 | M201_Simons | CB1262_Temuka No.2 | Z2_Urban No. 2
FLE | CB1_Waihuna | CB7_Waihaorunga | TIM_GRM_SUBTRANS | M205_Godley | CB1222_Clandeboye No.3 | Z3_Industrial
F374_Cricklewood | CB2_Tawai | CB8_Mt Studholme | TIM_GRMA_SUBTRANS | M206_Tekapo Township | CB1212_Temuka No.1 | Z4_Twizel Rural
F380_Fairlie Rural | CB522_CNR | CB9_Morven | TIM_GRMB_SUBTRANS | HLB | CB1202_Rangitata | Z5_Spare
F383_Fairlie Township | CNR |  | TIM_GRMC_SUBTRANS | M32_Lilybank | CB1192_Clandeboye No.1 | Z9_Local Supply
OPU | CB8_Drier 2 |  | TIM_GRMD_SUBTRANS | M33_Haldon | TMK
| CB9_WetProcess |  | CB2662_Waipopo | OMR | CB1_Temuka West
| CB11_Boiler/Chiller 1 |  | TIM_WSS_SUBTRANS | M338_Old Man Range | CB2_Milford
| CB12_Office |  | CB2672_Washdyke | TKA_M11 | CB3_Winchester
| CB642_CNR |  | CB2682_Showgrounds Hill | SBT_33kV | CB7_Rangitata
| CB236_STU Incomer |  | CB2702_Morgans Rd | UHT | CB8_Temuka East
| CB3602_CNR |  | CB2712_Mountain View Rd | M158_Village | CB9_Waitohi
|  |  | CB2732_ATM_T1 | M159_Village | GLD
|  |  | CB2742_Levels Plain |  | G194_Speechly
|  |  | CB2762_AEL Yard |  | G191_Geraldine Township
|  |  | CB2832_Grants Rd |  | G156_Woodbury
|  |  | CB2852_Hadlow |  | RGA_T1
|  |  | CB2862_Meadows Rd |  | CB2_Arundel
|  |  | CB2922_ATM_T2 |  | CB3_Mahan Road
|  |  | CB2942_Old North Rd |  | CB4_Main South Road
|  |  | CB2952_Highfield |  | RGA_T2
|  |  | CB2972_Smithfield |  | CB11_Belfield
|  |  | CB2992_Goulds Road |  | CB12_Orton
|  |  | CB3002_Elginshire |  | CB13_Rangitata Island
|  |  | CB3012_Arowhenua |  | CD_1
|  |  | GRM |  | T600_Tie to Milk Powder 2
|  |  | GRM_SUB |  | T601_Fire Services
|  |  | GRM_HNT_SUBTRANS |  | T602_Whey Processing
|  |  | GRM_NST_SUBTRANS |  | T603_Lactose Plant
|  |  | CB2_White St |  | T605_Tie to Milford
|  |  | CB4_GRM-HNT A |  | T609_Milk Reception
|  |  | CB5_Nile St |  | T610_Chilled Water 1
|  |  | CB6_Parkview Terrace |  | T611_Effluent Plant
|  |  | CB7_Douglas St |  | T612_Milk Treatment
|  |  | CB9_GRM-NST A |  | T613_Rolleston Rd
|  |  | CB10_Ashbury Park |  | T614_Tie to Powder Handling
|  |  | CB12_Selwyn St |  | CD_2
|  |  | CB13_GRM-HNT B |  | T650_Tie to Milk Powder 1
|  |  | CB15_Park Lane |  | T651_Milk Powder 3
|  |  | CB16_Evans St |  | T652_Tie to WPC
|  |  | CB17_June St |  | T653_Chilled Water 3
|  |  | CB18_GRM-NST B |  | T654_Tie to Boiler House
|  |  | CB20_Hobbs St |  | T658_Milk Powder 2
|  |  | NST |  | T659_Tie to Energy Centre 1
|  |  | NST_SUB |  | T660_Refrigeration
|  |  | CB3_Redruth 1 |  | T661_Laboratory
|  |  | CB4_Rose St |  | CB2_Mozz3_1
|  |  | CB5_Craigie Ave |  | CB15_Mozz3_2
|  |  | CB8_Barnard St |  | CNL
|  |  | CB9_Port 1 |  | CNL-RGA
CB10_Fraser St
CB11_Hayes St
CB12_High St
CB13_Port 2
CB16_Victoria St
CB17_Stafford St
CB18_Redruth 2
HNT
HNT_SUB
HNT_NST_SUBTRANS
CB1_Harper St
CB2_Wilson St
CB3_HNT-GRM A
CB4_Baker St
CB5_Le Cren St
CB6_HNT-NST A
CB7_Church St SS
CB8_Spare
CB9_Bus coupler
CB10_Gibson St
CB11_Rhodes St
CB12_HNT-GRM B
CB13_Clifton Terrace
CB14_Church St NS
CB15_HNT-NST B
CB16_Arthur St
CB17_Spare
ATM
L413_L418_Pareora
PAR
CB3_Works No. 1
CB4_St Andrews
CB5_Works No. 2
CB6_Normanby
CB7_Holmestation
ATM_2
L269_PleasantPoint
PLP
CB1_Waitawa
CB2_Sutherlands
CB3_Incomer
CB4_Totara Valley
CB5_Pleasant Point Township

## Protection Data
ID | Zone Sub | Source Query | GXP | Protection Type | CB ID | Location/Description | Feeder ID | Relay | Voltage (kV) | Pickup (A) | Min Pickup (A)
ABY-CB2742 | ABY | ABY_Protection | ABY_GXP | OC(IT) | CB2742 | Cave Feeder | CB2742_Cave | SEL 351S | 11 | 225 | 225
ABY-CB2732 | ABY | ABY_Protection | ABY_GXP | OC(IT) | CB2732 | Raincliff Feeder | CB2732_Raincliff | SEL 351S | 11 | 225 | 225
ABY-CB2722 | ABY | ABY_Protection | ABY_GXP | OC(IT) | CB2722 | Fairlie-Opuha Feeder | CB2722_Fairlie | SEL 351S | 11 | 450 | 450
ABY-CB4242 | ABY | ABY_Protection | ABY_GXP | OC(IT) | CB4242 | Albury 33/11 Substation 33 kV CB | CB4242_Albury 33/11 Substation 33 kV CB | SEL 311C | 33 | 150 | 150
FLE-F150 | FLE | ABY_Protection | ABY_GXP | OC | F150 | Brothers x CB2 | F150_Brothers x CB2 | NuLec Moderate | 11 | 100 | 100
FLE-F138 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F138 | Cave Cannington (Anne St) x CB1 | F138_Cave Cannington (Anne St) x CB1 | Noja RC-01ES | 11 | 70 | 70
FLE-F295 | FLE | ABY_Protection | ABY_GXP | OC | F295 | Clelands Rd x CB1 | F295_Clelands Rd x CB1 | SEL351R KFME | 11 | 50 | 50
FLE-F392 | FLE | ABY_Protection | ABY_GXP | OC | F392 | Proposed Ripple Plant | F392_Proposed Ripple Plant | SEL 751A | 11 | 60 | 60
FLE-F323 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F323 | Fairlie Substation 33 kV CB | F323_Fairlie Substation 33 kV CB | SEL 351S | 33 | 100 | 100
FLE-F377 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F377 | 11 kV incomer | F377_11 kV incomer | SEL 751A | 11 | 280 | 280
FLE-F374 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F374 | Cricklewood | F374_Cricklewood | SEL 751A | 11 | 192 | 192
FLE-F380 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F380 | FLE Rural | F380_FLE Rural | SEL 751A | 11 | 192 | 192
FLE-F383 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F383 | FLE Township | F383_FLE Township | SEL 751A | 11 | 192 | 192
FLE-F341 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F341 | Allandale | F341_Allandale | Nulec Moderate | 11 | 100 | 100
FLE-F287 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F287 | Burkes Pass | F287_Burkes Pass | SEL351R KFME | 11 | 100 | 100
FLE-F189 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F189 | Cricklewood | F189_Cricklewood | Nulec N-Series | 11 | 80 | 80
FLE-F359 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F359 | Clayton Road 11kV | F359_Clayton Road 11kV | Noja RC-01ES | 11 | 100 | 100
FLE-F418 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F418 | Hunterslea Rd | F418_Hunterslea Rd | SEL 651R | 11 | 100 | 100
FLE-F426 | FLE | ABY_Protection | ABY_GXP | OC(IT) | F426 | Chamberlain Rd | F426_Chamberlain Rd | SEL 651R | 11 | 50 | 50
OPU-F400 | OPU | ABY_Protection | ABY_GXP | OC | F400 | ABY-FLE-OPU 33 kV CB | F400_ABY-FLE-OPU 33 kV CB | SEL 351R | 33 | 150 | 150
FLE-F329 | FLE | ABY_Protection | ABY_GXP | OC | F329 | Opuha 33 kV CB x F319 | F329_Opuha 33 kV CB x F319 |  | 33 | 176.8 | 176.8
BPD-T2-CB522 | BPD | BPD_Protection | BPD_GXP | OC(IT)MV1 | CB522 | Dif (Winding 2 - CNR Feeder) | CB522_Dif (Winding 2 - CNR) | SEL 387-6 | 33 | 370 | 370
BPD-T2-CB482 | BPD | BPD_Protection | BPD_GXP | OC(IT)HV1 | CB482 | Dif (Winding 1) | CB482_Dif (Winding 1) | SEL 387-6 | 110 | 146 | 146
BPD-T1-CB442 | BPD | BPD_Protection | BPD_GXP | OC(IT)HV1 | CB442 | Dif (Winding 1) | CB442_Dif (Winding 1) | SEL 387-6 | 110 | 292 | 292
BPD-T1-CB3602 | BPD | BPD_Protection | BPD_GXP | OC(IT)HV1 | CB3602 | Dif (Winding 2 - CNR Feeder) | CB3602_Dif (Winding 2 - CNR) | SEL 387-6 | 33 | 492 | 492
BPD-T1-CB35 | BPD | BPD_Protection | BPD_GXP | OC(IT)LV1 | CB35 | Dif (Winding 3 - T1 Incomer) | CB35_Dif (Winding 3 - T1 Incomer) | SEL 387-6 | 11 | 2208 | 2208
BPD-T1-CB1 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB1 | Waihuna | CB1_Waihuna | SEL 751A | 11 | 400 | 400
BPD-T1-CB2 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB2 | Tawai | CB2_Tawai | SEL 751A | 11 | 400 | 400
BPD-T1-CB31 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB31 | Bus Coupler A | CB31_Bus Coupler A | SEL 751A | 11 | 1000 | 1000
BPD-T2-CB32 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB32 | Bus Coupler B (ex CB14) | CB32_Bus Coupler B (ex CB14) | SEL 351S-6 | 11 | 1000 | 1000
BPD-T2-CB36 | BPD | BPD_Protection | BPD_GXP | OC(IT)LV1 | CB36 | Dif (Winding 3 - T2 Incomer) | CB36_Dif (Winding 3 - T2 Incomer) | SEL 387-6 | 11 | 1100 | 1100
BPD-T2-CB11 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB11 | WDI Pump Station | CB11_WDI Pump Station | SEL 351S-6 | 11 | 400 | 400
BPD-T2-CB12 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB12 | Ikawai | CB12_Ikawai | SEL 351S-6 | 11 | 400 | 400
BPD-T2-CB13 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB13 | Waikakahi | CB13_Waikakahi | SEL 351S-6 | 11 | 400 | 400
BPD-T2-CB14 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB14 | Tawai/Waihuna | CB14_Tawai/Waihuna | SEL 351S-6 | 11 | 400 | 400
BPD-T2-CB15 | BPD | BPD_Protection | BPD_GXP | OC(IT) | CB15 | Ripple Plant | CB15_Ripple Plant | SEL 351S-6 | 11 | 60 | 60
BPD-W590 | BPD | BPD_Protection | BPD_GXP | OC(IT) | W590 | Glenavy Tawai xW608 | W590_Glenavy Tawai xW608 | SEL 351R-F | 11 | 140 | 140
BPD-W608 | BPD | BPD_Protection | BPD_GXP | OC(IT) | W608 | Tawai xCB14 | W608_Tawai xCB14 | SEL 351R-F | 11 | 250 | 250
BPD-W611 | BPD | BPD_Protection | BPD_GXP | OC(IT) | W611 | Waihuna leg xCB14 | W611_Waihuna leg xCB14 | SEL 351R-F | 11 | 250 | 250
BPD-CB642 | BPD | BPD_Protection | BPD_GXP | OC(IT)HV1 | CB642 | T1 | CB642_T1 | SEL 311C | 33 | 369 | 369
CNR-CB35 | CNR | BPD_Protection | BPD_GXP | OC(IT)LV1 | CB35 | Incomer T1 | CB35_Incomer T1 | SEL 751A | 11 | 1104 | 1104
CNR-CB35 | CNR | BPD_Protection | BPD_GXP | OC(Chk) | CB35 | Incomer T1 | CB35_Incomer T1 | SEL 751A | 11 | 1200 | 1104
CNR-CB36 | CNR | BPD_Protection | BPD_GXP | OC(IT)LV1 | CB36 | Incomer STU | CB36_Incomer STU | SEL 751A | 11 | 144 | 144
CNR-CB36 | CNR | BPD_Protection | BPD_GXP | OC(Chk) | CB36 | Incomer STU | CB36_Incomer STU | SEL 751A | 11 | 800 | 144
CNR-CB31 | CNR | BPD_Protection | BPD_GXP | OC(Chk) | CB31 | Bus Coupler 1 | CB31_Bus Coupler 1 | SEL 751A | 11 | 1200 | 1200
CNR-CB32 | CNR | BPD_Protection | BPD_GXP | OC(Chk) | CB32 | Bus Coupler 2 | CB32_Bus Coupler 2 | SEL 751A | 11 | 1200 | 1200
CNR-CB8 | CNR | BPD_Protection | BPD_GXP | OC(IT)1 | CB8 | Drier 2 | CB8_Drier 2 | SEL 751A | 11 | 402 | 402
CNR-CB9 | CNR | BPD_Protection | BPD_GXP | OC(IT)1 | CB9 | Wet Process | CB9_Wet Process | SEL 751A | 11 | 402 | 402
CNR-CB11 | CNR | BPD_Protection | BPD_GXP | OC(IT)1 | CB11 | Utilities Services | CB11_Utilities Services | SEL 751A | 11 | 402 | 402
CNR-CB12 | CNR | BPD_Protection | BPD_GXP | OC(IT)1 | CB12 | Office | CB12_Office | SEL 751A | 11 | 402 | 402
STU-CB4 | STU | STU_Protection | STU_GXP | OC(IT) | CB4 | Incomer T5 | CB4_Incomer T5 | SEL 351S | 11 | 900 | 900
STU-CB6 | STU | STU_Protection | STU_GXP | OC(IT) | CB6 | Incomer T6 | CB6_Incomer T6 | SEL 351S | 11 | 900 | 900
STU-CB5 | STU | STU_Protection | STU_GXP | OC(IT) | CB5 | Bus Coupler | CB5_Bus Coupler | SEL 351S | 11 | 744 | 744
STU-CB1 | STU | STU_Protection | STU_GXP | OC(IT) | CB1 | Otatio | CB1_Otatio | SEL 351S | 11 | 360 | 360
STU-CB2 | STU | STU_Protection | STU_GXP | OC(IT) | CB2 | Glenavy | CB2_Glenavy | SEL 351S | 11 | 300 | 300
STU-CB3 | STU | STU_Protection | STU_GXP | OC(IT) | CB3 | Waimate | CB3_Waimate | SEL 351S | 11 | 300 | 300
STU-CB7 | STU | STU_Protection | STU_GXP | OC(IT) | CB7 | Waihaorunga | CB7_Waihaorunga | SEL 351S | 11 | 360 | 360
STU-CB8 | STU | STU_Protection | STU_GXP | OC(IT) | CB8 | Mt. Studholme | CB8_Mt. Studholme | SEL 351S | 11 | 360 | 360
STU-CB9 | STU | STU_Protection | STU_GXP | OC(IT) | CB9 | Morven | CB9_Morven | SEL 351S | 11 | 300 | 300
STU-W196 | STU | STU_Protection | STU_GXP | OC(IT) | W196 | Faulkners Rd - Morven Feeder x CB | W196_Faulkners Rd - Morven x CB | Cooper FXB | 11 | 150 | 150
STU-W411 | STU | STU_Protection | STU_GXP | OC(IT) | W411 | Park Rd. Waimate x CB | W411_Park Rd. Waimate x CB | SEL 351R | 11 | 220 | 220
STU-W515 | STU | STU_Protection | STU_GXP | OC(IT) | W515 | Arno x W411 | W515_Arno x W411 | SEL 351R | 11 | 150 | 150
STU-W366 | STU | STU_Protection | STU_GXP | OC(IT) | W366 | Near Skeggs, Otaio Feeder | W366_Near Skeggs, Otaio | Noja RC-01ES | 11 | 260 | 260
STU-W365 | STU | STU_Protection | STU_GXP | OC(IT) | W365 | SH1 Folleys Rd, Studholme Feeder | W365_SH1 Folleys Rd, Studholme | Noja RC-01ES | 11 | 260 | 260
STU-W499 | STU | STU_Protection | STU_GXP | OC(IT) | W499 | Parsonage Rd, Mt Studholme Feeder | W499_Parsonage Rd, Mt Studholme | Noja RC-01ES | 11 | 150 | 150
STU-W465 | STU | STU_Protection | STU_GXP | OC(IT) | W465 | Hunter Makikihi Rd | W465_Hunter Makikihi Rd | Nova/351R | 11 | 100 | 100
STU-W245 | STU | STU_Protection | STU_GXP | OC(IT) | W245 | Crowes Rd | W245_Crowes Rd | Nova/351R RC-01ES | 11 | 150 | 150
STU-W664 | STU | STU_Protection | STU_GXP | OC(IT) | W664 | Park Rd. #2 Waimate x CB | W664_Park Rd. #2 Waimate x CB | SEL 351R | 11 | 170 | 170
STU-W685 | STU | STU_Protection | STU_GXP | OC(IT) | W685 | SH1 north of Makikihi | W685_SH1 north of Makikihi | SEL 651R | 11 | 200 | 200
STU-W176 | STU | STU_Protection | STU_GXP | OC(IT) | W176 | Morven Reg Site x CB3 | W176_Morven Reg Site x CB3 | SEL 351R-F | 11 | 190 | 190
TIM-CB2752 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2752 | 11 kV incomer T3 | 2752_11 kV incomer T3 | SEL 451 | 11 | 1800 | 1800
TIM-CB2842 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2842 | 11 kV incomer T4 | 2842_11 kV incomer T4 | SEL 451 | 11 | 1800 | 1800
TIM-CB2932 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2932 | 11 kV incomer T6 | 2932_11 kV incomer T6 | SEL 451 | 11 | 1800 | 1800
TIM-CB2728 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2728 | Bus Coupler | 2728_Bus Coupler | SEL 351S | 11 | 2496 | 2496
TIM-CB2968 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2968 | Bus Coupler | 2968_Bus Coupler | SEL 351S | 11 | 2496 | 2496
TIM-CB2788 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2788 | Bus Coupler | 2788_Bus Coupler | SEL 351S | 11 | 2496 | 2496
TIM-CB2878 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2878 | Bus Coupler | 2878_Bus Coupler | SEL 351S | 11 | 2496 | 2496
TIM-CB2682 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2682 | Ripple Plant 1/Showgrounds | 2682_Ripple Plant 1/Showgrounds | SEL 551C | 11 | 400 | 400
TIM-CB2992 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2992 | Ripple Plant 2/Goulds Road | 2992_Ripple Plant 2/Goulds Road | SEL 551C | 11 | 400 | 400
TIM-CB2702 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2702 | Morgans Road | 2702_Morgans Road | SEL 551C | 11 | 400 | 400
TIM-CB2712 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2712 | Mountainview Road | 2712_Mountainview Road | SEL 551C | 11 | 400 | 400
TIM-CB2742 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2742 | Seadown | 2742_Seadown | SEL 551C | 11 | 400 | 400
TIM-CB2762 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2762 | AEL Yard | 2762_AEL Yard | SEL 551C | 11 | 400 | 400
TIM-CB2832 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2832 | Grants Road | 2832_Grants Road | SEL 551C | 11 | 400 | 400
TIM-CB2852 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2852 | Levels | 2852_Levels | SEL 551C | 11 | 400 | 400
TIM-CB2862 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2862 | Meadows Road | 2862_Meadows Road | SEL 551C | 11 | 400 | 400
TIM-CB2942 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2942 | Old North Road | 2942_Old North Road | SEL 551C | 11 | 400 | 400
TIM-CB2952 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2952 | Highfield | 2952_Highfield | SEL 551C | 11 | 400 | 400
TIM-CB2972 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2972 | Smithfield | 2972_Smithfield | SEL 551C | 11 | 400 | 400
TIM-CB2732 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2732 | Transformer T1 | 2732_Transformer T1 | SEL 311C | 11 | 1068 | 1068
TIM-CB2922 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2922 | Transformer T2 | 2922_Transformer T2 | SEL 311C | 11 | 1068 | 1068
TIM-CB2692 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2692 | NST-TIM 1 | 2692_NST-TIM 1 | SEL 311L | 11 | 1184 | 1184
TIM-CB2982 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2982 | NST-TIM 2 | 2982_NST-TIM 2 | SEL 311L | 11 | 1184 | 1184
TIM-CB2912 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2912 | GRM-TIM A | 2912_GRM-TIM A | SEL 311L | 11 | 600 | 600
TIM-CB2822 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2822 | GRM-TIM B | 2822_GRM-TIM B | SEL 311L | 11 | 600 | 600
TIM-CB2812 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2812 | GRM-TIM C | 2812_GRM-TIM C | SEL 311L | 11 | 600 | 600
TIM-CB2772 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2772 | GRM-TIM D | 2772_GRM-TIM D | SEL 311L | 11 | 600 | 600
TIM-CB2662 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2662 | Waipopo | 2662_Waipopo | SEL 311L | 11 | 400 | 400
TIM-CB2672 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 2672 | Washdyke | 2672_Washdyke | SEL 311L | 11 | 400 | 400
TIM-CB3002 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 3002 | Elginshire | 3002_Elginshire | SEL 311L | 11 | 400 | 400
TIM-CB3012 | TIM | TIM_Protection | TIM_GXP | OC(IT) | 3012 | Arowhenua | 3012_Arowhenua | SEL 311L | 11 | 400 | 400
TIM-L509 | TIM | TIM_Protection | TIM_GXP | OC | L509 | Scenic Reserve Recloser - CB5 Highfield | L509_Scenic Reserve Recloser - CB5 Highfield | Noja RC-01ES | 11 | 280 | 280
TIM-L839 | TIM | TIM_Protection | TIM_GXP | OC(IT) | L839 | Kellands Hill Recloser - CB16 Levels | L839_Kellands Hill Recloser - CB16 Levels | Noja RC-01ES | 11 | 150 | 150
TIM-L811 | TIM | TIM_Protection | TIM_GXP | OC | L811 | Rosebrook Rd - CB16 Levels | L811_Rosebrook Rd - CB16 Levels | Noja RC-01ES | 11 | 100 | 100
TIM-L808 | TIM | TIM_Protection | TIM_GXP | OC | L808 | Hadlow Craigmore - CB16 Levels | L808_Hadlow Craigmore - CB16 Levels | Cooper FXB | 11 | 140 | 140
TIM-L355 | TIM | TIM_Protection | TIM_GXP | OC | L355 | Racecourse Rd - CB14 Seadown | L355_Racecourse Rd - CB14 Seadown | Noja RC-01ES | 11 | 200 | 200
TIM-L287 | TIM | TIM_Protection | TIM_GXP | OC | L287 | Pages Rd | L287_Pages Rd | Noja RC-01ES | 11 | 200 | 200
TIM-L876 | TIM | TIM_Protection | TIM_GXP | OC | L876 | SH8 Seadown Rd | L876_SH8 Seadown Rd | Noja RC-01ES | 11 | 200 | 200
TIM-L792 | TIM | TIM_Protection | TIM_GXP | OC | L792 | Aorangi Rd | L792_Aorangi Rd | Noja RC-01ES | 11 | 200 | 200
PAR-CB2358 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2358 | Bus Tie 1 | 2358_Bus Tie 1 | SEL 751A | 33 | 320 | 320
PAR-CB2368 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2368 | Bus Tie 2 | 2368_Bus Tie 2 | SEL 751A | 33 | 320 | 320
PAR-CB2332 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2332 | 33kV Incomer 1 | 2332_33kV Incomer 1 | SEL 751A | 33 | 320 | 320
PAR-CB2382 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2382 | 33kV Incomer 2 | 2382_33kV Incomer 2 | SEL 751A | 33 | 320 | 320
PAR-CB2342 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2342 | 33 kV T1 Incomer | 2342_33 kV T1 Incomer | SEL 751A | 33 | 320 | 320
PAR-CB2372 | PAR | TIM_Protection | TIM_GXP | OC(IT) | 2372 | 33 kV T2 Incomer | 2372_33 kV T2 Incomer | SEL 751A | 33 | 320 | 320
PAR-CB35 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB35 | 11kV No 1 Incomer | CB35_11kV No 1 Incomer | SEL 351S-7 | 11 | 950 | 950
PAR-CB36 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB36 | 11kV No 2 Incomer | CB36_11kV No 2 Incomer | SEL 351S-7 | 11 | 950 | 950
PAR-CB31 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB31 | Bus Coupler | CB31_Bus Coupler | SEL 351S-6 | 11 | 520 | 520
PAR-CB3 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB3 | Works No 1 Feeder - Protection Group 1 | CB3_Works No 1 - Protection Group 1 | SEL 351S-6 | 11 | 300 | 300
PAR-CB5 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Works No 2 Feeder - Protection Group 1 | CB5_Works No 2 - Protection Group 1 | SEL 351S-6 | 11 | 300 | 300
PAR-CB4 | PAR | TIM_Protection | TIM_GXP | OC | CB4 | St Andrews | CB4_St Andrews | SEL 351S-6 | 11 | 252 | 252
PAR-CB6 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB6 | Normanby | CB6_Normanby | SEL 351S-6 | 11 | 252 | 252
PAR-CB7 | PAR | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Holmestation | CB7_Holmestation | SEL 351S-6 | 11 | 252 | 252
PAR-L636 | PAR | TIM_Protection | TIM_GXP | OC(IT) | L636 | Southburn x CB7 | L636_Southburn x CB7 | Noja RC-01ES | 11 | 120 | 120
PAR-W470 | PAR | TIM_Protection | TIM_GXP | OC(IT) | W470 | Otaio River x CB4 | W470_Otaio River x CB4 | Noja RC-01ES | 11 | 200 | 200
PAR-L643 | PAR | TIM_Protection | TIM_GXP | OC(IT) | L643 | Pookes Rd x CB6 | L643_Pookes Rd x CB6 | SEL 351R-F | 11 | 110 | 110
PAR-W598 | PAR | TIM_Protection | TIM_GXP | OC(IT) | W598 | Springbank Road x W470 | W598_Springbank Road x W470 | SEL 351R-F | 11 | 120 | 120
PAR-W599 | PAR | TIM_Protection | TIM_GXP | OC(IT) | W599 | Campbell Forrest Road x W470 | W599_Campbell Forrest Road x W470 | SEL 351R-F | 11 | 120 | 120
PAR-L998 | PAR | TIM_Protection | TIM_GXP | OC(IT) | L998 | Bluecliffs Road x CB4 | L998_Bluecliffs Road x CB4 | SEL 351R-F | 11 | 200 | 200
PAR-L1220 | PAR | TIM_Protection | TIM_GXP | OC(IT) | L1220 | Normanby Road x CB6 | L1220_Normanby Road x CB6 | SEL 651R | 11 | 140 | 140
PLP-L250 | PLP | TIM_Protection | TIM_GXP | OC(IT)HV1 | L250 | 33 kV Incomer CB x L269 Timaru | L250_33 kV Incomer CB x L269 Timaru | SEL 387E | 33 | 134 | 134
PLP-CB3 | PLP | TIM_Protection | TIM_GXP | OC(IT)LV2 | CB3 | 11 kV Incomer | CB3_11 kV Incomer | SEL 387E | 11 | 348 | 348
PLP-CB5 | PLP | TIM_Protection | TIM_GXP | OC(IT) | CB5 | PLP Township | CB5_PLP Township | SEL 351A | 11 | 252 | 252
PLP-CB4 | PLP | TIM_Protection | TIM_GXP | OC(IT) | CB4 | Totara Valley Feeder | CB4_Totara Valley | SEL 351A | 11 | 252 | 252
PLP-CB2 | PLP | TIM_Protection | TIM_GXP | OC(IT) | CB2 | Sutherlands Feeder | CB2_Sutherlands | SEL 351A | 11 | 252 | 252
PLP-CB1 | PLP | TIM_Protection | TIM_GXP | OC(IT) | CB1 | Waitawa | CB1_Waitawa | SEL 351A | 11 | 252 | 252
PLP-L107 | PLP | TIM_Protection | TIM_GXP | OC(IT) | L107 | Tengawai Recloser | L107_Tengawai Recloser | SEL 351R-F | 11 | 150 | 150
PLP-L1159 | PLP | TIM_Protection | TIM_GXP | OC(IT) | L1159 | Halstead Road Recloser (Group 1 Current) | L1159_Halstead Road Recloser (Group 1 Current) | SEL 651R | 11 | 200 | 200
GRM-CB2 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB2 | White Street | CB2_White Street | SEL 751A | 11 | 304 | 304
GRM-CB2 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB2 | White Street | CB2_White Street | SEL 551C | 11 | 320 | 304
GRM-CB3 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB3 | GRM-TIM A | CB3_GRM-TIM A | SEL 751A | 11 | 600 | 600
GRM-CB3 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB3 | GRM-TIM A | CB3_GRM-TIM A | SEL 311L | 11 | 600 | 600
GRM-CB4 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB4 | GRM-HNT A | CB4_GRM-HNT A | SEL 751A | 11 | 400 | 400
GRM-CB4 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB4 | GRM-HNT A | CB4_GRM-HNT A | SEL 311L | 11 | 400 | 400
GRM-CB5 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Nile Street | CB5_Nile Street | SEL 751A | 11 | 304 | 304
GRM-CB5 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Nile Street | CB5_Nile Street | SEL 551C | 11 | 320 | 304
GRM-CB6 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB6 | Parkview Terrace | CB6_Parkview Terrace | SEL 751A | 11 | 304 | 304
GRM-CB6 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB6 | Parkview Terrace | CB6_Parkview Terrace | SEL 551C | 11 | 320 | 304
GRM-CB7 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Douglas Street | CB7_Douglas Street | SEL 751A | 11 | 304 | 304
GRM-CB7 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Douglas Street | CB7_Douglas Street | SEL 551C | 11 | 320 | 304
GRM-CB8 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB8 | GRM-TIM B | CB8_GRM-TIM B | SEL 751A | 11 | 600 | 600
GRM-CB8 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB8 | GRM-TIM B | CB8_GRM-TIM B | SEL 311L | 11 | 600 | 600
GRM-CB9 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB9 | GRM-NST A | CB9_GRM-NST A | SEL 751A | 11 | 400 | 400
GRM-CB9 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB9 | GRM-NST A | CB9_GRM-NST A | SEL 311L | 11 | 400 | 400
GRM-CB10 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Ashbury Park | CB10_Ashbury Park | SEL 751A | 11 | 304 | 304
GRM-CB10 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Ashbury Park | CB10_Ashbury Park | SEL 551C | 11 | 320 | 304
GRM-CB12 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB12 | Selwyn Street | CB12_Selwyn Street | SEL 751A | 11 | 304 | 304
GRM-CB12 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB12 | Selwyn Street | CB12_Selwyn Street | SEL 551C | 11 | 320 | 304
GRM-CB13 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB13 | GRM-HNT B | CB13_GRM-HNT B | SEL 751A | 11 | 400 | 400
GRM-CB13 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB13 | GRM-HNT B | CB13_GRM-HNT B | SEL 311L | 11 | 400 | 400
GRM-CB14 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB14 | GRM-TIM C | CB14_GRM-TIM C | SEL 751A | 11 | 600 | 600
GRM-CB14 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB14 | GRM-TIM C | CB14_GRM-TIM C | SEL 311L | 11 | 600 | 600
GRM-CB15 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB15 | Park Lane | CB15_Park Lane | SEL 751A | 11 | 304 | 304
GRM-CB15 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB15 | Park Lane | CB15_Park Lane | SEL 551C | 11 | 320 | 304
GRM-CB16 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Evans Street | CB16_Evans Street | SEL 751A | 11 | 304 | 304
GRM-CB16 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Evans Street | CB16_Evans Street | SEL 551C | 11 | 320 | 304
GRM-CB17 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB17 | June Street | CB17_June Street | SEL 751A | 11 | 304 | 304
GRM-CB17 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB17 | June Street | CB17_June Street | SEL 551C | 11 | 320 | 304
GRM-CB18 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB18 | GRM-NST B | CB18_GRM-NST B | SEL 751A | 11 | 400 | 400
GRM-CB18 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB18 | GRM-NST B | CB18_GRM-NST B | SEL 311L | 11 | 400 | 400
GRM-CB19 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB19 | GRM-TIM D | CB19_GRM-TIM D | SEL 751A | 11 | 600 | 600
GRM-CB19 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB19 | GRM-TIM D | CB19_GRM-TIM D | SEL 311L | 11 | 600 | 600
GRM-CB20 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB20 | Hobbs Street | CB20_Hobbs Street | SEL 751A | 11 | 304 | 304
GRM-CB20 | GRM | TIM_Protection | TIM_GXP | OC(IT) | CB20 | Hobbs Street | CB20_Hobbs Street | SEL 551C | 11 | 320 | 304
HNT-CB1 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB1 | Harper Street | CB1_Harper Street | SEL 751A | 11 | 200 | 200
HNT-CB1 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB1 | Harper Street | CB1_Harper Street | SEL 551C | 11 | 240 | 200
HNT-CB2 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB2 | Wilson St | CB2_Wilson St | SEL 751A | 11 | 200 | 200
HNT-CB2 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB2 | Wilson St | CB2_Wilson St | SEL 551C | 11 | 240 | 200
HNT-CB3 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB3 | GRM-HNT A | CB3_GRM-HNT A | SEL 751A | 11 | 400 | 400
HNT-CB3 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB3 | GRM-HNT A | CB3_GRM-HNT A | SEL 311L | 11 | 400 | 400
HNT-CB4 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB4 | Baker St | CB4_Baker St | SEL 751A | 11 | 200 | 200
HNT-CB4 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB4 | Baker St | CB4_Baker St | SEL 551C | 11 | 240 | 200
HNT-CB5 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Le Cren St | CB5_Le Cren St | SEL 751A | 11 | 200 | 200
HNT-CB5 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Le Cren St | CB5_Le Cren St | SEL 551C | 11 | 240 | 200
HNT-CB6 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB6 | HNT-NST A | CB6_HNT-NST A | SEL 751A | 11 | 400 | 400
HNT-CB6 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB6 | HNT-NST A | CB6_HNT-NST A | SEL 311L | 11 | 400 | 400
HNT-CB7 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Church St South Side | CB7_Church St South Side | SEL 751A | 11 | 200 | 200
HNT-CB7 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Church St South Side | CB7_Church St South Side | SEL 551C | 11 | 240 | 200
HNT-CB8 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB8 | Test Cubicle | CB8_Test Cubicle | SEL 751A | 11 | 200 | 200
HNT-CB8 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB8 | Test Cubicle | CB8_Test Cubicle | SEL 551C | 11 | 240 | 200
HNT-CB10 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Gibson St | CB10_Gibson St | SEL 751A | 11 | 200 | 200
HNT-CB10 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Gibson St | CB10_Gibson St | SEL 551C | 11 | 240 | 200
HNT-CB11 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB11 | Rhodes St | CB11_Rhodes St | SEL 751A | 11 | 200 | 200
HNT-CB11 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB11 | Rhodes St | CB11_Rhodes St | SEL 551C | 11 | 240 | 200
HNT-CB12 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB12 | GRM-HNT B | CB12_GRM-HNT B | SEL 751A | 11 | 400 | 400
HNT-CB12 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB12 | GRM-HNT B | CB12_GRM-HNT B | SEL 311L | 11 | 400 | 400
HNT-CB13 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB13 | Clifton Tce | CB13_Clifton Tce | SEL 751A | 11 | 200 | 200
HNT-CB13 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB13 | Clifton Tce | CB13_Clifton Tce | SEL 551C | 11 | 240 | 200
HNT-CB14 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB14 | Church St North Side | CB14_Church St North Side | SEL 751A | 11 | 200 | 200
HNT-CB14 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB14 | Church St North Side | CB14_Church St North Side | SEL 551C | 11 | 240 | 200
HNT-CB15 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB15 | HNT-NST B | CB15_HNT-NST B | SEL 751A | 11 | 400 | 400
HNT-CB15 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB15 | HNT-NST B | CB15_HNT-NST B | SEL 311L | 11 | 400 | 400
HNT-CB16 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Arthur St | CB16_Arthur St | SEL 751A | 11 | 200 | 200
HNT-CB16 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Arthur St | CB16_Arthur St | SEL 551C | 11 | 240 | 200
HNT-CB17 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB17 | Spare | CB17_Spare | SEL 751A | 11 | 200 | 200
HNT-CB17 | HNT | TIM_Protection | TIM_GXP | OC(IT) | CB17 | Spare | CB17_Spare | SEL 551C | 11 | 240 | 200
NST-CB3 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB3 | Redruth 1 | CB3_Redruth 1 | SEL 751A | 11 | 304 | 304
NST-CB3 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB3 | Redruth 1 | CB3_Redruth 1 | SEL 551C | 11 | 320 | 304
NST-CB4 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB4 | Rose Street | CB4_Rose Street | SEL 751A | 11 | 304 | 304
NST-CB4 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB4 | Rose Street | CB4_Rose Street | SEL 551C | 11 | 320 | 304
NST-CB5 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Cragie Ave + LS1 | CB5_Cragie Ave + LS1 | SEL 751A | 11 | 304 | 304
NST-CB5 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB5 | Cragie Ave + LS1 | CB5_Cragie Ave + LS1 | SEL 551C | 11 | 320 | 304
NST-CB6 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB6 | Grasmere A | CB6_Grasmere A | SEL 751A | 11 | 400 | 400
NST-CB6 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB6 | Grasmere A | CB6_Grasmere A | SEL 311L | 11 | 400 | 400
NST-CB35 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB35 | NST-TIM 1 | CB35_NST-TIM 1 | SEL 751A | 11 | 1188 | 1188
NST-CB35 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB35 | NST-TIM 1 | CB35_NST-TIM 1 | SEL 311L | 11 | 1188 | 1188
NST-CB7 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Hunt Street A | CB7_Hunt Street A | SEL 751A | 11 | 400 | 400
NST-CB7 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB7 | Hunt Street A | CB7_Hunt Street A | SEL 311L | 11 | 400 | 400
NST-CB8 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB8 | Barnard St | CB8_Barnard St | SEL 751A | 11 | 200 | 200
NST-CB8 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB8 | Barnard St | CB8_Barnard St | SEL 551C | 11 | 240 | 200
NST-CB9 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB9 | Port 1 | CB9_Port 1 | SEL 751A | 11 | 304 | 304
NST-CB9 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB9 | Port 1 | CB9_Port 1 | SEL 551C | 11 | 320 | 304
NST-CB10 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Fraser Steet | CB10_Fraser Steet | SEL 751A | 11 | 304 | 304
NST-CB10 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB10 | Fraser Steet | CB10_Fraser Steet | SEL 551C | 11 | 320 | 304
NST-CB11 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB11 | Hayes Street | CB11_Hayes Street | SEL 751A | 11 | 304 | 304
NST-CB11 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB11 | Hayes Street | CB11_Hayes Street | SEL 551C | 11 | 320 | 304
NST-CB12 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB12 | High Street | CB12_High Street | SEL 751A | 11 | 304 | 304
NST-CB12 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB12 | High Street | CB12_High Street | SEL 551C | 11 | 320 | 304
NST-CB13 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB13 | Port 2 | CB13_Port 2 | SEL 751A | 11 | 304 | 304
NST-CB13 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB13 | Port 2 | CB13_Port 2 | SEL 551C | 11 | 320 | 304
NST-CB14 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB14 | Hunt Street B | CB14_Hunt Street B | SEL 751A | 11 | 400 | 400
NST-CB14 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB14 | Hunt Street B | CB14_Hunt Street B | SEL 311L | 11 | 400 | 400
NST-CB36 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB36 | NST-TIM 2 | CB36_NST-TIM 2 | SEL 751A | 11 | 1188 | 1188
NST-CB36 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB36 | NST-TIM 2 | CB36_NST-TIM 2 | SEL 311L | 11 | 1188 | 1188
NST-CB15 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB15 | Grasmere B | CB15_Grasmere B | SEL 751A | 11 | 400 | 400
NST-CB15 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB15 | Grasmere B | CB15_Grasmere B | SEL 311L | 11 | 400 | 400
NST-CB16 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Victoria Steet | CB16_Victoria Steet | SEL 751A | 11 | 304 | 304
NST-CB16 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB16 | Victoria Steet | CB16_Victoria Steet | SEL 551C | 11 | 320 | 304
NST-CB17 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB17 | Stafford Street | CB17_Stafford Street | SEL 751A | 11 | 200 | 200
NST-CB17 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB17 | Stafford Street | CB17_Stafford Street | SEL 551C | 11 | 240 | 200
NST-CB18 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB18 | Redruth 2 | CB18_Redruth 2 | SEL 751A | 11 | 304 | 304
NST-CB18 | NST | TIM_Protection | TIM_GXP | OC(IT) | CB18 | Redruth 2 | CB18_Redruth 2 | SEL 551C | 11 | 320 | 304
TEK-M167 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M167 | 33 kV Incomer x CB1042 | M167_33 kV Incomer x CB1042 | SEL 311C | 33 | 150 | 150
TEK-M202 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M202 | 11kV incomer | M202_11kV incomer | SEL 751A | 11 | 400 | 400
TEK-M204 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M204 | 11kV alt incomer | M204_11kV alt incomer | SEL 751A | 11 | 400 | 400
TEK-M205 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M205 | Godley Peaks Feeder | M205_Godley Peaks | SEL 751A | 11 | 200 | 200
TEK-M201 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M201 | Simons Pass Feeder | M201_Simons Pass | SEL 751A | 11 | 250 | 250
TEK-M206 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M206 | Township Feeder | M206_Township | SEL 751A | 11 | 276 | 276
TEK-M200 | TEK | TKA_Protection | TKA_GXP | OC(IT) | M200 | Haldon - Lilybank Feeder | M200_Haldon - Lilybank | SEL 751A | 11 | 276 | 276
TKA_M11-M346 | TKA_M11 | TKA_Protection | TKA_GXP | OC(IT) | M346 | Mt Cook 33 kV Feeder | M346_Mt Cook 33 kV | SEL 751 | 33 | 150 | 150
OMR-M216 | OMR | TKA_Protection | TKA_GXP | OC(IT) | M216 | Golf Course Sub Tekapo x M214 | M216_Golf Course Sub Tekapo x M214 | Eng. Elec. CDG | 22 | 15 | 15
OMR-M331 | OMR | TKA_Protection | TKA_GXP | OC(IT) | M331 | 11kV incomer | M331_11kV incomer | SEL 751 | 11 | 120 | 120
OMR-M338 | OMR | TKA_Protection | TKA_GXP | OC(IT) | M338 | 22 kV feeder to Simons Pass | M338_22 kV to Simons Pass | SEL 751 | 22 | 60 | 60
UHT-M302 | UHT | TKA_Protection | TKA_GXP | OC(IT) | M302 | Mt Cook Sub 33 kV Incomer x M272 | M302_Mt Cook Sub 33 kV Incomer x M272 | SEL751 | 33 | 50 | 50
UHT-M158 | UHT | TKA_Protection | TKA_GXP | OC(IT) | M158 | Mt Cook Sub 11 kV Feeder x M302 | M158_Mt Cook Sub 11 kV x M302 | SEL751 | 11 | 100 | 100
UHT-M159 | UHT | TKA_Protection | TKA_GXP | OC(IT) | M159 | Mt Cook Sub 11 kV Feeder x M302 | M159_Mt Cook Sub 11 kV x M302 | SEL751 | 11 | 100 | 100
HLB-M82 | HLB | TKA_Protection | TKA_GXP | OC(IT) | M82 | Haldon/Lilybank Incomer x M200 | M82_Haldon/Lilybank Incomer x M200 | SEL/Nova/Ex CT 351R | 11 | 60 | 60
HLB-M86 | HLB | TKA_Protection | TKA_GXP | OC(IT) | M86 | Haldon/Lilybank Incomer x M82 | M86_Haldon/Lilybank Incomer x M82 | SEL/Nova/Ex CT 351R | 22 | 30 | 30
SBT_33kV-M24 | SBT_33kV | TKA_Protection | TKA_GXP | OC(IT) | M24 | To Glentanner x M318 x M346 | M24_To Glentanner x M318 x M346 | SEL351R | 33 | 100 | 100
SBT_33kV-M357 | SBT_33kV | TKA_Protection | TKA_GXP | OC | M357 | Black Hole x M346 | M357_Black Hole x M346 | SEL351R | 33 | 15 | 15
SBT_33kV-M272 | SBT_33kV | TKA_Protection | TKA_GXP | OC | M272 | To UHT x M318 x M346 | M272_To UHT x M318 x M346 | SEL351R | 33 | 80 | 80
SBT_33kV-M318 | SBT_33kV | TKA_Protection | TKA_GXP | OC | M318 | Guide Hill x M346 | M318_Guide Hill x M346 | SEL351R | 33 | 80 | 80
TMK-CB1212 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1212 | Temuka - Temuka 1 | CB1212_Temuka - Temuka 1 |  | 33 | 582 | 582
TMK-CB1222 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1222 | Temuka - Clandeboye T3 | CB1222_Temuka - Clandeboye T3 |  | 33 | 540 | 540
TMK-CB1262 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1262 | Temuka - Temuka 2 | CB1262_Temuka - Temuka 2 |  | 33 | 582 | 582
TMK-CB1272 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1272 | Temuka - Clandeboye T2 | CB1272_Temuka - Clandeboye T2 |  | 33 | 510 | 510
TMK-CB1202 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1202 | Temuka - Rangitata Settings Group 1 | CB1202_Temuka - Rangitata Settings Group 1 |  | 33 | 462 | 462
TMK-CB1192 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1192 | Temuka - Clandeboye T1 | CB1192_Temuka - Clandeboye T1 |  | 33 | 510 | 510
TMK-CB1282 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1282 | Temuka - Clandeboye T4 | CB1282_Temuka - Clandeboye T4 |  | 33 | 660 | 660
TMK-CB1292 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1292 | Temuka - Geraldine Settings Group 1 | CB1292_Temuka - Geraldine Settings Group 1 |  | 33 | 462 | 462
TMK-CB1 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB1 | Temuka West Feeder x T4 | CB1_Temuka West x T4 | SEL351S | 11 | 402 | 402
TMK-CB2 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB2 | Milford Feeder x T4 | CB2_Milford x T4 | SEL351S | 11 | 402 | 402
TMK-CB3 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB3 | Winchester x T4 | CB3_Winchester x T4 | SEL351S | 11 | 402 | 402
TMK-CB4 | TMK | TMK_Protection | TMK_GXP | OC(IT)LV | CB4 | Incoming No. 1 x CB1212 | CB4_Incoming No. 1 x CB1212 | SEL351S | 11 | 1080 | 1080
TMK-CB5 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB5 | Bus Coupler | CB5_Bus Coupler | SEL351S | 11 | 984 | 984
TMK-CB6 | TMK | TMK_Protection | TMK_GXP | OC(IT)LV | CB6 | Incoming No. 2 x CB1262 | CB6_Incoming No. 2 x CB1262 | SEL351S | 11 | 1080 | 1080
TMK-CB7 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB7 | Rangitata x T6 | CB7_Rangitata x T6 | SEL351S | 11 | 402 | 402
TMK-CB8 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB8 | Temuka East Feeder x T6 | CB8_Temuka East x T6 | SEL351S | 11 | 402 | 402
TMK-CB9 | TMK | TMK_Protection | TMK_GXP | OC(IT) | CB9 | Waitohi x T6 | CB9_Waitohi x T6 | SEL351S | 11 | 402 | 402
TMK-G297 | TMK | TMK_Protection | TMK_GXP | OC(IT) | G297 | Waihi Orari x CB3 | G297_Waihi Orari x CB3 | Nova/351R 351R-F | 11 | 200 | 200
TMK-G300 | TMK | TMK_Protection | TMK_GXP | OC(IT) | G300 | Geraldine Winchester Road x CB3 | G300_ Geraldine Winchester Road x CB3 | Nova/351R 351R-F | 11 | 200 | 200
CD1-T615 | CD1 | TMK_Protection | TMK_GXP | OC(IT)HV | T615 | Clandeboye 33 Incomer No.1 x CB1192 | T615_Clandeboye 33 Incomer No.1 x CB1192 | SEL 387E | 33 | 512 | 512
CD1-T616 | CD1 | TMK_Protection | TMK_GXP | OC(IT)HV | T616 | Clandeboye 33 Incomer No.2 x CB1272 | T616_Clandeboye 33 Incomer No.2 x CB1272 | SEL 387E | 33 | 512 | 512
CD1-T600 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T600 | Milk Powder 2 | T600_Milk Powder 2 | SEL 751A | 11 | 1200 | 480
CD1-T600 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T600 | Milk Powder 2 | T600_Milk Powder 2 | SEL 751A | 11 | 480 | 480
CD1-T601 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T601 | Fire Services | T601_Fire Services | SEL 751A | 11 | 1200 | 480
CD1-T601 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T601 | Fire Services | T601_Fire Services | SEL 751A | 11 | 480 | 480
CD1-T602 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T602 | Whey Processing | T602_Whey Processing | SEL 751A | 11 | 1200 | 480
CD1-T602 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T602 | Whey Processing | T602_Whey Processing | SEL 751A | 11 | 480 | 480
CD1-T603 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T603 | Lactose Plant | T603_Lactose Plant | SEL 751A | 11 | 1200 | 480
CD1-T603 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T603 | Lactose Plant | T603_Lactose Plant | SEL 751A | 11 | 480 | 480
CD1-T604 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T604 | Spare | T604_Spare | SEL 751A | 11 | 1200 | 480
CD1-T604 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T604 | Spare | T604_Spare | SEL 751A | 11 | 480 | 480
CD1-T605 | CD1 | TMK_Protection | TMK_GXP | OC(IT) | T605 | Milford/Clandeboye Rd | T605_Milford/Clandeboye Rd | SEL 751A | 11 | 252 | 252
CD1-T606 | CD1 | TMK_Protection | TMK_GXP | OC(IT) | T606 | T1 Incomer | T606_T1 Incomer | SEL 387E | 11 | 1440 | 1440
CD1-T607 | CD1 | TMK_Protection | TMK_GXP | OC(IT) | T607 | Bus Coupler | T607_Bus Coupler | SEL 751A | 11 | 1440 | 1440
CD1-T608 | CD1 | TMK_Protection | TMK_GXP | OC(IT) | T608 | T2 Incomer | T608_T2 Incomer | SEL 387E | 11 | 1440 | 1440
CD1-T609 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T609 | Milk Reception | T609_Milk Reception | SEL 751A | 11 | 1200 | 480
CD1-T609 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T609 | Milk Reception | T609_Milk Reception | SEL 751A | 11 | 480 | 480
CD1-T610 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T610 | Chilled Water No. 1 | T610_Chilled Water No. 1 | SEL 751A | 11 | 1200 | 480
CD1-T610 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T610 | Chilled Water No. 1 | T610_Chilled Water No. 1 | SEL 751A | 11 | 480 | 480
CD1-T611 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T611 | Effluent Plant | T611_Effluent Plant | SEL 751A | 11 | 1200 | 480
CD1-T611 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T611 | Effluent Plant | T611_Effluent Plant | SEL 751A | 11 | 480 | 480
CD1-T612 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T612 | Milk Treatment | T612_Milk Treatment | SEL 751A | 11 | 1200 | 480
CD1-T612 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T612 | Milk Treatment | T612_Milk Treatment | SEL 751A | 11 | 480 | 480
CD1-T613 | CD1 | TMK_Protection | TMK_GXP | OC(IT) | T613 | Rolleston Rd | T613_Rolleston Rd | SEL 751A | 11 | 360 | 360
CD1-T614 | CD1 | TMK_Protection | TMK_GXP | OC(IT)1 | T614 | Powder Handling | T614_Powder Handling | SEL 751A | 11 | 1200 | 480
CD1-T614 | CD1 | TMK_Protection | TMK_GXP | OC(IT)2 | T614 | Powder Handling | T614_Powder Handling | SEL 751A | 11 | 480 | 480
CD2-T662 | CD2 | TMK_Protection | TMK_GXP | OC(IT)HV | T662 | Clandeboye 33 Incomer No.3 x CB1222 | T662_Clandeboye 33 Incomer No.3 x CB1222 | SEL 387E | 33 | 540 | 540
CD2-T663 | CD2 | TMK_Protection | TMK_GXP | OC(IT)HV | T663 | Clandeboye 33 Incomer No.4 x CB1282 | T663_Clandeboye 33 Incomer No.4 x CB1282 | SEL 387E | 33 | 660 | 660
CD2-CB2 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | CB2 | Mozz3 Packing | CB2_Mozz3 Packing | SEL 751A | 11 | 600 | 600
CD2-CB2 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | CB2 | Mozz3 Packing | CB2_Mozz3 Packing | SEL 751A | 11 | 1200 | 600
CD2-T650 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T650 | Tie to Milk Powder 1 | T650_Tie to Milk Powder 1 | Micom P122 | 11 | 1200 | 480
CD2-T650 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T650 | Tie to Milk Powder 1 | T650_Tie to Milk Powder 1 | Micom P122 | 11 | 480 | 480
CD2-T651 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T651 | Milk Powder 3 | T651_Milk Powder 3 | Micom P122 | 11 | 1200 | 480
CD2-T651 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T651 | Milk Powder 3 | T651_Milk Powder 3 | Micom P122 | 11 | 480 | 480
CD2-T652 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T652 | Tie to WPC | T652_Tie to WPC | Micom P122 | 11 | 1200 | 1200
CD2-T653 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T653 | Chilled Water 3 | T653_Chilled Water 3 | Micom P122 | 11 | 1200 | 480
CD2-T653 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T653 | Chilled Water 3 | T653_Chilled Water 3 | Micom P122 | 11 | 480 | 480
CD2-T654 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T654 | Tie to Boiler House | T654_Tie to Boiler House | Micom P122 | 11 | 1200 | 480
CD2-T654 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T654 | Tie to Boiler House | T654_Tie to Boiler House | Micom P122 | 11 | 480 | 480
CD2-T655 | CD2 | TMK_Protection | TMK_GXP | OC(IT) | T655 | Main Incomer - T4 | T655_Main Incomer - T4 | Micom P141 | 11 | 1600 | 1600
CD2-T656 | CD2 | TMK_Protection | TMK_GXP | OC(IT) | T656 | Bus Coupler | T656_Bus Coupler | Micom P141 | 11 | 1400 | 1400
CD2-T657 | CD2 | TMK_Protection | TMK_GXP | OC(IT) | T657 | Main Incomer - T3 | T657_Main Incomer - T3 | Micom P141 | 11 | 1400 | 1400
CD2-T658 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T658 | Milk Powder 2 | T658_Milk Powder 2 | Micom P122 | 11 | 1200 | 480
CD2-T658 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T658 | Milk Powder 2 | T658_Milk Powder 2 | Micom P122 | 11 | 480 | 480
CD2-T659 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T659 | Mozz Refrig/Mozz 2 | T659_Mozz Refrig/Mozz 2 | Micom P122 | 11 | 1200 | 480
CD2-T659 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T659 | Mozz Refrig/Mozz 2 | T659_Mozz Refrig/Mozz 2 | Micom P122 | 11 | 480 | 480
CD2-T660 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T660 | Refrigeration | T660_Refrigeration | Micom P122 | 11 | 1200 | 480
CD2-T660 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T660 | Refrigeration | T660_Refrigeration | Micom P122 | 11 | 480 | 480
CD2-T661 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | T661 | Laboratory | T661_Laboratory | Micom P122 | 11 | 1200 | 480
CD2-T661 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | T661 | Laboratory | T661_Laboratory | Micom P122 | 11 | 480 | 480
CD2-CB15 | CD2 | TMK_Protection | TMK_GXP | OC(IT)1 | CB15 | Mozz3 Main Process | CB15_Mozz3 Main Process | SEL 751A | 11 | 600 | 600
CD2-CB15 | CD2 | TMK_Protection | TMK_GXP | OC(IT)2 | CB15 | Mozz3 Main Process | CB15_Mozz3 Main Process | SEL 751A | 11 | 1200 | 600
GLD-T127 | GLD | TMK_Protection | TMK_GXP | OC(IT) | T127 | Rangitata Badham Rd x CB4 | T127_Rangitata Badham Rd x CB4 | SEL 351R | 11 | 200 | 200
GLD-T685 | GLD | TMK_Protection | TMK_GXP | OC(IT) | T685 | Waitohi Rd x CB9 | T685_Waitohi Rd x CB9 | NOVA 351 Falcon | 11 | 100 | 100
GLD-G259 | GLD | TMK_Protection | TMK_GXP | OC(IT)HV1 | G259 | Gld Sub 33kV CB T2 x CB1292 | G259_Gld Sub 33kV CB T2 x CB1292 | SEL 351R | 33 | 350 | 350
GLD-G260 | GLD | TMK_Protection | TMK_GXP | OC(IT)LV1 | G260 | Gld Sub 11 kV CB T2 x G259 | G260_Gld Sub 11 kV CB T2 x G259 | SEL 387E | 11 | 948 | 948
GLD-G260 | GLD | TMK_Protection | TMK_GXP | OC(IT)LV1 | G260 | Gld Sub 11 kV CB T2 x G259 | G260_Gld Sub 11 kV CB T2 x G259 | Nulec U-Series | 11 | 950 | 948
GLD-G194 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G194 | Speechleys x G260 | G194_Speechleys x G260 | Nulec U-Series | 11 | 350 | 350
GLD-G156 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G156 | Woodbury Feeder x G260 | G156_Woodbury x G260 | Nulec U-Series | 11 | 350 | 350
GLD-G191 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G191 | Geraldine Township x G260 | G191_Geraldine Township x G260 | Nulec U-Series | 11 | 350 | 350
GLD-G249 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G249 | Woodbury x G156 | G249_Woodbury x G156 | Noja RC-01ES | 11 | 165 | 165
GLD-G251 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G251 | Speechly x G194 | G251_Speechly x G194 | Noja RC-01ES | 11 | 165 | 165
GLD-T565 | GLD | TMK_Protection | TMK_GXP | OC(IT) | T565 | Pratt Rd x G249 | T565_Pratt Rd x G249 | Nova/351R | 11 | 100 | 100
GLD-G295 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G295 | Sercombe Rd x G249 | G295_Sercombe Rd x G249 | Nova/351R | 11 | 120 | 120
GLD-G305 | GLD | TMK_Protection | TMK_GXP | OC(IT) | G305 | Te Moana Road x G194 | G305_Te Moana Road x G194 | NOVA15 SEL351R | 11 | 120 | 120
RGA-G332 | RGA | TMK_Protection | TMK_GXP | OC(IT) | G332 | Earl Road - Siemens Fusesaver | G332_Earl Road - Siemens Fusesaver | Siemens Fusesaver | 11 | 90 | 90
RGA-T550 | RGA | TMK_Protection | TMK_GXP | OC(IT) | T550 | 33 kV Incomer Recloser | T550_33 kV Incomer Recloser | Micom P123 | 33 | 220 | 220
RGA-T551 | RGA | TMK_Protection | TMK_GXP | OC | T551 | 11 kV Incomer CB | T551_11 kV Incomer CB | Micom P123, P142 | 11 | 540 | 540
RGA-T552 | RGA | TMK_Protection | TMK_GXP | OC(IT) | T552 | Arundel Feeder | T552_Arundel | Micom P123 | 11 | 300 | 300
RGA-T553 | RGA | TMK_Protection | TMK_GXP | OC(IT) | T553 | Rangitata Island Feeder | T553_Rangitata Island | Micom P123 | 11 | 300 | 300
RGA-T554 | RGA | TMK_Protection | TMK_GXP | OC(IT) | T554 | Orton Feeder | T554_Orton | Micom P123 | 11 | 300 | 300
RGA_T1-CBT555 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | T555 | Main South Rd Feeder | T555_Main South Rd | Micom P123 | 11 | 300 | 300
RGA_T1-CB1522 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 1522 | 33kV T1 Incomer GL107x | 1522_33kV T1 Incomer GL107x | SEL 311C-1 | 33 | 402 | 402
RGA_T2-CB1522 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 1522 | 33kV T1 Incomer GL107x | 1522_33kV T1 Incomer GL107x | SEL 387E | 33 | 402 | 402
RGA_T2-CB1562 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 1562 | 33kV T2 Incomer GL107x | 1562_33kV T2 Incomer GL107x | SEL 311C-1 | 33 | 402 | 402
RGA_T1-CB1562 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 1562 | 33kV T2 Incomer GL107x | 1562_33kV T2 Incomer GL107x | SEL 387E | 33 | 402 | 402
RGA_T1-CB35 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 35 | 11kV T1 Incomer CB | 35_11kV T1 Incomer CB | SEL 751A | 11 | 1048 | 1048
RGA_T2-CB35 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 35 | 11kV T1 Incomer 387E | 35_11kV T1 Incomer 387E | SEL 387E | 11 | 1048 | 1048
RGA_T2-CB36 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 36 | 11kV T2 Incomer CB | 36_11kV T2 Incomer CB | SEL 751A | 11 | 1048 | 1048
RGA_T1-CB36 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 36 | 11kV T2 Incomer 387E | 36_11kV T2 Incomer 387E | SEL 387E | 11 | 1048 | 1048
RGA_T2-CB31 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 31 | Bus Coupler (Tamco Bd) | 31_Bus Coupler (Tamco Bd) | SEL 751A | 11 | 600 | 600
RGA_T2-CB32 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 32 | Bus Coupler (RPS Bd) | 32_Bus Coupler (RPS Bd) | SEL 751A | 11 | 600 | 600
RGA_T1-CB32 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 32 | Bus Coupler (RPS Bd) | 32_Bus Coupler (RPS Bd) | SEL 587 | 11 | 600 | 600
RGA_T1-CB2 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 2 | Arundel Feeder | 2_Arundel | SEL 311C-1 | 11 | 300 | 300
RGA_T1-CB3 | RGA_T1 | TMK_Protection | TMK_GXP | OC(IT) | 3 | Orton Feeder | 3_Orton | SEL 311C-1 | 11 | 300 | 300
RGA_T2-CB4 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 4 | Main South Rd Feeder | 4_Main South Rd | SEL 311C-1 | 11 | 300 | 300
RGA_T2-CB11 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 11 | Belfield | 11_Belfield | SEL 311C-1 | 11 | 300 | 300
RGA_T2-CB12 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 12 | Orton | 12_Orton | SEL 311C-1 | 11 | 300 | 300
RGA_T2-CB13 | RGA_T2 | TMK_Protection | TMK_GXP | OC(IT) | 13 | Rangitata island Feeder | 13_Rangitata island | SEL 311C-1 | 11 | 300 | 300
CNL-RGA-CB1412 | CNL-RGA | TMK_Protection | TMK_GXP | OC(IT) | 1412 | CNL - RGA | 1412_CNL - RGA | SEL 311C-1 | 33 | 423 | 423
CNL-RGA-1412 | CNL-RGA | TMK_Protection | TMK_GXP | OC(IT) | 1412 | CNL - RGA | 1412_CNL - RGA | SEL 751A | 33 | 423 | 423
TWZ-CB6312 | TWZ | TWZ_Protection | TWZ_GXP | OC(IT) | CB6312 | Twizel - AE Feeder | CB6312_Twizel - AE |  | 33 | 252 | 252
TWZ-CB6372 | TWZ | TWZ_Protection | TWZ_GXP | OC(IT) | CB6372 | Twizel - AE Feeder | CB6372_Twizel - AE |  | 33 | 250 | 250
TVS-Z68 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z68 | Twizel Substation Incoming 33 kV CB | Z68_Twizel Substation Incoming 33 kV CB | AEL/Eng. Elec PBO2/CAG | 33 | 150 | 150
TVS-Z1 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z1 | Twizel Substation - Urban No 1 | Z1_Twizel Substation - Urban No 1 | SEL 551C | 11 | 152 | 152
TVS-Z2 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z2 | Twizel Substation - Urban No 2 | Z2_Twizel Substation - Urban No 2 | SEL 551C | 11 | 152 | 152
TVS-Z3 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z3 | Twizel Substation - Industrial | Z3_Twizel Substation - Industrial | SEL 551C | 11 | 150 | 150
TVS-Z4 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z4 | Twizel Substation - Rural Feeder | Z4_Twizel Substation - Rural | SEL 551C | 11 | 152
TVS-Z9 | TVS | TWZ_Protection | TWZ_GXP | OC(IT) | Z9 | Twizel Substation - Local Service | Z9_Twizel Substation - Local Service | SEL 551C | 11 | 30 | 30